## 4QBEP, 4QOP, MC, System Curves
Interpolated Suter Data |  |  |  | Dimensionless |  |  |  | Dimensionalized Curves |  |  |  | Dimensionalized Curves |  |  |  | Manufacturer Curve |  | System Curve |  | System Curve
For MC Region |  |  |  | Flow and Head |  |  |  | at BEP (4QBEP) |  |  |  | at OP (4QOP) | [5 empty] | Initial |  | Final
[9 empty] | QBEP (m3/s) | 0.3895 |  |  | QOP (m3/s) | 0.2243 | [7 empty] | All 4QBEP Curves
All data in θ=atan(α/ν) form |  |  |  |  | Speed (α) = | 1 |  |  | HBEP (m) | 23.62 |  |  | HOP (m) | 28.51
Ns = | 0.42 | 0.46 | 0.79 | Ns = | 0.42 | 0.46 | 0.79 | Ns = | 0.42 | 0.46 | 0.79 | Ns = | 0.42 | 0.46 | 0.79
θ | FH | FH | FH | ν | h | h | h | Q | H | H | H | Q | H | H | H | Q (m3/s) | H (m) | Q (m3/s) | H (m) | Q (m3/s) | H (m) |  | Graphing Points and Lines
20 | -0.06 | -0.17768 | -0.14 | 2.7475 | -0.51292 | -1.5189 | -1.1968 | 1.0701 | -12.1151 | -35.8761 | -28.2686 | 0.61626 | -14.6233 | -43.3035 | -34.121 | 0 | 28.8581 | 0.017241 | 25.0207 | 0.017241 | 11.0156 |  | BEP | 0.3895 | 0
20.5 | -0.05155 | -0.16716 | -0.13 | 2.6746 | -0.42032 | -1.363 | -1.06 | 1.0418 | -9.9279 | -32.193 | -25.0364 | 0.59992 | -11.9833 | -38.8578 | -30.2197 | 0.01 | 28.9986 | 0.033888 | 25.0802 | 0.033888 | 11.0604 |  |  | 0.3895 | 100
21 | -0.0432 | -0.158 | -0.12 | 2.6051 | -0.33638 | -1.2302 | -0.93438 | 1.0147 | -7.9452 | -29.058 | -22.07 | 0.58432 | -9.5901 | -35.0738 | -26.6391 | 0.02 | 29.1245 | 0.050535 | 25.1782 | 0.050535 | 11.1343 |  | Initial OP | 0.2243 | 28.51
21.5 | -0.03495 | -0.14914 | -0.11 | 2.5386 | -0.26019 | -1.1103 | -0.81892 | 0.9888 | -6.1458 | -26.2262 | -19.3429 | 0.56942 | -7.4181 | -31.6557 | -23.3474 | 0.03 | 29.2357 | 0.067182 | 25.315 | 0.067182 | 11.2374 |  | Initial 4QBEP | 0.18 | 27.1
22 | -0.0268 | -0.14061 | -0.1 | 2.4751 | -0.19098 | -1.002 | -0.71261 | 0.96405 | -4.5109 | -23.6666 | -16.8317 | 0.55516 | -5.4448 | -28.5662 | -20.3164 | 0.04 | 29.3323 | 0.083829 | 25.4905 | 0.083829 | 11.3696 |  | Final MC | 0.4418 | 21.27
22.5 | -0.01875 | -0.13238 | -0.09 | 2.4142 | -0.12803 | -0.90397 | -0.61456 | 0.94034 | -3.0241 | -21.3517 | -14.5159 | 0.54151 | -3.6502 | -25.7721 | -17.5211 | 0.05 | 29.4143 | 0.10048 | 25.7046 | 0.10048 | 11.531 |  | Final 4QOP | 0.397 | 19.1
23 | -0.0108 | -0.12447 | -0.08 | 2.3559 | -0.07074 | -0.8153 | -0.524 | 0.9176 | -1.6709 | -19.2575 | -12.377 | 0.52842 | -2.0168 | -23.2443 | -14.9393 | 0.06 | 29.4816 | 0.11712 | 25.9574 | 0.11712 | 11.7216 |  | Final 4QBEP | 0.488 | 23.4
23.5 | -0.00295 | -0.11688 | -0.07 | 2.2998 | -0.018553 | -0.73507 | -0.44025 | 0.89579 | -0.43823 | -17.3624 | -10.3987 | 0.51585 | -0.52896 | -20.9569 | -12.5515 | 0.07 | 29.5344 | 0.13377 | 26.2489 | 0.13377 | 11.9412 | 4QOP Curves
24 | 0.0048 | -0.10959 | -0.06 | 2.246 | 0.029014 | -0.66246 | -0.36268 | 0.87483 | 0.68532 | -15.6474 | -8.5665 | 0.50379 | 0.8272 | -18.8868 | -10.34 | 0.08 | 29.5726 | 0.15042 | 26.5791 | 0.15042 | 12.1901
24.5 | 0.01245 | -0.10263 | -0.05 | 2.1943 | 0.072396 | -0.59676 | -0.29075 | 0.85468 | 1.71 | -14.0955 | -6.8675 | 0.49218 | 2.064 | -17.0137 | -8.2892 | 0.09 | 29.5963 | 0.16706 | 26.9479 | 0.16706 | 12.4681
25 | 0.02 | -0.091778 | -0.04 | 2.1445 | 0.11198 | -0.51386 | -0.22396 | 0.83529 | 2.6449 | -12.1373 | -5.2899 | 0.48101 | 3.1925 | -14.6501 | -6.385 | 0.1 | 29.6054 | 0.18371 | 27.3555 | 0.18371 | 12.7752
25.5 | 0.0324 | -0.079851 | -0.03165 | 2.0965 | 0.17481 | -0.43084 | -0.17077 | 0.8166 | 4.1291 | -10.1764 | -4.0335 | 0.47025 | 4.9839 | -12.2831 | -4.8686 | 0.11 | 29.6 | 0.20036 | 27.8017 | 0.20036 | 13.1115
26 | 0.0456 | -0.067222 | -0.0236 | 2.0503 | 0.23729 | -0.34981 | -0.12281 | 0.79859 | 5.6048 | -8.2624 | -2.9007 | 0.45988 | 6.7652 | -9.973 | -3.5013 | 0.12 | 29.58 | 0.217 | 28.2866 | 0.217 | 13.477
26.5 | 0.0596 | -0.053891 | -0.01585 | 2.0057 | 0.29936 | -0.27068 | -0.079611 | 0.78122 | 7.0708 | -6.3935 | -1.8804 | 0.44988 | 8.5347 | -7.7171 | -2.2697 | 0.13 | 29.5456 | 0.23365 | 28.8102 | 0.23365 | 13.8716
27 | 0.0744 | -0.039857 | -0.0084 | 1.9626 | 0.36098 | -0.19338 | -0.040755 | 0.76444 | 8.5263 | -4.5677 | -0.96264 | 0.44021 | 10.2915 | -5.5133 | -1.1619 | 0.14 | 29.4966 | 0.2503 | 29.3724 | 0.2503 | 14.2954
27.5 | 0.09 | -0.025122 | -0.00125 | 1.921 | 0.42212 | -0.11783 | -0.0058627 | 0.74822 | 9.9704 | -2.783 | -0.13848 | 0.43088 | 12.0345 | -3.3592 | -0.16715 | 0.15 | 29.4332 | 0.26694 | 29.9734 | 0.26694 | 14.7483
28 | 0.1064 | -0.0096843 | 0.0056 | 1.8807 | 0.48275 | -0.043939 | 0.025408 | 0.73254 | 11.4026 | -1.0378 | 0.60014 | 0.42185 | 13.7632 | -1.2527 | 0.72438 | 0.16 | 29.3553 | 0.28359 | 30.613 | 0.28359 | 15.2304
28.5 | 0.1236 | 0.0064552 | 0.01215 | 1.8418 | 0.54287 | 0.028352 | 0.053364 | 0.71737 | 12.8225 | 0.66968 | 1.2605 | 0.41311 | 15.4771 | 0.80832 | 1.5214 | 0.17 | 29.2629 | 0.30024 | 31.2913 | 0.30024 | 15.7416
29 | 0.1416 | 0.021075 | 0.0184 | 1.804 | 0.60245 | 0.089665 | 0.078284 | 0.70268 | 14.2299 | 2.1179 | 1.8491 | 0.40465 | 17.1758 | 2.5564 | 2.2319 | 0.18 | 29.1561 | 0.31688 | 32.0083 | 0.31688 | 16.2819 | Curve Comparison for Ns = 0.42 (22.1 Metric/1140 US) after flow path change
29.5 | 0.1604 | 0.034965 | 0.02435 | 1.7675 | 0.6615 | 0.1442 | 0.10042 | 0.68844 | 15.6245 | 3.4059 | 2.3719 | 0.39645 | 18.8592 | 4.1111 | 2.863 | 0.19 | 29.0349 | 0.33353 | 32.764 | 0.33353 | 16.8515
30 | 0.18 | 0.04887 | 0.03 | 1.7321 | 0.72 | 0.19548 | 0.12 | 0.67463 | 17.0064 | 4.6173 | 2.8344 | 0.3885 | 20.5272 | 5.5732 | 3.4212 | 0.2 | 28.8993 | 0.35018 | 33.5584 | 0.35018 | 17.4502
30.5 | 0.19435 | 0.06279 | 0.0403 | 1.6977 | 0.75448 | 0.24376 | 0.15645 | 0.66124 | 17.8208 | 5.7575 | 3.6953 | 0.38079 | 21.5102 | 6.9495 | 4.4603 | 0.21 | 28.7492 | 0.36683 | 34.3914 | 0.36683 | 18.078
31 | 0.2084 | 0.076725 | 0.0512 | 1.6643 | 0.78563 | 0.28924 | 0.19302 | 0.64824 | 18.5566 | 6.8319 | 4.559 | 0.3733 | 22.3984 | 8.2463 | 5.5029 | 0.22 | 28.5848 | 0.38347 | 35.2631 | 0.38347 | 18.735
31.5 | 0.22215 | 0.090675 | 0.0627 | 1.6319 | 0.81372 | 0.33214 | 0.22967 | 0.63561 | 19.2201 | 7.8451 | 5.4247 | 0.36602 | 23.1992 | 9.4693 | 6.5478 | 0.23 | 28.4059 | 0.40012 | 36.1735 | 0.40012 | 19.4211
32 | 0.2356 | 0.10464 | 0.0748 | 1.6003 | 0.83899 | 0.37263 | 0.26637 | 0.62333 | 19.8169 | 8.8016 | 6.2916 | 0.35896 | 23.9196 | 10.6237 | 7.5942 | 0.24 | 28.2128 | 0.41677 | 37.1226 | 0.41677 | 20.1364
32.5 | 0.24875 | 0.11862 | 0.0875 | 1.5697 | 0.86165 | 0.41089 | 0.30309 | 0.61139 | 20.3521 | 9.7052 | 7.159 | 0.35208 | 24.5656 | 11.7145 | 8.6412 | 0.25 | 28.0052 | 0.43341 | 38.1104 | 0.43341 | 20.8809
33 | 0.2616 | 0.13262 | 0.1008 | 1.5399 | 0.8819 | 0.44707 | 0.33982 | 0.59978 | 20.8305 | 10.5598 | 8.0264 | 0.34539 | 25.143 | 12.746 | 9.6881 | 0.26 | 27.7833 | 0.45006 | 39.1368 | 0.45006 | 21.6545
33.5 | 0.27415 | 0.14662 | 0.1147 | 1.5108 | 0.89993 | 0.48131 | 0.37652 | 0.58847 | 21.2564 | 11.3686 | 8.8933 | 0.33888 | 25.657 | 13.7223 | 10.7345 | 0.27 | 27.5471 | 0.46671 | 40.2019 | 0.46671 | 22.4572
34 | 0.2864 | 0.16065 | 0.1292 | 1.4826 | 0.9159 | 0.51375 | 0.41318 | 0.57746 | 21.6336 | 12.1349 | 9.7593 | 0.33254 | 26.1124 | 14.6471 | 11.7798 | 0.28 | 27.2966 | 0.48335 | 41.3058 | 0.48335 | 23.2891
34.5 | 0.29835 | 0.17469 | 0.1443 | 1.455 | 0.92997 | 0.54451 | 0.44979 | 0.56673 | 21.9659 | 12.8614 | 10.6241 | 0.32636 | 26.5135 | 15.5241 | 12.8235 | 0.29 | 27.0318 | 0.5 | 42.4483 | 0.5 | 24.1502
35 | 0.31 | 0.18874 | 0.16 | 1.4281 | 0.94228 | 0.57371 | 0.48634 | 0.55626 | 22.2566 | 13.5509 | 11.4873 | 0.32033 | 26.8643 | 16.3564 | 13.8655 | 0.3 | 26.7527
35.5 | 0.32135 | 0.20281 | 0.173 | 1.4019 | 0.95295 | 0.60143 | 0.51302 | 0.54606 | 22.5087 | 14.2059 | 12.1176 | 0.31446 | 27.1686 | 17.1469 | 14.6263 | 0.31 | 26.4593
36 | 0.3324 | 0.2169 | 0.186 | 1.3764 | 0.96211 | 0.62779 | 0.53836 | 0.5361 | 22.725 | 14.8285 | 12.7161 | 0.30872 | 27.4297 | 17.8984 | 15.3487 | 0.32 | 26.1517
36.5 | 0.34315 | 0.231 | 0.199 | 1.3514 | 0.96986 | 0.65288 | 0.56244 | 0.52638 | 22.9081 | 15.4209 | 13.2849 | 0.30312 | 27.6507 | 18.6135 | 16.0352 | 0.33 | 25.8298
37 | 0.3536 | 0.24539 | 0.212 | 1.327 | 0.97631 | 0.67753 | 0.58534 | 0.51688 | 23.0604 | 16.0032 | 13.8258 | 0.29766 | 27.8345 | 19.3163 | 16.6881 | 0.34 | 25.4937
37.5 | 0.36375 | 0.26041 | 0.225 | 1.3032 | 0.98154 | 0.70268 | 0.60714 | 0.50761 | 23.184 | 16.5972 | 14.3406 | 0.29231 | 27.9838 | 20.0333 | 17.3095 | 0.35 | 25.1433
38 | 0.3736 | 0.27562 | 0.238 | 1.2799 | 0.98565 | 0.72715 | 0.6279 | 0.49854 | 23.2811 | 17.1752 | 14.8311 | 0.28709 | 28.1009 | 20.7309 | 17.9015 | 0.36 | 24.7788
38.5 | 0.38315 | 0.29102 | 0.251 | 1.2572 | 0.98871 | 0.75098 | 0.6477 | 0.48967 | 23.3534 | 17.7381 | 15.2987 | 0.28198 | 28.1882 | 21.4104 | 18.466 | 0.37 | 24.4
39 | 0.3924 | 0.30662 | 0.264 | 1.2349 | 0.9908 | 0.77421 | 0.66659 | 0.48099 | 23.4027 | 18.2869 | 15.7449 | 0.27699 | 28.2477 | 22.0728 | 19.0045 | 0.38 | 24.0071
39.5 | 0.40135 | 0.32242 | 0.277 | 1.2131 | 0.99198 | 0.79688 | 0.68463 | 0.4725 | 23.4305 | 18.8224 | 16.1711 | 0.2721 | 28.2813 | 22.7191 | 19.5189 | 0.39 | 23.6
40 | 0.41 | 0.3384 | 0.29 | 1.1918 | 0.99231 | 0.81903 | 0.70188 | 0.46419 | 23.4384 | 19.3455 | 16.5784 | 0.26731 | 28.2909 | 23.3505 | 20.0106 | 0.4 | 23.1787
40.5 | 0.41945 | 0.35459 | 0.3074 | 1.1708 | 0.99447 | 0.84068 | 0.72881 | 0.45605 | 23.4894 | 19.8569 | 17.2145 | 0.26262 | 28.3523 | 23.9679 | 20.7784 | 0.41 | 22.7433
41 | 0.4288 | 0.37086 | 0.3256 | 1.1504 | 0.99625 | 0.86164 | 0.75648 | 0.44807 | 23.5315 | 20.3519 | 17.8681 | 0.25803 | 28.4031 | 24.5653 | 21.5673 | 0.42 | 22.2938
41.5 | 0.43805 | 0.38679 | 0.3446 | 1.1303 | 0.99769 | 0.88094 | 0.78485 | 0.44025 | 23.5654 | 20.8078 | 18.5381 | 0.25353 | 28.4441 | 25.1156 | 22.376 | 0.43 | 21.8301
42 | 0.4472 | 0.40278 | 0.3644 | 1.1106 | 0.9988 | 0.89959 | 0.81387 | 0.43258 | 23.5917 | 21.2483 | 19.2237 | 0.24911 | 28.4759 | 25.6473 | 23.2035 | 0.44 | 21.3524
42.5 | 0.45625 | 0.41883 | 0.385 | 1.0913 | 0.99962 | 0.91763 | 0.84352 | 0.42506 | 23.6111 | 21.6745 | 19.9239 | 0.24478 | 28.4992 | 26.1617 | 24.0487 | 0.45 | 20.8605
43 | 0.4652 | 0.43494 | 0.4064 | 1.0724 | 1.0002 | 0.9351 | 0.87375 | 0.41769 | 23.624 | 22.0871 | 20.638 | 0.24053 | 28.5148 | 26.6597 | 24.9106 | 0.46 | 20.3546
43.5 | 0.47405 | 0.4511 | 0.4286 | 1.0538 | 1.0005 | 0.95203 | 0.90454 | 0.41045 | 23.6309 | 22.487 | 21.3652 | 0.23636 | 28.5231 | 27.1425 | 25.7884 | 0.47 | 19.8346
44 | 0.4828 | 0.46733 | 0.4516 | 1.0355 | 1.0005 | 0.96846 | 0.93586 | 0.40334 | 23.6322 | 22.8751 | 22.105 | 0.23227 | 28.5248 | 27.6109 | 26.6814 | 0.48 | 19.3006
44.5 | 0.49145 | 0.48362 | 0.4754 | 1.0176 | 1.0004 | 0.98442 | 0.96769 | 0.39636 | 23.6285 | 23.252 | 22.8568 | 0.22825 | 28.5202 | 28.0658 | 27.5888 | 0.49 | 18.7525
45 | 0.5 | 0.49997 | 0.5 | 1 | 1 | 0.99993 | 1 | 0.3895 | 23.62 | 23.6185 | 23.62 | 0.2243 | 28.51 | 28.5081 | 28.51 | 0.5 | 18.1904
45.5 | 0.5101 | 0.51507 | 0.51605 | 0.9827 | 1.0027 | 1.0125 | 1.0144 | 0.38276 | 23.6838 | 23.9147 | 23.96 | 0.22042 | 28.587 | 28.8658 | 28.9204
46 | 0.5204 | 0.52995 | 0.5312 | 0.96569 | 1.0057 | 1.0242 | 1.0266 | 0.37614 | 23.7547 | 24.1908 | 24.2477 | 0.2166 | 28.6726 | 29.199 | 29.2676
46.5 | 0.5309 | 0.54461 | 0.54545 | 0.94896 | 1.009 | 1.0351 | 1.0366 | 0.36962 | 23.8324 | 24.4479 | 24.4856 | 0.21285 | 28.7664 | 29.5094 | 29.5548
47 | 0.5416 | 0.55904 | 0.5588 | 0.93252 | 1.0126 | 1.0452 | 1.0447 | 0.36321 | 23.9168 | 24.6872 | 24.6764 | 0.20916 | 28.8683 | 29.7981 | 29.7851
47.5 | 0.5525 | 0.57325 | 0.57125 | 0.91633 | 1.0164 | 1.0546 | 1.0509 | 0.35691 | 24.0077 | 24.9095 | 24.8224 | 0.20553 | 28.978 | 30.0664 | 29.9614
48 | 0.5636 | 0.58724 | 0.5828 | 0.9004 | 1.0205 | 1.0633 | 1.0553 | 0.35071 | 24.1048 | 25.1158 | 24.926 | 0.20196 | 29.0952 | 30.3154 | 30.0864
48.5 | 0.5749 | 0.601 | 0.59345 | 0.88473 | 1.0249 | 1.0714 | 1.058 | 0.3446 | 24.2081 | 25.307 | 24.9892 | 0.19844 | 29.2198 | 30.5462 | 30.1626
49 | 0.5864 | 0.61453 | 0.6032 | 0.86929 | 1.0295 | 1.0789 | 1.059 | 0.33859 | 24.3172 | 25.4839 | 25.0139 | 0.19498 | 29.3516 | 30.7598 | 30.1925
49.5 | 0.5981 | 0.62861 | 0.61205 | 0.85408 | 1.0344 | 1.0872 | 1.0585 | 0.33266 | 24.4322 | 25.6787 | 25.0021 | 0.19157 | 29.4904 | 30.9949 | 30.1782
50 | 0.61 | 0.64283 | 0.62 | 0.8391 | 1.0395 | 1.0954 | 1.0565 | 0.32683 | 24.5528 | 25.8744 | 24.9553 | 0.18821 | 29.636 | 31.2311 | 30.1218
50.5 | 0.6199 | 0.65704 | 0.6331 | 0.82434 | 1.0411 | 1.1035 | 1.0633 | 0.32108 | 24.5917 | 26.065 | 25.1154 | 0.1849 | 29.6829 | 31.4612 | 30.315
51 | 0.6296 | 0.67123 | 0.6464 | 0.80978 | 1.0425 | 1.1114 | 1.0703 | 0.31541 | 24.6229 | 26.2508 | 25.2799 | 0.18163 | 29.7205 | 31.6855 | 30.5136
51.5 | 0.6391 | 0.6854 | 0.6599 | 0.79544 | 1.0435 | 1.1191 | 1.0774 | 0.30982 | 24.6468 | 26.4323 | 25.4489 | 0.17842 | 29.7493 | 31.9045 | 30.7176
52 | 0.6484 | 0.69956 | 0.6736 | 0.78129 | 1.0442 | 1.1266 | 1.0848 | 0.30431 | 24.6637 | 26.6097 | 25.6223 | 0.17524 | 29.7698 | 32.1186 | 30.9268
52.5 | 0.6575 | 0.7137 | 0.6875 | 0.76733 | 1.0446 | 1.1339 | 1.0923 | 0.29887 | 24.6742 | 26.7833 | 25.8 | 0.17211 | 29.7824 | 32.3282 | 31.1413
53 | 0.6664 | 0.72783 | 0.7016 | 0.75355 | 1.0448 | 1.1411 | 1.1 | 0.29351 | 24.6784 | 26.9534 | 25.982 | 0.16902 | 29.7876 | 32.5335 | 31.361
53.5 | 0.6751 | 0.7417 | 0.7159 | 0.73996 | 1.0447 | 1.1478 | 1.1079 | 0.28821 | 24.6769 | 27.1112 | 26.1683 | 0.16597 | 29.7857 | 32.724 | 31.5858
54 | 0.6836 | 0.75533 | 0.7304 | 0.72654 | 1.0444 | 1.154 | 1.116 | 0.28299 | 24.6699 | 27.2584 | 26.3588 | 0.16296 | 29.7772 | 32.9016 | 31.8158
54.5 | 0.6919 | 0.76885 | 0.7451 | 0.71329 | 1.0439 | 1.16 | 1.1242 | 0.27783 | 24.6576 | 27.4001 | 26.5535 | 0.15999 | 29.7624 | 33.0727 | 32.0509
55 | 0.7 | 0.78228 | 0.76 | 0.70021 | 1.0432 | 1.1658 | 1.1326 | 0.27273 | 24.6405 | 27.5366 | 26.7525 | 0.15706 | 29.7417 | 33.2375 | 32.291
55.5 | 0.71175 | 0.79559 | 0.7773 | 0.68728 | 1.0479 | 1.1714 | 1.1445 | 0.2677 | 24.7525 | 27.6684 | 27.0322 | 0.15416 | 29.877 | 33.3965 | 32.6286
56 | 0.724 | 0.80881 | 0.7952 | 0.67451 | 1.0534 | 1.1768 | 1.157 | 0.26272 | 24.8811 | 27.7956 | 27.328 | 0.15129 | 30.0322 | 33.5501 | 32.9857
56.5 | 0.73675 | 0.82191 | 0.8137 | 0.66189 | 1.0595 | 1.182 | 1.1702 | 0.2578 | 25.0257 | 27.9186 | 27.6396 | 0.14846 | 30.2068 | 33.6985 | 33.3617
57 | 0.75 | 0.83492 | 0.8328 | 0.64941 | 1.0663 | 1.187 | 1.184 | 0.25294 | 25.186 | 28.0376 | 27.9665 | 0.14566 | 30.4001 | 33.8422 | 33.7563
57.5 | 0.76375 | 0.84776 | 0.8525 | 0.63707 | 1.0737 | 1.1918 | 1.1985 | 0.24814 | 25.3614 | 28.151 | 28.3084 | 0.14289 | 30.6119 | 33.9791 | 34.1691
58 | 0.778 | 0.8604 | 0.8728 | 0.62487 | 1.0818 | 1.1964 | 1.2136 | 0.24339 | 25.5516 | 28.258 | 28.6651 | 0.14016 | 30.8415 | 34.1082 | 34.5996
58.5 | 0.79275 | 0.87291 | 0.8937 | 0.6128 | 1.0904 | 1.2007 | 1.2293 | 0.23869 | 25.7564 | 28.3608 | 29.0362 | 0.13745 | 31.0887 | 34.2323 | 35.0475
59 | 0.808 | 0.88529 | 0.9152 | 0.60086 | 1.0997 | 1.2049 | 1.2456 | 0.23404 | 25.9753 | 28.4599 | 29.4215 | 0.13477 | 31.3529 | 34.3519 | 35.5126
59.5 | 0.82375 | 0.89753 | 0.9373 | 0.58905 | 1.1096 | 1.2089 | 1.2625 | 0.22943 | 26.208 | 28.5553 | 29.8207 | 0.13212 | 31.6338 | 34.4671 | 35.9944
60 | 0.84 | 0.90963 | 0.96 | 0.57735 | 1.12 | 1.2128 | 1.28 | 0.22488 | 26.4544 | 28.6474 | 30.2336 | 0.1295 | 31.9312 | 34.5782 | 36.4928
60.5 | 0.8518 | 0.92161 | 0.9767 | 0.56577 | 1.1245 | 1.2166 | 1.2893 | 0.22037 | 26.5597 | 28.7364 | 30.4542 | 0.1269 | 32.0584 | 34.6856 | 36.7591
61 | 0.8632 | 0.93344 | 0.9928 | 0.55431 | 1.1284 | 1.2203 | 1.2978 | 0.2159 | 26.6534 | 28.8224 | 30.6551 | 0.12433 | 32.1714 | 34.7894 | 37.0016
61.5 | 0.8742 | 0.94511 | 1.0083 | 0.54296 | 1.1319 | 1.2237 | 1.3055 | 0.21148 | 26.7358 | 28.9046 | 30.837 | 0.12178 | 32.2709 | 34.8886 | 37.2212
62 | 0.8848 | 0.95654 | 1.0232 | 0.53171 | 1.1349 | 1.227 | 1.3125 | 0.2071 | 26.8074 | 28.9809 | 31.0006 | 0.11926 | 32.3573 | 34.9807 | 37.4186
62.5 | 0.895 | 0.96779 | 1.0375 | 0.52057 | 1.1375 | 1.2301 | 1.3187 | 0.20276 | 26.8686 | 29.054 | 31.1466 | 0.11676 | 32.4312 | 35.0689 | 37.5948
63 | 0.9048 | 0.97889 | 1.0512 | 0.50953 | 1.1397 | 1.233 | 1.3241 | 0.19846 | 26.9197 | 29.124 | 31.2754 | 0.11429 | 32.4929 | 35.1535 | 37.7503
63.5 | 0.9142 | 0.98982 | 1.0643 | 0.49858 | 1.1415 | 1.2359 | 1.3289 | 0.1942 | 26.9612 | 29.1913 | 31.3879 | 0.11183 | 32.5429 | 35.2347 | 37.886
64 | 0.9232 | 1.0006 | 1.0768 | 0.48773 | 1.1428 | 1.2386 | 1.333 | 0.18997 | 26.9933 | 29.2559 | 31.4843 | 0.1094 | 32.5816 | 35.3127 | 38.0025
64.5 | 0.9318 | 1.0112 | 1.0887 | 0.47698 | 1.1438 | 1.2412 | 1.3364 | 0.18578 | 27.0163 | 29.318 | 31.5654 | 0.10699 | 32.6094 | 35.3877 | 38.1003
65 | 0.94 | 1.0216 | 1.1 | 0.46631 | 1.1444 | 1.2438 | 1.3392 | 0.18163 | 27.0306 | 29.3778 | 31.6316 | 0.10459 | 32.6267 | 35.4599 | 38.1802
65.5 | 0.9522 | 1.0319 | 1.1135 | 0.45573 | 1.15 | 1.2462 | 1.3447 | 0.17751 | 27.162 | 29.4351 | 31.7618 | 0.10222 | 32.7853 | 35.529 | 38.3374
66 | 0.9648 | 1.0419 | 1.1268 | 0.44523 | 1.1561 | 1.2484 | 1.3502 | 0.17342 | 27.3059 | 29.4868 | 31.8909 | 0.099865 | 32.959 | 35.5913 | 38.4932
66.5 | 0.9778 | 1.0516 | 1.1401 | 0.43481 | 1.1627 | 1.2505 | 1.3556 | 0.16936 | 27.4621 | 29.5357 | 32.019 | 0.097528 | 33.1476 | 35.6504 | 38.6479
67 | 0.9912 | 1.0612 | 1.1532 | 0.42447 | 1.1698 | 1.2524 | 1.361 | 0.16533 | 27.6305 | 29.5821 | 32.1464 | 0.09521 | 33.3508 | 35.7065 | 38.8016
67.5 | 1.005 | 1.0706 | 1.1663 | 0.41421 | 1.1774 | 1.2543 | 1.3663 | 0.16134 | 27.8109 | 29.6262 | 32.2731 | 0.092908 | 33.5686 | 35.7596 | 38.9545
68 | 1.0192 | 1.0798 | 1.1792 | 0.40403 | 1.1856 | 1.2561 | 1.3717 | 0.15737 | 28.0032 | 29.6679 | 32.3993 | 0.090623 | 33.8006 | 35.81 | 39.1069
68.5 | 1.0338 | 1.0888 | 1.1921 | 0.39391 | 1.1942 | 1.2577 | 1.377 | 0.15343 | 28.2072 | 29.7076 | 32.5251 | 0.088354 | 34.0469 | 35.8579 | 39.2587
69 | 1.0488 | 1.0976 | 1.2048 | 0.38386 | 1.2033 | 1.2593 | 1.3823 | 0.14952 | 28.4229 | 29.7452 | 32.6506 | 0.086101 | 34.3073 | 35.9033 | 39.4102
69.5 | 1.0642 | 1.1062 | 1.2175 | 0.37388 | 1.213 | 1.2608 | 1.3876 | 0.14563 | 28.6502 | 29.781 | 32.776 | 0.083862 | 34.5816 | 35.9464 | 39.5615
70 | 1.08 | 1.1147 | 1.23 | 0.36397 | 1.2231 | 1.2624 | 1.3929 | 0.14177 | 28.889 | 29.8182 | 32.9013 | 0.081639 | 34.8698 | 35.9914 | 39.7128
70.5 | 1.0929 | 1.1231 | 1.2463 | 0.35412 | 1.2299 | 1.264 | 1.4026 | 0.13793 | 29.0514 | 29.8548 | 33.1291 | 0.079429 | 35.0659 | 36.0356 | 39.9877
71 | 1.1056 | 1.1313 | 1.2632 | 0.34433 | 1.2367 | 1.2655 | 1.413 | 0.13412 | 29.2104 | 29.8906 | 33.3743 | 0.077233 | 35.2578 | 36.0788 | 40.2837
71.5 | 1.1181 | 1.1394 | 1.2807 | 0.3346 | 1.2433 | 1.267 | 1.4241 | 0.13032 | 29.3662 | 29.9257 | 33.6368 | 0.07505 | 35.4458 | 36.1211 | 40.6005
72 | 1.1304 | 1.1473 | 1.2988 | 0.32492 | 1.2497 | 1.2684 | 1.4359 | 0.12656 | 29.5188 | 29.96 | 33.9164 | 0.072879 | 35.6301 | 36.1626 | 40.938
72.5 | 1.1425 | 1.155 | 1.3175 | 0.3153 | 1.2561 | 1.2698 | 1.4485 | 0.12281 | 29.6686 | 29.9938 | 34.213 | 0.070722 | 35.8108 | 36.2034 | 41.2961
73 | 1.1544 | 1.1626 | 1.3368 | 0.30573 | 1.2623 | 1.2713 | 1.4618 | 0.11908 | 29.8156 | 30.0271 | 34.5266 | 0.068575 | 35.9883 | 36.2435 | 41.6746
73.5 | 1.1661 | 1.17 | 1.3567 | 0.29621 | 1.2684 | 1.2726 | 1.4757 | 0.11538 | 29.96 | 30.0599 | 34.857 | 0.066441 | 36.1626 | 36.2831 | 42.0734
74 | 1.1776 | 1.1772 | 1.3772 | 0.28675 | 1.2744 | 1.274 | 1.4904 | 0.11169 | 30.1019 | 30.091 | 35.2041 | 0.064317 | 36.3339 | 36.3207 | 42.4924
74.5 | 1.1889 | 1.1842 | 1.3983 | 0.27732 | 1.2803 | 1.2752 | 1.5058 | 0.10802 | 30.2416 | 30.1211 | 35.568 | 0.062204 | 36.5024 | 36.357 | 42.9315
75 | 1.2 | 1.191 | 1.42 | 0.26795 | 1.2862 | 1.2765 | 1.522 | 0.10437 | 30.379 | 30.1506 | 35.9485 | 0.060101 | 36.6683 | 36.3926 | 43.3908
75.5 | 1.2103 | 1.1976 | 1.4362 | 0.25862 | 1.2913 | 1.2777 | 1.5323 | 0.10073 | 30.5006 | 30.1795 | 36.1932 | 0.058008 | 36.815 | 36.4275 | 43.6862
76 | 1.2204 | 1.2041 | 1.452 | 0.24933 | 1.2963 | 1.2789 | 1.5423 | 0.097113 | 30.6178 | 30.208 | 36.4282 | 0.055924 | 36.9565 | 36.4619 | 43.9699
76.5 | 1.2302 | 1.2103 | 1.4673 | 0.24008 | 1.3011 | 1.2801 | 1.5518 | 0.093511 | 30.7309 | 30.236 | 36.654 | 0.05385 | 37.093 | 36.4957 | 44.2424
77 | 1.2396 | 1.2164 | 1.482 | 0.23087 | 1.3057 | 1.2813 | 1.561 | 0.089923 | 30.8399 | 30.2636 | 36.8706 | 0.051784 | 37.2247 | 36.529 | 44.5038
77.5 | 1.2488 | 1.2224 | 1.4962 | 0.22169 | 1.3101 | 1.2824 | 1.5698 | 0.08635 | 30.9451 | 30.2909 | 37.0784 | 0.049726 | 37.3516 | 36.562 | 44.7547
78 | 1.2576 | 1.2279 | 1.51 | 0.21256 | 1.3144 | 1.2834 | 1.5782 | 0.082791 | 31.0466 | 30.3127 | 37.2776 | 0.047676 | 37.4741 | 36.5883 | 44.9951
78.5 | 1.2661 | 1.233 | 1.5232 | 0.20345 | 1.3186 | 1.284 | 1.5863 | 0.079245 | 31.1444 | 30.3283 | 37.4684 | 0.045634 | 37.5921 | 36.6071 | 45.2255
79 | 1.2744 | 1.2378 | 1.536 | 0.19438 | 1.3226 | 1.2846 | 1.594 | 0.075711 | 31.2387 | 30.3415 | 37.6511 | 0.0436 | 37.7059 | 36.6231 | 45.446
79.5 | 1.2824 | 1.2424 | 1.5483 | 0.18534 | 1.3264 | 1.285 | 1.6014 | 0.07219 | 31.3296 | 30.3526 | 37.8259 | 0.041572 | 37.8156 | 36.6364 | 45.6569
80 | 1.29 | 1.2467 | 1.56 | 0.17633 | 1.3301 | 1.2854 | 1.6085 | 0.068679 | 31.4171 | 30.3614 | 37.9928 | 0.03955 | 37.9214 | 36.6471 | 45.8584
80.5 | 1.2974 | 1.2507 | 1.5735 | 0.16734 | 1.3337 | 1.2857 | 1.6175 | 0.06518 | 31.5015 | 30.3682 | 38.2056 | 0.037535 | 38.0232 | 36.6552 | 46.1153
81 | 1.3044 | 1.2544 | 1.5868 | 0.15838 | 1.3371 | 1.2859 | 1.6266 | 0.061691 | 31.5828 | 30.3728 | 38.4204 | 0.035526 | 38.1213 | 36.6609 | 46.3745
81.5 | 1.3112 | 1.2579 | 1.6001 | 0.14945 | 1.3404 | 1.286 | 1.6358 | 0.058211 | 31.6611 | 30.3755 | 38.6373 | 0.033522 | 38.2158 | 36.6641 | 46.6363
82 | 1.3176 | 1.2612 | 1.6132 | 0.14054 | 1.3436 | 1.2861 | 1.6451 | 0.054741 | 31.7364 | 30.3784 | 38.8564 | 0.031523 | 38.3067 | 36.6676 | 46.9008
82.5 | 1.3237 | 1.2645 | 1.6262 | 0.13165 | 1.3467 | 1.2864 | 1.6544 | 0.051279 | 31.8089 | 30.3842 | 39.0778 | 0.02953 | 38.3942 | 36.6746 | 47.168
83 | 1.3296 | 1.2675 | 1.6392 | 0.12278 | 1.3496 | 1.2866 | 1.6639 | 0.047825 | 31.8786 | 30.3896 | 39.3016 | 0.027541 | 38.4784 | 36.681 | 47.4381
83.5 | 1.3352 | 1.2703 | 1.6521 | 0.11394 | 1.3525 | 1.2868 | 1.6735 | 0.044378 | 31.9456 | 30.3944 | 39.528 | 0.025556 | 38.5593 | 36.6869 | 47.7114
84 | 1.3404 | 1.2729 | 1.6648 | 0.1051 | 1.3552 | 1.287 | 1.6832 | 0.040938 | 32.01 | 30.3988 | 39.757 | 0.023575 | 38.637 | 36.6922 | 47.9878
84.5 | 1.3453 | 1.2753 | 1.6774 | 0.096289 | 1.3578 | 1.2872 | 1.693 | 0.037505 | 32.0718 | 30.4028 | 39.9887 | 0.021598 | 38.7115 | 36.697 | 48.2675
85 | 1.35 | 1.2775 | 1.69 | 0.087489 | 1.3603 | 1.2873 | 1.7029 | 0.034077 | 32.1311 | 30.4064 | 40.2233 | 0.019624 | 38.7831 | 36.7013 | 48.5507
85.5 | 1.3544 | 1.2795 | 1.703 | 0.078702 | 1.3627 | 1.2874 | 1.7135 | 0.030654 | 32.1879 | 30.4095 | 40.474 | 0.017653 | 38.8517 | 36.7051 | 48.8533
86 | 1.3584 | 1.2813 | 1.716 | 0.069927 | 1.365 | 1.2876 | 1.7244 | 0.027236 | 32.2423 | 30.4123 | 40.7301 | 0.015685 | 38.9174 | 36.7085 | 49.1624
86.5 | 1.3622 | 1.2829 | 1.729 | 0.061163 | 1.3672 | 1.2877 | 1.7355 | 0.023823 | 32.2943 | 30.4148 | 40.9918 | 0.013719 | 38.9802 | 36.7115 | 49.4782
87 | 1.3656 | 1.2842 | 1.742 | 0.052408 | 1.3694 | 1.2878 | 1.7468 | 0.020413 | 32.3441 | 30.4168 | 41.2591 | 0.011755 | 39.0402 | 36.714 | 49.8008
87.5 | 1.3687 | 1.2854 | 1.755 | 0.043661 | 1.3714 | 1.2878 | 1.7583 | 0.017006 | 32.3915 | 30.4186 | 41.5321 | 0.0097931 | 39.0975 | 36.7161 | 50.1304
88 | 1.3716 | 1.2863 | 1.768 | 0.034921 | 1.3733 | 1.2879 | 1.7702 | 0.013602 | 32.4367 | 30.42 | 41.8111 | 0.0078327 | 39.152 | 36.7178 | 50.4671
88.5 | 1.3741 | 1.2871 | 1.781 | 0.026186 | 1.3751 | 1.2879 | 1.7822 | 0.010199 | 32.4797 | 30.4211 | 42.0961 | 0.0058735 | 39.2039 | 36.7191 | 50.8111
89 | 1.3764 | 1.2876 | 1.794 | 0.017455 | 1.3768 | 1.288 | 1.7945 | 0.0067987 | 32.5205 | 30.4219 | 42.3872 | 0.0039152 | 39.2531 | 36.7201 | 51.1625
89.5 | 1.3783 | 1.2879 | 1.807 | 0.0087269 | 1.3785 | 1.288 | 1.8071 | 0.0033991 | 32.5591 | 30.4224 | 42.6846 | 0.0019574 | 39.2998 | 36.7207 | 51.5215
90 | 1.38 | 1.288 | 1.82 | 6.1257e-17 | 1.38 | 1.288 | 1.82 | 2.386e-17 | 32.5956 | 30.4226 | 42.9884 | 1.374e-17 | 39.3438 | 36.7209 | 51.8882

## ESD Exit Transient (Ns = 0.42)
Transient conditions immediately downstream of ESD
| Pressure (m H2O std) |  |  | Velocity (m/s)
Time (s) | MC | 4QBEP | 4QOP | MC | 4QBEP | 4QOP | Event Times
0 | 88.425 | 87.1322 | 88.425 | 1.1422 | 0.90099 | 1.1422 | 10 | -10
0.0041667 | 88.4262 | 87.1329 | 88.4262 | 1.1422 | 0.901 | 1.1422 | 10 | 200
0.0083333 | 88.4262 | 87.1329 | 88.4262 | 1.1422 | 0.901 | 1.1422
0.0125 | 88.1521 | 86.8712 | 88.1533 | 1.1444 | 0.90313 | 1.1444 | 20 | -10
0.016667 | 87.8933 | 86.623 | 87.8944 | 1.1465 | 0.90516 | 1.1465 | 20 | 200
0.020833 | 87.7031 | 86.4614 | 87.7339 | 1.1476 | 0.90638 | 1.1479
0.025 | 87.5398 | 86.3035 | 87.576 | 1.1489 | 0.90756 | 1.1492 | 27 | -10
0.029167 | 87.604 | 86.3739 | 87.6664 | 1.1523 | 0.91095 | 1.1529 | 27 | 200
0.033333 | 87.679 | 86.4426 | 87.7509 | 1.1557 | 0.91419 | 1.1565
0.0375 | 87.5784 | 86.3419 | 87.6622 | 1.159 | 0.91723 | 1.1599
0.041667 | 87.4853 | 86.2488 | 87.579 | 1.1622 | 0.92019 | 1.1632 | Atmosphere
0.045833 | 87.5339 | 86.2994 | 87.6538 | 1.1644 | 0.92228 | 1.1656 | 0 | 10.3326
0.05 | 87.5842 | 86.3425 | 87.7187 | 1.1667 | 0.92434 | 1.1679 | 30 | 10.3326
0.054167 | 87.6565 | 86.3989 | 87.798 | 1.17 | 0.92745 | 1.1714
0.058333 | 87.7209 | 86.4619 | 87.875 | 1.1732 | 0.9305 | 1.1748
0.0625 | 87.6601 | 86.4041 | 87.8212 | 1.1754 | 0.93254 | 1.177
0.066667 | 87.6025 | 86.3527 | 87.7717 | 1.1776 | 0.93462 | 1.1792
0.070833 | 87.6644 | 86.4203 | 87.8492 | 1.1796 | 0.9367 | 1.1814
0.075 | 87.724 | 86.4809 | 87.9188 | 1.1817 | 0.9387 | 1.1836
0.079167 | 87.7269 | 86.4844 | 87.9245 | 1.1842 | 0.94116 | 1.1862
0.083333 | 87.7284 | 86.495 | 87.9344 | 1.1867 | 0.94354 | 1.1887
0.0875 | 87.6964 | 86.4741 | 87.9102 | 1.1884 | 0.94521 | 1.1905
0.091667 | 87.666 | 86.4516 | 87.8871 | 1.1901 | 0.94687 | 1.1923
0.095833 | 87.7125 | 86.5015 | 87.9424 | 1.1921 | 0.94885 | 1.1944
0.1 | 87.7535 | 86.5474 | 87.9928 | 1.194 | 0.95075 | 1.1964
0.10417 | 87.738 | 86.5352 | 87.9793 | 1.196 | 0.95266 | 1.1985
0.10833 | 87.722 | 86.5278 | 87.9705 | 1.1979 | 0.95453 | 1.2005
0.1125 | 87.7178 | 86.5317 | 87.9747 | 1.1995 | 0.95604 | 1.2022
0.11667 | 87.7145 | 86.5321 | 87.9772 | 1.201 | 0.95752 | 1.2038
0.12083 | 87.7402 | 86.5603 | 88.0098 | 1.2028 | 0.95926 | 1.2057
0.125 | 87.7634 | 86.588 | 88.0404 | 1.2045 | 0.96094 | 1.2075
0.12917 | 87.7493 | 86.5784 | 88.0299 | 1.2061 | 0.96247 | 1.2092
0.13333 | 87.7366 | 86.5712 | 88.0223 | 1.2077 | 0.96397 | 1.2108
0.1375 | 87.7437 | 86.5832 | 88.0366 | 1.2091 | 0.96535 | 1.2123
0.14167 | 87.7503 | 86.5926 | 88.0485 | 1.2105 | 0.96669 | 1.2138
0.14583 | 87.7624 | 86.6062 | 88.0648 | 1.212 | 0.96815 | 1.2154
0.15 | 87.7713 | 86.6205 | 88.0807 | 1.2135 | 0.96957 | 1.2169
0.15417 | 87.7646 | 86.6173 | 88.0773 | 1.2148 | 0.97084 | 1.2183
0.15833 | 87.7576 | 86.6147 | 88.0752 | 1.2161 | 0.97209 | 1.2197
0.1625 | 87.766 | 86.6262 | 88.0891 | 1.2174 | 0.97332 | 1.221
0.16667 | 87.7724 | 86.6361 | 88.1012 | 1.2186 | 0.97451 | 1.2223
0.17083 | 87.7782 | 86.6428 | 88.1093 | 1.2199 | 0.97572 | 1.2237
0.175 | 87.781 | 86.6501 | 88.1177 | 1.2211 | 0.97691 | 1.225
0.17917 | 87.7799 | 86.6513 | 88.1194 | 1.2223 | 0.978 | 1.2262
0.18333 | 87.7776 | 86.6523 | 88.1214 | 1.2234 | 0.97906 | 1.2274
0.1875 | 87.7833 | 86.6609 | 88.1319 | 1.2245 | 0.98013 | 1.2286
0.19167 | 87.7891 | 86.6687 | 88.1414 | 1.2256 | 0.98116 | 1.2297
0.19583 | 87.7907 | 86.6727 | 88.1464 | 1.2266 | 0.98218 | 1.2308
0.2 | 87.7933 | 86.6771 | 88.1518 | 1.2277 | 0.98317 | 1.2319
0.20417 | 87.7931 | 86.6802 | 88.1557 | 1.2287 | 0.98411 | 1.233
0.20833 | 87.794 | 86.6829 | 88.1595 | 1.2296 | 0.98503 | 1.234
0.2125 | 87.7964 | 86.6889 | 88.167 | 1.2306 | 0.98594 | 1.235
0.21667 | 87.8005 | 86.6945 | 88.1739 | 1.2315 | 0.98683 | 1.236
0.22083 | 87.801 | 86.6977 | 88.1779 | 1.2324 | 0.98769 | 1.237
0.225 | 87.8027 | 86.701 | 88.1821 | 1.2333 | 0.98853 | 1.2379
0.22917 | 87.8046 | 86.7043 | 88.1864 | 1.2341 | 0.98934 | 1.2388
0.23333 | 87.805 | 86.7074 | 88.1905 | 1.235 | 0.99013 | 1.2397
0.2375 | 87.8078 | 86.7116 | 88.1959 | 1.2358 | 0.99091 | 1.2406
0.24167 | 87.8104 | 86.7157 | 88.201 | 1.2366 | 0.99167 | 1.2415
0.24583 | 87.8107 | 86.7184 | 88.2046 | 1.2374 | 0.99241 | 1.2423
0.25 | 87.813 | 86.7212 | 88.2082 | 1.2381 | 0.99313 | 1.2431
0.25417 | 87.8134 | 86.7242 | 88.2121 | 1.2389 | 0.99382 | 1.2439
0.25833 | 87.8146 | 86.7271 | 88.2159 | 1.2396 | 0.9945 | 1.2446
0.2625 | 87.8168 | 86.7302 | 88.22 | 1.2403 | 0.99517 | 1.2454
0.26667 | 87.8177 | 86.7332 | 88.2239 | 1.241 | 0.99582 | 1.2461
0.27083 | 87.8194 | 86.7356 | 88.2271 | 1.2416 | 0.99645 | 1.2469
0.275 | 87.8194 | 86.738 | 88.2302 | 1.2423 | 0.99707 | 1.2476
0.27917 | 87.8204 | 86.7406 | 88.2336 | 1.2429 | 0.99767 | 1.2482
0.28333 | 87.8222 | 86.743 | 88.2368 | 1.2435 | 0.99825 | 1.2489
0.2875 | 87.8225 | 86.7454 | 88.2401 | 1.2441 | 0.99882 | 1.2496
0.29167 | 87.8244 | 86.7478 | 88.2432 | 1.2447 | 0.99938 | 1.2502
0.29583 | 87.8256 | 86.7499 | 88.246 | 1.2453 | 0.99993 | 1.2508
0.3 | 87.8252 | 86.7519 | 88.2487 | 1.2459 | 1.0005 | 1.2514
0.30417 | 87.827 | 86.754 | 88.2515 | 1.2464 | 1.001 | 1.252
0.30833 | 87.8283 | 86.7561 | 88.2542 | 1.2469 | 1.0015 | 1.2526
0.3125 | 87.8278 | 86.758 | 88.2569 | 1.2475 | 1.002 | 1.2531
0.31667 | 87.8297 | 86.7599 | 88.2594 | 1.248 | 1.0025 | 1.2537
0.32083 | 87.8309 | 86.7616 | 88.2618 | 1.2485 | 1.0029 | 1.2542
0.325 | 87.8301 | 86.7634 | 88.2642 | 1.249 | 1.0034 | 1.2548
0.32917 | 87.8317 | 86.7651 | 88.2665 | 1.2494 | 1.0038 | 1.2553
0.33333 | 87.833 | 86.7667 | 88.2688 | 1.2499 | 1.0043 | 1.2558
0.3375 | 87.8321 | 86.7683 | 88.271 | 1.2504 | 1.0047 | 1.2563
0.34167 | 87.8336 | 86.7699 | 88.2731 | 1.2508 | 1.0051 | 1.2567
0.34583 | 87.8348 | 86.7713 | 88.2751 | 1.2512 | 1.0055 | 1.2572
0.35 | 87.8338 | 86.7728 | 88.2771 | 1.2516 | 1.0059 | 1.2577
0.35417 | 87.8365 | 86.7742 | 88.2791 | 1.2521 | 1.0063 | 1.2581
0.35833 | 87.8367 | 86.7755 | 88.281 | 1.2525 | 1.0067 | 1.2586
0.3625 | 87.8371 | 86.7768 | 88.2828 | 1.2529 | 1.007 | 1.259
0.36667 | 87.8373 | 86.7781 | 88.2846 | 1.2533 | 1.0074 | 1.2594
0.37083 | 87.8375 | 86.7793 | 88.2863 | 1.2536 | 1.0078 | 1.2598
0.375 | 87.8381 | 86.7805 | 88.288 | 1.254 | 1.0081 | 1.2602
0.37917 | 87.8392 | 86.7817 | 88.2896 | 1.2544 | 1.0084 | 1.2606
0.38333 | 87.8394 | 86.7828 | 88.2912 | 1.2547 | 1.0088 | 1.261
0.3875 | 87.84 | 86.7839 | 88.2928 | 1.2551 | 1.0091 | 1.2613
0.39167 | 87.8388 | 86.7849 | 88.2943 | 1.2554 | 1.0094 | 1.2617
0.39583 | 87.8402 | 86.7859 | 88.2957 | 1.2557 | 1.0097 | 1.2621
0.4 | 87.8404 | 86.7869 | 88.2971 | 1.256 | 1.01 | 1.2624
0.40417 | 87.841 | 86.7879 | 88.2985 | 1.2564 | 1.0103 | 1.2628
0.40833 | 87.8408 | 86.7888 | 88.2998 | 1.2567 | 1.0106 | 1.2631
0.4125 | 87.8418 | 86.7897 | 88.3011 | 1.257 | 1.0109 | 1.2634
0.41667 | 87.8413 | 86.7906 | 88.3024 | 1.2573 | 1.0111 | 1.2637
0.42083 | 87.8419 | 86.7914 | 88.3036 | 1.2576 | 1.0114 | 1.2641
0.425 | 87.8431 | 86.7922 | 88.3048 | 1.2578 | 1.0117 | 1.2644
0.42917 | 87.8418 | 86.793 | 88.306 | 1.2581 | 1.0119 | 1.2647
0.43333 | 87.8422 | 86.7937 | 88.3072 | 1.2584 | 1.0122 | 1.265
0.4375 | 87.843 | 86.7945 | 88.3083 | 1.2586 | 1.0124 | 1.2653
0.44167 | 87.8431 | 86.7952 | 88.3094 | 1.2589 | 1.0127 | 1.2655
0.44583 | 87.8427 | 86.7959 | 88.3104 | 1.2592 | 1.0129 | 1.2658
0.45 | 87.8447 | 86.7966 | 88.3113 | 1.2594 | 1.0131 | 1.2661
0.45417 | 87.8439 | 86.7972 | 88.3123 | 1.2596 | 1.0134 | 1.2663
0.45833 | 87.8437 | 86.7979 | 88.3133 | 1.2599 | 1.0136 | 1.2666
0.4625 | 87.845 | 86.7985 | 88.3142 | 1.2601 | 1.0138 | 1.2669
0.46667 | 87.8437 | 86.7991 | 88.3151 | 1.2603 | 1.014 | 1.2671
0.47083 | 87.8436 | 86.7997 | 88.316 | 1.2606 | 1.0142 | 1.2674
0.475 | 87.8443 | 86.8002 | 88.3168 | 1.2608 | 1.0144 | 1.2676
0.47917 | 87.8444 | 86.8008 | 88.3176 | 1.261 | 1.0146 | 1.2678
0.48333 | 87.8452 | 86.8013 | 88.3184 | 1.2612 | 1.0148 | 1.2681
0.4875 | 87.8461 | 86.8018 | 88.3192 | 1.2614 | 1.015 | 1.2683
0.49167 | 87.8452 | 86.8023 | 88.32 | 1.2616 | 1.0152 | 1.2685
0.49583 | 87.8449 | 86.8028 | 88.3207 | 1.2618 | 1.0154 | 1.2687
0.5 | 87.845 | 86.8032 | 88.3215 | 1.262 | 1.0156 | 1.2689
0.50417 | 87.8452 | 86.8037 | 88.3222 | 1.2622 | 1.0157 | 1.2691
0.50833 | 87.8463 | 86.8041 | 88.3229 | 1.2624 | 1.0159 | 1.2693
0.5125 | 87.8457 | 86.8045 | 88.3235 | 1.2626 | 1.0161 | 1.2695
0.51667 | 87.8453 | 86.805 | 88.3242 | 1.2628 | 1.0163 | 1.2697
0.52083 | 87.8452 | 86.8054 | 88.3248 | 1.2629 | 1.0164 | 1.2699
0.525 | 87.8452 | 86.8057 | 88.3254 | 1.2631 | 1.0166 | 1.2701
0.52917 | 87.8461 | 86.8061 | 88.326 | 1.2633 | 1.0167 | 1.2703
0.53333 | 87.8469 | 86.8065 | 88.3266 | 1.2635 | 1.0169 | 1.2705
0.5375 | 87.8458 | 86.8068 | 88.3272 | 1.2636 | 1.017 | 1.2707
0.54167 | 87.8468 | 86.8072 | 88.3278 | 1.2638 | 1.0172 | 1.2708
0.54583 | 87.8461 | 86.8075 | 88.3283 | 1.2639 | 1.0173 | 1.271
0.55 | 87.8458 | 86.8078 | 88.3288 | 1.2641 | 1.0175 | 1.2712
0.55417 | 87.8467 | 86.8082 | 88.3293 | 1.2642 | 1.0176 | 1.2714
0.55833 | 87.8467 | 86.8085 | 88.3298 | 1.2644 | 1.0178 | 1.2715
0.5625 | 87.8456 | 86.8088 | 88.3303 | 1.2645 | 1.0179 | 1.2717
0.56667 | 87.8471 | 86.809 | 88.3308 | 1.2647 | 1.018 | 1.2718
0.57083 | 87.8463 | 86.8093 | 88.3313 | 1.2648 | 1.0181 | 1.272
0.575 | 87.8457 | 86.8096 | 88.3317 | 1.265 | 1.0183 | 1.2721
0.57917 | 87.8464 | 86.8099 | 88.3321 | 1.2651 | 1.0184 | 1.2723
0.58333 | 87.8463 | 86.8101 | 88.3326 | 1.2652 | 1.0185 | 1.2724
0.5875 | 87.845 | 86.8104 | 88.333 | 1.2653 | 1.0186 | 1.2726
0.59167 | 87.8463 | 86.8106 | 88.3334 | 1.2655 | 1.0188 | 1.2727
0.59583 | 87.8455 | 86.8108 | 88.3338 | 1.2656 | 1.0189 | 1.2728
0.6 | 87.8463 | 86.8111 | 88.3342 | 1.2657 | 1.019 | 1.273
0.60417 | 87.8463 | 86.8113 | 88.3346 | 1.2658 | 1.0191 | 1.2731
0.60833 | 87.8472 | 86.8115 | 88.3349 | 1.266 | 1.0192 | 1.2732
0.6125 | 87.8456 | 86.8117 | 88.3353 | 1.2661 | 1.0193 | 1.2734
0.61667 | 87.847 | 86.8119 | 88.3356 | 1.2662 | 1.0194 | 1.2735
0.62083 | 87.8458 | 86.8121 | 88.336 | 1.2663 | 1.0195 | 1.2736
0.625 | 87.8458 | 86.8123 | 88.3363 | 1.2664 | 1.0196 | 1.2738
0.62917 | 87.8459 | 86.8125 | 88.3367 | 1.2665 | 1.0197 | 1.2739
0.63333 | 87.8462 | 86.8127 | 88.337 | 1.2666 | 1.0198 | 1.274
0.6375 | 87.8459 | 86.8128 | 88.3373 | 1.2667 | 1.0199 | 1.2741
0.64167 | 87.847 | 86.813 | 88.3376 | 1.2669 | 1.02 | 1.2742
0.64583 | 87.8467 | 86.8132 | 88.3379 | 1.267 | 1.0201 | 1.2743
0.65 | 87.846 | 86.8133 | 88.3382 | 1.2671 | 1.0202 | 1.2744
0.65417 | 87.8462 | 86.8135 | 88.3384 | 1.2672 | 1.0203 | 1.2746
0.65833 | 87.8461 | 86.8136 | 88.3387 | 1.2673 | 1.0204 | 1.2747
0.6625 | 87.8464 | 86.8138 | 88.339 | 1.2674 | 1.0205 | 1.2748
0.66667 | 87.847 | 86.8139 | 88.3392 | 1.2675 | 1.0206 | 1.2749
0.67083 | 87.8458 | 86.8141 | 88.3395 | 1.2675 | 1.0207 | 1.275
0.675 | 87.8466 | 86.8142 | 88.3397 | 1.2676 | 1.0207 | 1.2751
0.67917 | 87.8458 | 86.8143 | 88.34 | 1.2677 | 1.0208 | 1.2752
0.68333 | 87.8465 | 86.8144 | 88.3402 | 1.2678 | 1.0209 | 1.2753
0.6875 | 87.8466 | 86.8146 | 88.3405 | 1.2679 | 1.021 | 1.2754
0.69167 | 87.8459 | 86.8147 | 88.3407 | 1.268 | 1.0211 | 1.2755
0.69583 | 87.846 | 86.8148 | 88.3409 | 1.2681 | 1.0211 | 1.2755
0.7 | 87.8457 | 86.8149 | 88.3411 | 1.2681 | 1.0212 | 1.2756
0.70417 | 87.8459 | 86.815 | 88.3413 | 1.2682 | 1.0213 | 1.2757
0.70833 | 87.8464 | 86.8151 | 88.3415 | 1.2683 | 1.0214 | 1.2758
0.7125 | 87.8465 | 86.8152 | 88.3417 | 1.2684 | 1.0214 | 1.2759
0.71667 | 87.8453 | 86.8153 | 88.3419 | 1.2685 | 1.0215 | 1.276
0.72083 | 87.8459 | 86.8154 | 88.3421 | 1.2685 | 1.0216 | 1.2761
0.725 | 87.8451 | 86.8155 | 88.3423 | 1.2686 | 1.0216 | 1.2761
0.72917 | 87.8457 | 86.8156 | 88.3425 | 1.2687 | 1.0217 | 1.2762
0.73333 | 87.8457 | 86.8157 | 88.3427 | 1.2688 | 1.0218 | 1.2763
0.7375 | 87.8464 | 86.8158 | 88.3429 | 1.2688 | 1.0218 | 1.2764
0.74167 | 87.8447 | 86.8159 | 88.343 | 1.2689 | 1.0219 | 1.2765
0.74583 | 87.8457 | 86.816 | 88.3432 | 1.269 | 1.022 | 1.2765
0.75 | 87.8444 | 86.816 | 88.3434 | 1.269 | 1.022 | 1.2766
0.75417 | 87.8454 | 86.8161 | 88.3435 | 1.2691 | 1.0221 | 1.2767
0.75833 | 87.8449 | 86.8162 | 88.3437 | 1.2692 | 1.0222 | 1.2768
0.7625 | 87.846 | 86.8163 | 88.3438 | 1.2692 | 1.0222 | 1.2768
0.76667 | 87.8452 | 86.8164 | 88.344 | 1.2693 | 1.0223 | 1.2769
0.77083 | 87.8448 | 86.8164 | 88.3441 | 1.2694 | 1.0223 | 1.277
0.775 | 87.8443 | 86.8165 | 88.3443 | 1.2694 | 1.0224 | 1.277
0.77917 | 87.8445 | 86.8166 | 88.3444 | 1.2695 | 1.0224 | 1.2771
0.78333 | 87.844 | 86.8166 | 88.3445 | 1.2695 | 1.0225 | 1.2772
0.7875 | 87.8449 | 86.8167 | 88.3447 | 1.2696 | 1.0226 | 1.2772
0.79167 | 87.8446 | 86.8167 | 88.3448 | 1.2697 | 1.0226 | 1.2773
0.79583 | 87.8436 | 86.8168 | 88.345 | 1.2697 | 1.0227 | 1.2774
0.8 | 87.8435 | 86.8168 | 88.3451 | 1.2698 | 1.0227 | 1.2774
0.80417 | 87.8445 | 86.8169 | 88.3452 | 1.2698 | 1.0228 | 1.2775
0.80833 | 87.8442 | 86.817 | 88.3453 | 1.2699 | 1.0228 | 1.2776
0.8125 | 87.8456 | 86.817 | 88.3454 | 1.27 | 1.0229 | 1.2776
0.81667 | 87.8453 | 86.817 | 88.3455 | 1.27 | 1.0229 | 1.2777
0.82083 | 87.8443 | 86.8171 | 88.3456 | 1.2701 | 1.023 | 1.2777
0.825 | 87.8444 | 86.8171 | 88.3457 | 1.2701 | 1.023 | 1.2778
0.82917 | 87.8441 | 86.8172 | 88.3459 | 1.2702 | 1.0231 | 1.2779
0.83333 | 87.8443 | 86.8172 | 88.346 | 1.2702 | 1.0231 | 1.2779
0.8375 | 87.8447 | 86.8173 | 88.3461 | 1.2703 | 1.0232 | 1.278
0.84167 | 87.8449 | 86.8173 | 88.3462 | 1.2703 | 1.0232 | 1.278
0.84583 | 87.8436 | 86.8174 | 88.3463 | 1.2704 | 1.0232 | 1.2781
0.85 | 87.844 | 86.8174 | 88.3464 | 1.2704 | 1.0233 | 1.2781
0.85417 | 87.5815 | 86.5659 | 88.0853 | 1.2726 | 1.0254 | 1.2803
0.85833 | 87.3336 | 86.3273 | 87.8373 | 1.2747 | 1.0274 | 1.2824
0.8625 | 87.262 | 86.2618 | 87.7686 | 1.2752 | 1.0279 | 1.283
0.86667 | 87.1903 | 86.1965 | 87.7003 | 1.2758 | 1.0285 | 1.2836
0.87083 | 87.3275 | 86.3331 | 87.8427 | 1.2788 | 1.0314 | 1.2867
0.875 | 87.4567 | 86.463 | 87.9776 | 1.2817 | 1.0342 | 1.2896
0.87917 | 87.3523 | 86.355 | 87.8619 | 1.2835 | 1.036 | 1.2916
0.88333 | 87.2446 | 86.2545 | 87.7542 | 1.2854 | 1.0379 | 1.2936
0.8875 | 87.1318 | 86.1366 | 87.6211 | 1.2881 | 1.0406 | 1.2966
0.89167 | 87.003 | 86.017 | 87.4885 | 1.2909 | 1.0432 | 1.2994
0.89583 | 86.9049 | 85.94 | 87.4002 | 1.2942 | 1.0464 | 1.303
0.9 | 86.818 | 85.8642 | 87.3138 | 1.2975 | 1.0496 | 1.3065
0.90417 | 86.7874 | 85.8527 | 87.2983 | 1.3011 | 1.0532 | 1.3106
0.90833 | 86.7701 | 85.843 | 87.2829 | 1.3048 | 1.0567 | 1.3145
0.9125 | 86.7029 | 85.7826 | 87.2179 | 1.3091 | 1.0609 | 1.3192
0.91667 | 86.6339 | 85.7172 | 87.1506 | 1.3134 | 1.065 | 1.3238
0.92083 | 86.6084 | 85.7045 | 87.144 | 1.3172 | 1.0686 | 1.3279
0.925 | 86.5924 | 85.6876 | 87.1358 | 1.3208 | 1.0721 | 1.3319
0.92917 | 86.6374 | 85.7291 | 87.1936 | 1.325 | 1.0762 | 1.3365
0.93333 | 86.6804 | 85.7719 | 87.2474 | 1.3292 | 1.0803 | 1.341
0.9375 | 86.6367 | 85.7254 | 87.2068 | 1.3332 | 1.0841 | 1.3453
0.94167 | 86.591 | 85.6811 | 87.1668 | 1.3371 | 1.0879 | 1.3495
0.94583 | 86.6077 | 85.7053 | 87.1995 | 1.3405 | 1.0913 | 1.3532
0.95 | 86.6314 | 85.7265 | 87.2291 | 1.3438 | 1.0946 | 1.3568
0.95417 | 86.6578 | 85.7515 | 87.2637 | 1.3477 | 1.0984 | 1.361
0.95833 | 86.683 | 85.779 | 87.297 | 1.3514 | 1.1021 | 1.365
0.9625 | 86.6474 | 85.7465 | 87.2709 | 1.3547 | 1.1053 | 1.3686
0.96667 | 86.6116 | 85.715 | 87.2454 | 1.3579 | 1.1085 | 1.3721
0.97083 | 86.6421 | 85.7489 | 87.2929 | 1.361 | 1.1116 | 1.3756
0.975 | 86.6708 | 85.7795 | 87.3376 | 1.364 | 1.1146 | 1.379
0.97917 | 86.6753 | 85.783 | 87.3508 | 1.3673 | 1.1178 | 1.3826
0.98333 | 86.6786 | 85.7892 | 87.3652 | 1.3705 | 1.121 | 1.3861
0.9875 | 86.6587 | 85.7749 | 87.3591 | 1.3733 | 1.1237 | 1.3892
0.99167 | 86.6428 | 85.7599 | 87.3517 | 1.376 | 1.1263 | 1.3923
0.99583 | 86.6672 | 85.7873 | 87.3908 | 1.3788 | 1.1291 | 1.3954
1 | 86.6919 | 85.8125 | 87.4283 | 1.3815 | 1.1318 | 1.3985
1.0042 | 86.6843 | 85.8063 | 87.43 | 1.3842 | 1.1345 | 1.4015
1.0083 | 86.6797 | 85.8022 | 87.4331 | 1.3869 | 1.1371 | 1.4045
1.0125 | 86.6742 | 85.8006 | 87.4395 | 1.3893 | 1.1394 | 1.4072
1.0167 | 86.6707 | 85.7975 | 87.4437 | 1.3917 | 1.1417 | 1.4098
1.0208 | 86.6864 | 85.8138 | 87.4688 | 1.3941 | 1.1441 | 1.4126
1.025 | 86.7014 | 85.8291 | 87.4934 | 1.3965 | 1.1465 | 1.4153
1.0292 | 86.6933 | 85.8182 | 87.4924 | 1.3988 | 1.1487 | 1.4178
1.0333 | 86.6871 | 85.8063 | 87.4922 | 1.4011 | 1.1508 | 1.4203
1.0375 | 86.6879 | 85.8014 | 87.5027 | 1.4032 | 1.1528 | 1.4227
1.0417 | 86.6904 | 85.7939 | 87.5113 | 1.4053 | 1.1547 | 1.425
1.0458 | 86.6974 | 85.7934 | 87.5254 | 1.4074 | 1.1566 | 1.4274
1.05 | 86.7056 | 85.7941 | 87.5396 | 1.4095 | 1.1585 | 1.4297
1.0542 | 86.7008 | 85.7817 | 87.5396 | 1.4114 | 1.1603 | 1.4318
1.0583 | 86.6959 | 85.7693 | 87.5398 | 1.4134 | 1.162 | 1.434
1.0625 | 86.6985 | 85.7649 | 87.5495 | 1.4152 | 1.1637 | 1.436
1.0667 | 86.702 | 85.7593 | 87.5578 | 1.417 | 1.1653 | 1.4381
1.0708 | 86.7048 | 85.7542 | 87.5651 | 1.4188 | 1.1669 | 1.4401
1.075 | 86.7083 | 85.7498 | 87.5727 | 1.4206 | 1.1685 | 1.442
1.0792 | 86.7066 | 85.7401 | 87.5741 | 1.4223 | 1.17 | 1.4439
1.0833 | 86.7044 | 85.7307 | 87.5753 | 1.424 | 1.1715 | 1.4457
1.0875 | 86.7064 | 85.7264 | 87.5824 | 1.4256 | 1.1729 | 1.4475
1.0917 | 86.7102 | 85.7218 | 87.5887 | 1.4272 | 1.1743 | 1.4493
1.0958 | 86.71 | 85.7158 | 87.5926 | 1.4288 | 1.1757 | 1.451
1.1 | 86.7121 | 85.7103 | 87.5967 | 1.4303 | 1.1771 | 1.4527
1.1042 | 86.7109 | 85.7032 | 87.5986 | 1.4318 | 1.1784 | 1.4543
1.1083 | 86.7093 | 85.6962 | 87.6002 | 1.4332 | 1.1797 | 1.4559
1.1125 | 86.7052 | 85.6869 | 87.5987 | 1.4347 | 1.181 | 1.4575
1.1167 | 86.7014 | 85.6775 | 87.5969 | 1.4361 | 1.1822 | 1.4591
1.1208 | 86.6955 | 85.6669 | 87.5932 | 1.4375 | 1.1835 | 1.4606
1.125 | 86.6919 | 85.6567 | 87.5897 | 1.4389 | 1.1847 | 1.4621
1.1292 | 86.691 | 85.6513 | 87.5916 | 1.4403 | 1.1859 | 1.4637
1.1333 | 86.6907 | 85.6457 | 87.5933 | 1.4416 | 1.1871 | 1.4651
1.1375 | 86.6898 | 85.6398 | 87.5941 | 1.4429 | 1.1882 | 1.4666
1.1417 | 86.6885 | 85.6338 | 87.5947 | 1.4442 | 1.1894 | 1.468
1.1458 | 86.6865 | 85.6273 | 87.5943 | 1.4455 | 1.1905 | 1.4694
1.15 | 86.6852 | 85.621 | 87.5939 | 1.4468 | 1.1916 | 1.4708
1.1542 | 86.6849 | 85.6166 | 87.5954 | 1.448 | 1.1927 | 1.4721
1.1583 | 86.6858 | 85.6121 | 87.5968 | 1.4492 | 1.1938 | 1.4734
1.1625 | 86.6845 | 85.6075 | 87.5978 | 1.4504 | 1.1948 | 1.4747
1.1667 | 86.6852 | 85.603 | 87.5986 | 1.4515 | 1.1958 | 1.476
1.1708 | 86.6834 | 85.5982 | 87.5988 | 1.4526 | 1.1968 | 1.4772
1.175 | 86.6818 | 85.5936 | 87.599 | 1.4538 | 1.1978 | 1.4784
1.1792 | 86.6829 | 85.5897 | 87.5999 | 1.4548 | 1.1987 | 1.4796
1.1833 | 86.6842 | 85.5858 | 87.6007 | 1.4559 | 1.1997 | 1.4807
1.1875 | 86.6824 | 85.582 | 87.6013 | 1.4569 | 1.2006 | 1.4819
1.1917 | 86.6834 | 85.5781 | 87.6018 | 1.458 | 1.2015 | 1.483
1.1958 | 86.6821 | 85.5743 | 87.6019 | 1.4589 | 1.2024 | 1.4841
1.2 | 86.6802 | 85.5705 | 87.602 | 1.4599 | 1.2032 | 1.4851
1.2042 | 86.6815 | 85.5671 | 87.6024 | 1.4609 | 1.2041 | 1.4862
1.2083 | 86.6831 | 85.5637 | 87.6027 | 1.4618 | 1.2049 | 1.4872
1.2125 | 86.6801 | 85.5606 | 87.6031 | 1.4627 | 1.2057 | 1.4882
1.2167 | 86.6821 | 85.5575 | 87.6035 | 1.4636 | 1.2065 | 1.4891
1.2208 | 86.6809 | 85.5545 | 87.6036 | 1.4645 | 1.2072 | 1.4901
1.225 | 86.6793 | 85.5515 | 87.6038 | 1.4654 | 1.208 | 1.491
1.2292 | 86.6814 | 85.5485 | 87.6038 | 1.4662 | 1.2087 | 1.4919
1.2333 | 86.6802 | 85.5455 | 87.6037 | 1.467 | 1.2095 | 1.4928
1.2375 | 86.6789 | 85.5426 | 87.6035 | 1.4678 | 1.2102 | 1.4937
1.2417 | 86.6796 | 85.5398 | 87.6034 | 1.4686 | 1.2109 | 1.4946
1.2458 | 86.679 | 85.537 | 87.6032 | 1.4694 | 1.2115 | 1.4954
1.25 | 86.6793 | 85.5344 | 87.603 | 1.4701 | 1.2122 | 1.4962
1.2542 | 86.679 | 85.5317 | 87.6026 | 1.4709 | 1.2128 | 1.497
1.2583 | 86.6779 | 85.529 | 87.6022 | 1.4716 | 1.2135 | 1.4978
1.2625 | 86.6762 | 85.5265 | 87.6019 | 1.4723 | 1.2141 | 1.4986
1.2667 | 86.6769 | 85.5239 | 87.6015 | 1.473 | 1.2147 | 1.4993
1.2708 | 86.6762 | 85.5214 | 87.601 | 1.4737 | 1.2153 | 1.5001
1.275 | 86.6763 | 85.519 | 87.6005 | 1.4743 | 1.2159 | 1.5008
1.2792 | 86.6757 | 85.5166 | 87.6 | 1.475 | 1.2165 | 1.5015
1.2833 | 86.6745 | 85.5143 | 87.5994 | 1.4756 | 1.217 | 1.5022
1.2875 | 86.6752 | 85.512 | 87.5989 | 1.4763 | 1.2176 | 1.5029
1.2917 | 86.674 | 85.5097 | 87.5983 | 1.4769 | 1.2181 | 1.5035
1.2958 | 86.6745 | 85.5075 | 87.5977 | 1.4775 | 1.2187 | 1.5042
1.3 | 86.6741 | 85.5053 | 87.5971 | 1.4781 | 1.2192 | 1.5048
1.3042 | 86.6721 | 85.5032 | 87.5964 | 1.4787 | 1.2197 | 1.5055
1.3083 | 86.6726 | 85.5011 | 87.5959 | 1.4793 | 1.2202 | 1.5061
1.3125 | 86.6733 | 85.4999 | 87.5963 | 1.4798 | 1.2207 | 1.5067
1.3167 | 86.6732 | 85.4988 | 87.5967 | 1.4803 | 1.2212 | 1.5073
1.3208 | 86.6734 | 85.4977 | 87.597 | 1.4809 | 1.2216 | 1.5078
1.325 | 86.6748 | 85.4966 | 87.5973 | 1.4814 | 1.2221 | 1.5084
1.3292 | 86.6726 | 85.4946 | 87.5965 | 1.4819 | 1.2225 | 1.509
1.3333 | 86.6728 | 85.4927 | 87.5958 | 1.4824 | 1.223 | 1.5095
1.3375 | 86.6733 | 85.4912 | 87.5954 | 1.4829 | 1.2234 | 1.51
1.3417 | 86.6722 | 85.4897 | 87.595 | 1.4833 | 1.2238 | 1.5105
1.3458 | 86.6704 | 85.4882 | 87.5945 | 1.4838 | 1.2242 | 1.511
1.35 | 86.6726 | 85.4867 | 87.594 | 1.4843 | 1.2246 | 1.5115
1.3542 | 86.6708 | 85.4849 | 87.5932 | 1.4847 | 1.225 | 1.512
1.3583 | 86.6714 | 85.4832 | 87.5924 | 1.4852 | 1.2254 | 1.5125
1.3625 | 86.6727 | 85.4817 | 87.5918 | 1.4856 | 1.2258 | 1.5129
1.3667 | 86.6693 | 85.4801 | 87.5911 | 1.486 | 1.2261 | 1.5134
1.3708 | 86.6691 | 85.4786 | 87.5903 | 1.4864 | 1.2265 | 1.5138
1.375 | 86.6689 | 85.4771 | 87.5896 | 1.4868 | 1.2269 | 1.5143
1.3792 | 86.669 | 85.4755 | 87.5888 | 1.4872 | 1.2272 | 1.5147
1.3833 | 86.6684 | 85.474 | 87.588 | 1.4876 | 1.2276 | 1.5151
1.3875 | 86.6695 | 85.4725 | 87.5873 | 1.488 | 1.2279 | 1.5156
1.3917 | 86.6652 | 85.4711 | 87.5865 | 1.4884 | 1.2282 | 1.516
1.3958 | 86.6655 | 85.4697 | 87.588 | 1.4888 | 1.2286 | 1.5163
1.4 | 86.665 | 85.4683 | 87.5872 | 1.4891 | 1.2289 | 1.5167
1.4042 | 86.6641 | 85.4669 | 87.5865 | 1.4895 | 1.2292 | 1.5171
1.4083 | 86.6687 | 85.4654 | 87.5857 | 1.4898 | 1.2295 | 1.5175
1.4125 | 86.6666 | 85.4634 | 87.5819 | 1.4902 | 1.2298 | 1.5179
1.4167 | 86.6639 | 85.4615 | 87.5804 | 1.4905 | 1.2301 | 1.5183
1.4208 | 86.6642 | 85.4596 | 87.5796 | 1.4909 | 1.2304 | 1.5186
1.425 | 86.6586 | 85.4576 | 87.5781 | 1.4912 | 1.2307 | 1.519
1.4292 | 86.6601 | 85.4564 | 87.5773 | 1.4915 | 1.231 | 1.5193
1.4333 | 86.6615 | 85.4551 | 87.5765 | 1.4919 | 1.2313 | 1.5197
1.4375 | 86.6596 | 85.4536 | 87.5748 | 1.4922 | 1.2316 | 1.52
1.4417 | 86.6594 | 85.4522 | 87.5738 | 1.4925 | 1.2319 | 1.5204
1.4458 | 86.6588 | 85.4508 | 87.573 | 1.4928 | 1.2321 | 1.5207
1.45 | 86.6564 | 85.4493 | 87.572 | 1.4931 | 1.2324 | 1.5211
1.4542 | 86.6581 | 85.4482 | 87.5713 | 1.4934 | 1.2327 | 1.5214
1.4583 | 86.657 | 85.447 | 87.5705 | 1.4937 | 1.233 | 1.5217
1.4625 | 86.6557 | 85.4457 | 87.5694 | 1.494 | 1.2332 | 1.522
1.4667 | 86.655 | 85.4445 | 87.5686 | 1.4943 | 1.2335 | 1.5224
1.4708 | 86.6549 | 85.4433 | 87.5678 | 1.4946 | 1.2337 | 1.5227
1.475 | 86.6524 | 85.4422 | 87.567 | 1.4949 | 1.234 | 1.523
1.4792 | 86.6534 | 85.4411 | 87.5662 | 1.4952 | 1.2342 | 1.5233
1.4833 | 86.6525 | 85.4399 | 87.5655 | 1.4955 | 1.2345 | 1.5236
1.4875 | 86.6503 | 85.4389 | 87.5646 | 1.4957 | 1.2347 | 1.5239
1.4917 | 86.6519 | 85.4378 | 87.5639 | 1.496 | 1.2349 | 1.5241
1.4958 | 86.6499 | 85.4367 | 87.5631 | 1.4962 | 1.2352 | 1.5244
1.5 | 86.6498 | 85.4357 | 87.5623 | 1.4965 | 1.2354 | 1.5247
1.5042 | 86.6489 | 85.4346 | 87.5616 | 1.4967 | 1.2356 | 1.525
1.5083 | 86.6502 | 85.4336 | 87.5609 | 1.497 | 1.2358 | 1.5252
1.5125 | 86.6468 | 85.4323 | 87.5597 | 1.4972 | 1.236 | 1.5255
1.5167 | 86.6477 | 85.431 | 87.5586 | 1.4975 | 1.2363 | 1.5258
1.5208 | 86.6465 | 85.4297 | 87.5575 | 1.4977 | 1.2365 | 1.526
1.525 | 86.6439 | 85.4285 | 87.5564 | 1.498 | 1.2367 | 1.5263
1.5292 | 86.6454 | 85.4275 | 87.5558 | 1.4982 | 1.2369 | 1.5265
1.5333 | 86.6438 | 85.4266 | 87.555 | 1.4985 | 1.2371 | 1.5268
1.5375 | 86.6447 | 85.4256 | 87.5542 | 1.4987 | 1.2373 | 1.527
1.5417 | 86.6438 | 85.4246 | 87.5534 | 1.4989 | 1.2375 | 1.5273
1.5458 | 86.6444 | 85.4236 | 87.5526 | 1.4992 | 1.2377 | 1.5275
1.55 | 86.6424 | 85.4226 | 87.5518 | 1.4994 | 1.2379 | 1.5278
1.5542 | 86.6428 | 85.4217 | 87.5511 | 1.4996 | 1.2381 | 1.528
1.5583 | 86.6423 | 85.4208 | 87.5504 | 1.4998 | 1.2382 | 1.5282
1.5625 | 86.6429 | 85.42 | 87.5497 | 1.5 | 1.2384 | 1.5284
1.5667 | 86.6406 | 85.4191 | 87.549 | 1.5002 | 1.2386 | 1.5287
1.5708 | 86.6417 | 85.4182 | 87.5483 | 1.5004 | 1.2388 | 1.5289
1.575 | 86.6401 | 85.4173 | 87.5476 | 1.5006 | 1.239 | 1.5291
1.5792 | 86.6392 | 85.4165 | 87.5469 | 1.5008 | 1.2391 | 1.5293
1.5833 | 86.6407 | 85.4157 | 87.5463 | 1.501 | 1.2393 | 1.5295
1.5875 | 86.6395 | 85.4149 | 87.5456 | 1.5012 | 1.2395 | 1.5297
1.5917 | 86.6376 | 85.4141 | 87.5449 | 1.5014 | 1.2396 | 1.5299
1.5958 | 86.6381 | 85.4133 | 87.5443 | 1.5016 | 1.2398 | 1.5301
1.6 | 86.6373 | 85.4126 | 87.5436 | 1.5018 | 1.24 | 1.5303
1.6042 | 86.6371 | 85.4118 | 87.543 | 1.502 | 1.2401 | 1.5305
1.6083 | 86.6386 | 85.411 | 87.5424 | 1.5021 | 1.2403 | 1.5307
1.6125 | 86.6385 | 85.4105 | 87.542 | 1.5023 | 1.2404 | 1.5309
1.6167 | 86.6372 | 85.41 | 87.5417 | 1.5025 | 1.2406 | 1.5311
1.6208 | 86.6373 | 85.4095 | 87.5413 | 1.5027 | 1.2407 | 1.5313
1.625 | 86.636 | 85.409 | 87.5409 | 1.5028 | 1.2409 | 1.5315
1.6292 | 86.6376 | 85.4083 | 87.5404 | 1.503 | 1.241 | 1.5316
1.6333 | 86.6373 | 85.4094 | 87.5397 | 1.5031 | 1.2412 | 1.5318
1.6375 | 86.6378 | 85.4088 | 87.5392 | 1.5033 | 1.2413 | 1.532
1.6417 | 86.6375 | 85.4082 | 87.5387 | 1.5035 | 1.2414 | 1.5322
1.6458 | 86.6354 | 85.4076 | 87.5382 | 1.5036 | 1.2416 | 1.5323
1.65 | 86.6351 | 85.4053 | 87.5377 | 1.5038 | 1.2417 | 1.5325
1.6542 | 86.6354 | 85.4047 | 87.5371 | 1.5039 | 1.2418 | 1.5326
1.6583 | 86.635 | 85.4047 | 87.5366 | 1.5041 | 1.2419 | 1.5328
1.6625 | 86.6341 | 85.4041 | 87.536 | 1.5042 | 1.2421 | 1.533
1.6667 | 86.6342 | 85.4035 | 87.5355 | 1.5044 | 1.2422 | 1.5331
1.6708 | 86.6313 | 85.4028 | 87.535 | 1.5045 | 1.2423 | 1.5333
1.675 | 86.6313 | 85.4017 | 87.5345 | 1.5046 | 1.2424 | 1.5334
1.6792 | 86.6329 | 85.4011 | 87.5339 | 1.5048 | 1.2426 | 1.5336
1.6833 | 86.6327 | 85.4008 | 87.5334 | 1.5049 | 1.2427 | 1.5337
1.6875 | 86.6338 | 85.4005 | 87.5332 | 1.5051 | 1.2428 | 1.5338
1.6917 | 86.634 | 85.4002 | 87.5331 | 1.5052 | 1.2429 | 1.534
1.6958 | 86.6392 | 85.4069 | 87.5404 | 1.5053 | 1.2429 | 1.5341
1.7 | 86.645 | 85.4132 | 87.5474 | 1.5053 | 1.243 | 1.5341
1.7042 | 86.7393 | 85.5025 | 87.6393 | 1.5047 | 1.2424 | 1.5335
1.7083 | 86.8257 | 85.5876 | 87.7269 | 1.5041 | 1.2418 | 1.5329
1.7125 | 86.9238 | 85.6162 | 87.7556 | 1.5045 | 1.2416 | 1.5327
1.7167 | 86.9528 | 85.645 | 87.7851 | 1.5043 | 1.2414 | 1.5325
1.7208 | 86.9609 | 85.6129 | 87.7509 | 1.5039 | 1.2404 | 1.5315
1.725 | 86.9306 | 85.5829 | 87.7195 | 1.503 | 1.2395 | 1.5306
1.7292 | 86.7339 | 85.4153 | 87.5459 | 1.5042 | 1.2405 | 1.5316
1.7333 | 86.5725 | 85.2559 | 87.3809 | 1.5051 | 1.2415 | 1.5326
1.7375 | 86.5051 | 85.2375 | 87.364 | 1.5041 | 1.2409 | 1.532
1.7417 | 86.4883 | 85.219 | 87.3456 | 1.5035 | 1.2403 | 1.5315
1.7458 | 86.6005 | 85.3539 | 87.4881 | 1.5042 | 1.2415 | 1.5327
1.75 | 86.7349 | 85.4822 | 87.6224 | 1.5053 | 1.2426 | 1.5338
1.7542 | 86.6514 | 85.3305 | 87.4614 | 1.5063 | 1.2433 | 1.5346
1.7583 | 86.5337 | 85.189 | 87.3136 | 1.5072 | 1.244 | 1.5354
1.7625 | 86.393 | 85.0938 | 87.2053 | 1.5076 | 1.2448 | 1.5363
1.7667 | 86.3127 | 84.9987 | 87.0981 | 1.5087 | 1.2456 | 1.5372
1.7708 | 86.2123 | 84.9716 | 87.0616 | 1.5099 | 1.2477 | 1.5394
1.775 | 86.1734 | 84.9443 | 87.0223 | 1.5119 | 1.2496 | 1.5415
1.7792 | 86.1313 | 84.8652 | 86.9297 | 1.5138 | 1.2516 | 1.5439
1.7833 | 86.062 | 84.7916 | 86.843 | 1.5158 | 1.2535 | 1.5461
1.7875 | 85.9683 | 84.712 | 86.7505 | 1.5185 | 1.2561 | 1.5491
1.7917 | 85.8931 | 84.6283 | 86.6563 | 1.5212 | 1.2587 | 1.552
1.7958 | 85.8324 | 84.5943 | 86.6203 | 1.5237 | 1.2613 | 1.5551
1.8 | 85.7988 | 84.5574 | 86.5805 | 1.5264 | 1.2638 | 1.5579
1.8042 | 85.8196 | 84.5555 | 86.5826 | 1.5293 | 1.2667 | 1.5613
1.8083 | 85.827 | 84.5565 | 86.5823 | 1.5324 | 1.2696 | 1.5646
1.8125 | 85.7653 | 84.4895 | 86.5115 | 1.5355 | 1.2727 | 1.5681
1.8167 | 85.7085 | 84.4238 | 86.4407 | 1.5387 | 1.2757 | 1.5714
1.8208 | 85.6912 | 84.4183 | 86.4309 | 1.5413 | 1.2783 | 1.5744
1.825 | 85.6919 | 84.4101 | 86.4176 | 1.544 | 1.2809 | 1.5773
1.8292 | 85.7194 | 84.4253 | 86.4276 | 1.5471 | 1.284 | 1.5809
1.8333 | 85.7437 | 84.4438 | 86.4341 | 1.5503 | 1.2871 | 1.5842
1.8375 | 85.6944 | 84.3903 | 86.3697 | 1.5532 | 1.2899 | 1.5874
1.8417 | 85.6449 | 84.3388 | 86.3067 | 1.556 | 1.2926 | 1.5905
1.8458 | 85.6584 | 84.3555 | 86.3174 | 1.5585 | 1.2952 | 1.5934
1.85 | 85.6737 | 84.3688 | 86.3249 | 1.561 | 1.2977 | 1.5962
1.8542 | 85.6886 | 84.374 | 86.3222 | 1.5639 | 1.3005 | 1.5994
1.8583 | 85.6974 | 84.3828 | 86.3182 | 1.5668 | 1.3033 | 1.6026
1.8625 | 85.6637 | 84.3484 | 86.2721 | 1.5692 | 1.3057 | 1.6053
1.8667 | 85.6295 | 84.3144 | 86.227 | 1.5716 | 1.3081 | 1.6079
1.8708 | 85.6491 | 84.3369 | 86.2427 | 1.574 | 1.3105 | 1.6106
1.875 | 85.6713 | 84.3566 | 86.2558 | 1.5764 | 1.3128 | 1.6132
1.8792 | 85.6689 | 84.3514 | 86.2411 | 1.5789 | 1.3153 | 1.616
1.8833 | 85.6674 | 84.3496 | 86.2269 | 1.5813 | 1.3177 | 1.6187
1.8875 | 85.6476 | 84.3364 | 86.1992 | 1.5834 | 1.3198 | 1.621
1.8917 | 85.6304 | 84.3241 | 86.1716 | 1.5855 | 1.3218 | 1.6233
1.8958 | 85.6452 | 84.3503 | 86.1816 | 1.5877 | 1.3239 | 1.6257
1.9 | 85.6624 | 84.3769 | 86.1898 | 1.5898 | 1.3259 | 1.628
1.9042 | 85.6539 | 84.3749 | 86.1704 | 1.5919 | 1.3278 | 1.6303
1.9083 | 85.6462 | 84.3729 | 86.1523 | 1.594 | 1.3298 | 1.6326
1.9125 | 85.6394 | 84.3718 | 86.1377 | 1.5959 | 1.3315 | 1.6346
1.9167 | 85.6329 | 84.3685 | 86.123 | 1.5977 | 1.3331 | 1.6366
1.9208 | 85.6442 | 84.3842 | 86.1256 | 1.5996 | 1.3348 | 1.6386
1.925 | 85.6529 | 84.4007 | 86.1279 | 1.6015 | 1.3365 | 1.6406
1.9292 | 85.6467 | 84.3965 | 86.1098 | 1.6033 | 1.3381 | 1.6426
1.9333 | 85.6377 | 84.392 | 86.0922 | 1.6051 | 1.3396 | 1.6445
1.9375 | 85.6363 | 84.3935 | 86.0833 | 1.6067 | 1.341 | 1.6462
1.9417 | 85.6352 | 84.3931 | 86.0735 | 1.6084 | 1.3424 | 1.6479
1.9458 | 85.6385 | 84.3996 | 86.0693 | 1.61 | 1.3438 | 1.6497
1.95 | 85.6422 | 84.4071 | 86.0658 | 1.6117 | 1.3452 | 1.6514
1.9542 | 85.6288 | 84.3982 | 86.0449 | 1.6132 | 1.3466 | 1.6531
1.9583 | 85.6184 | 84.3892 | 86.0242 | 1.6148 | 1.3479 | 1.6547
1.9625 | 85.6139 | 84.3878 | 86.0129 | 1.6163 | 1.3492 | 1.6563
1.9667 | 85.6111 | 84.3854 | 86.0014 | 1.6178 | 1.3504 | 1.6578
1.9708 | 85.6141 | 84.3892 | 85.9955 | 1.6193 | 1.3517 | 1.6594
1.975 | 85.6155 | 84.3939 | 85.9905 | 1.6208 | 1.353 | 1.6609
1.9792 | 85.6091 | 84.3899 | 85.9763 | 1.6222 | 1.3542 | 1.6624
1.9833 | 85.6024 | 84.3858 | 85.962 | 1.6236 | 1.3554 | 1.6638
1.9875 | 85.5967 | 84.3823 | 85.9485 | 1.625 | 1.3566 | 1.6653
1.9917 | 85.5922 | 84.3785 | 85.935 | 1.6264 | 1.3577 | 1.6667
1.9958 | 85.5854 | 84.3756 | 85.9219 | 1.6277 | 1.3589 | 1.6681
2 | 85.5822 | 84.3735 | 85.9095 | 1.6291 | 1.36 | 1.6694
2.0042 | 85.5787 | 84.372 | 85.8983 | 1.6304 | 1.3611 | 1.6708
2.0083 | 85.574 | 84.3704 | 85.8872 | 1.6317 | 1.3623 | 1.6721
2.0125 | 85.5717 | 84.3679 | 85.8749 | 1.633 | 1.3634 | 1.6734
2.0167 | 85.5652 | 84.3653 | 85.8627 | 1.6343 | 1.3645 | 1.6747
2.0208 | 85.56 | 84.3625 | 85.85 | 1.6355 | 1.3655 | 1.676
2.025 | 85.555 | 84.3601 | 85.8378 | 1.6368 | 1.3666 | 1.6772
2.0292 | 85.5542 | 84.3598 | 85.8282 | 1.638 | 1.3676 | 1.6785
2.0333 | 85.5526 | 84.3595 | 85.8188 | 1.6392 | 1.3687 | 1.6797
2.0375 | 85.5494 | 84.3586 | 85.8086 | 1.6404 | 1.3697 | 1.6809
2.0417 | 85.5462 | 84.3576 | 85.7986 | 1.6416 | 1.3707 | 1.682
2.0458 | 85.5402 | 84.3563 | 85.7881 | 1.6427 | 1.3717 | 1.6832
2.05 | 85.5377 | 84.3553 | 85.7778 | 1.6439 | 1.3726 | 1.6843
2.0542 | 85.5376 | 84.3556 | 85.7694 | 1.6449 | 1.3736 | 1.6854
2.0583 | 85.537 | 84.3558 | 85.7612 | 1.646 | 1.3745 | 1.6865
2.0625 | 85.5347 | 84.3558 | 85.7524 | 1.6471 | 1.3754 | 1.6875
2.0667 | 85.5333 | 84.3557 | 85.7438 | 1.6482 | 1.3764 | 1.6886
2.0708 | 85.5294 | 84.3551 | 85.7347 | 1.6492 | 1.3772 | 1.6896
2.075 | 85.5262 | 84.3546 | 85.7256 | 1.6502 | 1.3781 | 1.6906
2.0792 | 85.5251 | 84.3548 | 85.7177 | 1.6512 | 1.379 | 1.6915
2.0833 | 85.5242 | 84.355 | 85.7098 | 1.6521 | 1.3798 | 1.6925
2.0875 | 85.5216 | 84.3552 | 85.702 | 1.6531 | 1.3806 | 1.6934
2.0917 | 85.5227 | 84.3555 | 85.6942 | 1.654 | 1.3814 | 1.6943
2.0958 | 85.5198 | 84.3555 | 85.6864 | 1.6549 | 1.3822 | 1.6952
2.1 | 85.5172 | 84.3555 | 85.6786 | 1.6559 | 1.383 | 1.6961
2.1042 | 85.5162 | 84.3557 | 85.6711 | 1.6567 | 1.3838 | 1.697
2.1083 | 85.5129 | 84.3559 | 85.6638 | 1.6576 | 1.3845 | 1.6978
2.1125 | 85.5119 | 84.3562 | 85.6567 | 1.6584 | 1.3853 | 1.6986
2.1167 | 85.5126 | 84.3566 | 85.6497 | 1.6593 | 1.386 | 1.6994
2.1208 | 85.5118 | 84.3569 | 85.6428 | 1.6601 | 1.3867 | 1.7002
2.125 | 85.5099 | 84.3571 | 85.6359 | 1.6609 | 1.3874 | 1.701
2.1292 | 85.509 | 84.3573 | 85.6289 | 1.6617 | 1.3881 | 1.7018
2.1333 | 85.5048 | 84.3574 | 85.6221 | 1.6624 | 1.3887 | 1.7025
2.1375 | 85.5036 | 84.3577 | 85.6155 | 1.6632 | 1.3894 | 1.7032
2.1417 | 85.5025 | 84.3591 | 85.6089 | 1.6639 | 1.3901 | 1.7039
2.1458 | 85.5015 | 84.3608 | 85.6024 | 1.6646 | 1.3907 | 1.7046
2.15 | 85.4998 | 84.3634 | 85.596 | 1.6653 | 1.3913 | 1.7053
2.1542 | 85.4975 | 84.3669 | 85.5906 | 1.666 | 1.392 | 1.706
2.1583 | 85.498 | 84.3699 | 85.5854 | 1.6667 | 1.3926 | 1.7066
2.1625 | 85.4984 | 84.3725 | 85.5799 | 1.6674 | 1.3932 | 1.7073
2.1667 | 85.4953 | 84.3754 | 85.5745 | 1.668 | 1.3938 | 1.7079
2.1708 | 85.4964 | 84.3775 | 85.5681 | 1.6687 | 1.3944 | 1.7085
2.175 | 85.4928 | 84.3799 | 85.5619 | 1.6693 | 1.395 | 1.7091
2.1792 | 85.4897 | 84.3828 | 85.5564 | 1.6699 | 1.3956 | 1.7097
2.1833 | 85.492 | 84.3855 | 85.5511 | 1.6705 | 1.3962 | 1.7103
2.1875 | 85.4919 | 84.3887 | 85.5465 | 1.6711 | 1.3967 | 1.7109
2.1917 | 85.491 | 84.392 | 85.542 | 1.6717 | 1.3973 | 1.7114
2.1958 | 85.4911 | 84.395 | 85.5372 | 1.6722 | 1.3978 | 1.712
2.2 | 85.4888 | 84.3979 | 85.5325 | 1.6728 | 1.3983 | 1.7125
2.2042 | 85.4876 | 84.4003 | 85.5273 | 1.6733 | 1.3988 | 1.713
2.2083 | 85.4855 | 84.4026 | 85.5222 | 1.6739 | 1.3993 | 1.7135
2.2125 | 85.4886 | 84.4058 | 85.5183 | 1.6744 | 1.3998 | 1.714
2.2167 | 85.4856 | 84.409 | 85.5144 | 1.6749 | 1.4003 | 1.7145
2.2208 | 85.4846 | 84.412 | 85.5105 | 1.6754 | 1.4008 | 1.715
2.225 | 85.4858 | 84.4149 | 85.5065 | 1.6759 | 1.4013 | 1.7154
2.2292 | 85.4822 | 84.4169 | 85.5018 | 1.6763 | 1.4017 | 1.7159
2.2333 | 85.4833 | 84.4188 | 85.4971 | 1.6768 | 1.4021 | 1.7163
2.2375 | 85.4831 | 84.4212 | 85.4952 | 1.6773 | 1.4026 | 1.7167
2.2417 | 85.4804 | 84.4234 | 85.4911 | 1.6777 | 1.403 | 1.7171
2.2458 | 85.4794 | 84.4256 | 85.4864 | 1.6782 | 1.4034 | 1.7176
2.25 | 85.4829 | 84.4278 | 85.4823 | 1.6786 | 1.4038 | 1.718
2.2542 | 85.4789 | 84.4289 | 85.4752 | 1.679 | 1.4042 | 1.7184
2.2583 | 85.4785 | 84.43 | 85.4702 | 1.6794 | 1.4046 | 1.7188
2.2625 | 85.4779 | 84.4314 | 85.467 | 1.6798 | 1.405 | 1.7192
2.2667 | 85.4703 | 84.4328 | 85.4625 | 1.6802 | 1.4054 | 1.7195
2.2708 | 85.4698 | 84.4349 | 85.4604 | 1.6806 | 1.4058 | 1.7199
2.275 | 85.4718 | 84.4368 | 85.4567 | 1.681 | 1.4062 | 1.7203
2.2792 | 85.4672 | 84.4382 | 85.452 | 1.6814 | 1.4066 | 1.7207
2.2833 | 85.4718 | 84.4395 | 85.4477 | 1.6818 | 1.4069 | 1.721
2.2875 | 85.4699 | 84.4405 | 85.4419 | 1.6822 | 1.4073 | 1.7214
2.2917 | 85.4637 | 84.4414 | 85.4373 | 1.6825 | 1.4077 | 1.7217
2.2958 | 85.4647 | 84.4426 | 85.4342 | 1.6829 | 1.408 | 1.7221
2.3 | 85.4606 | 84.4437 | 85.43 | 1.6833 | 1.4084 | 1.7224
2.3042 | 85.4589 | 84.4451 | 85.4261 | 1.6836 | 1.4087 | 1.7228
2.3083 | 85.4633 | 84.4465 | 85.4222 | 1.684 | 1.409 | 1.7231
2.3125 | 85.4601 | 84.4475 | 85.4173 | 1.6844 | 1.4094 | 1.7234
2.3167 | 85.457 | 84.4486 | 85.4132 | 1.6847 | 1.4097 | 1.7238
2.3208 | 85.4568 | 84.4498 | 85.41 | 1.6851 | 1.4101 | 1.7241
2.325 | 85.4524 | 84.4508 | 85.4061 | 1.6854 | 1.4104 | 1.7244
2.3292 | 85.4536 | 84.4522 | 85.4026 | 1.6857 | 1.4107 | 1.7247
2.3333 | 85.4535 | 84.4535 | 85.3991 | 1.686 | 1.411 | 1.7251
2.3375 | 85.4523 | 84.4546 | 85.395 | 1.6864 | 1.4113 | 1.7254
2.3417 | 85.4498 | 84.4557 | 85.3914 | 1.6867 | 1.4116 | 1.7257
2.3458 | 85.4508 | 84.4568 | 85.3883 | 1.687 | 1.4119 | 1.726
2.35 | 85.4465 | 84.458 | 85.3848 | 1.6873 | 1.4122 | 1.7263
2.3542 | 85.4497 | 84.4589 | 85.3811 | 1.6876 | 1.4125 | 1.7266
2.3583 | 85.4468 | 84.4597 | 85.3775 | 1.688 | 1.4128 | 1.7268
2.3625 | 85.4458 | 84.4606 | 85.3738 | 1.6882 | 1.4131 | 1.7271
2.3667 | 85.4437 | 84.4615 | 85.3703 | 1.6886 | 1.4134 | 1.7274
2.3708 | 85.4425 | 84.4627 | 85.3673 | 1.6888 | 1.4137 | 1.7277
2.375 | 85.4411 | 84.4639 | 85.3643 | 1.6891 | 1.414 | 1.728
2.3792 | 85.4409 | 84.4649 | 85.3611 | 1.6894 | 1.4142 | 1.7282
2.3833 | 85.4424 | 84.4659 | 85.3579 | 1.6897 | 1.4145 | 1.7285
2.3875 | 85.4391 | 84.4666 | 85.3545 | 1.69 | 1.4148 | 1.7288
2.3917 | 85.4393 | 84.4673 | 85.3511 | 1.6903 | 1.415 | 1.729
2.3958 | 85.4358 | 84.4681 | 85.3479 | 1.6905 | 1.4153 | 1.7293
2.4 | 85.4332 | 84.4689 | 85.3447 | 1.6908 | 1.4156 | 1.7295
2.4042 | 85.4313 | 84.4699 | 85.3419 | 1.6911 | 1.4158 | 1.7298
2.4083 | 85.4337 | 84.4709 | 85.339 | 1.6913 | 1.4161 | 1.73
2.4125 | 85.4308 | 84.4714 | 85.3355 | 1.6916 | 1.4163 | 1.7303
2.4167 | 85.4319 | 84.4719 | 85.3321 | 1.6919 | 1.4166 | 1.7305
2.4208 | 85.429 | 84.4724 | 85.3288 | 1.6922 | 1.4168 | 1.7308
2.425 | 85.4261 | 84.4729 | 85.3256 | 1.6924 | 1.4171 | 1.731
2.4292 | 85.424 | 84.4738 | 85.3228 | 1.6927 | 1.4173 | 1.7313
2.4333 | 85.425 | 84.4747 | 85.3201 | 1.6929 | 1.4175 | 1.7315
2.4375 | 85.4242 | 84.4754 | 85.3172 | 1.6931 | 1.4178 | 1.7317
2.4417 | 85.4241 | 84.4762 | 85.3143 | 1.6934 | 1.418 | 1.732
2.4458 | 85.4244 | 84.4769 | 85.3115 | 1.6937 | 1.4182 | 1.7322
2.45 | 85.4232 | 84.4776 | 85.3087 | 1.6939 | 1.4185 | 1.7324
2.4542 | 85.4205 | 84.4787 | 85.3063 | 1.6941 | 1.4187 | 1.7326
2.4583 | 85.4223 | 84.4797 | 85.304 | 1.6943 | 1.4189 | 1.7328
2.4625 | 85.4197 | 84.4806 | 85.3016 | 1.6946 | 1.4191 | 1.7331
2.4667 | 85.4187 | 84.4815 | 85.2992 | 1.6948 | 1.4194 | 1.7333
2.4708 | 85.4178 | 84.4821 | 85.2966 | 1.695 | 1.4196 | 1.7335
2.475 | 85.4171 | 84.4845 | 85.294 | 1.6952 | 1.4198 | 1.7337
2.4792 | 85.4154 | 84.4853 | 85.2916 | 1.6955 | 1.42 | 1.7339
2.4833 | 85.4179 | 84.4856 | 85.2894 | 1.6957 | 1.4202 | 1.7341
2.4875 | 85.4154 | 84.4865 | 85.2873 | 1.6959 | 1.4204 | 1.7343
2.4917 | 85.4148 | 84.4856 | 85.2851 | 1.6961 | 1.4206 | 1.7345
2.4958 | 85.4136 | 84.4865 | 85.283 | 1.6963 | 1.4207 | 1.7347
2.5 | 85.4126 | 84.4884 | 85.2809 | 1.6965 | 1.4209 | 1.7348
2.5042 | 85.4142 | 84.489 | 85.2787 | 1.6967 | 1.4211 | 1.735
2.5083 | 85.4138 | 84.491 | 85.2765 | 1.6969 | 1.4213 | 1.7352
2.5125 | 85.4142 | 84.4915 | 85.2742 | 1.6971 | 1.4215 | 1.7354
2.5167 | 85.4116 | 84.4916 | 85.272 | 1.6973 | 1.4217 | 1.7356
2.5208 | 85.4121 | 84.4921 | 85.2699 | 1.6975 | 1.4218 | 1.7357
2.525 | 85.4092 | 84.4916 | 85.2677 | 1.6976 | 1.422 | 1.7359
2.5292 | 85.4115 | 84.4922 | 85.2655 | 1.6978 | 1.4222 | 1.7361
2.5333 | 85.4097 | 84.4937 | 85.2635 | 1.698 | 1.4223 | 1.7362
2.5375 | 85.4051 | 84.4921 | 85.2586 | 1.6982 | 1.4225 | 1.7364
2.5417 | 85.4008 | 84.4905 | 85.2539 | 1.6984 | 1.4227 | 1.7366
2.5458 | 85.3945 | 84.4875 | 85.2475 | 1.6986 | 1.4229 | 1.7368
2.55 | 85.3893 | 84.4839 | 85.2413 | 1.6988 | 1.4231 | 1.737
2.5542 | 85.3626 | 84.4579 | 85.2112 | 1.6993 | 1.4235 | 1.7374
2.5583 | 85.3378 | 84.4338 | 85.1824 | 1.6997 | 1.4239 | 1.7378
2.5625 | 85.3279 | 84.4285 | 85.1717 | 1.7 | 1.4242 | 1.7381
2.5667 | 85.3217 | 84.4234 | 85.1612 | 1.7003 | 1.4244 | 1.7383
2.5708 | 85.2758 | 84.4408 | 85.1736 | 1.7012 | 1.4249 | 1.7388
2.575 | 85.2885 | 84.4568 | 85.1847 | 1.7017 | 1.4254 | 1.7392
2.5792 | 85.3603 | 84.5822 | 85.3088 | 1.7014 | 1.4247 | 1.7385
2.5833 | 85.4783 | 84.7011 | 85.4255 | 1.7007 | 1.424 | 1.7378
2.5875 | 85.5637 | 84.7263 | 85.4549 | 1.7013 | 1.4241 | 1.7379
2.5917 | 85.666 | 84.7508 | 85.4833 | 1.7021 | 1.4243 | 1.7381
2.5958 | 85.6731 | 84.6832 | 85.4224 | 1.7012 | 1.4231 | 1.737
2.6 | 85.661 | 84.6189 | 85.3658 | 1.7009 | 1.4219 | 1.736
2.6042 | 85.613 | 84.554 | 85.3021 | 1.7013 | 1.4224 | 1.7366
2.6083 | 85.5223 | 84.493 | 85.2429 | 1.702 | 1.4228 | 1.7371
2.6125 | 85.4864 | 84.5159 | 85.2704 | 1.7014 | 1.422 | 1.7363
2.6167 | 85.4398 | 84.5387 | 85.2959 | 1.7004 | 1.4212 | 1.7355
2.6208 | 85.5791 | 84.6539 | 85.421 | 1.6999 | 1.4213 | 1.7356
2.625 | 85.6677 | 84.7638 | 85.5398 | 1.6998 | 1.4213 | 1.7356
2.6292 | 85.7031 | 84.6277 | 85.4075 | 1.7 | 1.4214 | 1.7358
2.6333 | 85.6313 | 84.5004 | 85.2873 | 1.7005 | 1.4215 | 1.7359
2.6375 | 85.5567 | 84.4505 | 85.2334 | 1.7004 | 1.421 | 1.7354
2.6417 | 85.4726 | 84.4024 | 85.1826 | 1.7 | 1.4205 | 1.735
2.6458 | 85.4033 | 84.4343 | 85.2009 | 1.7001 | 1.4214 | 1.736
2.65 | 85.3652 | 84.4663 | 85.2193 | 1.7005 | 1.4223 | 1.7369
2.6542 | 85.3172 | 84.3562 | 85.0909 | 1.701 | 1.4231 | 1.7378
2.6583 | 85.2127 | 84.2528 | 84.975 | 1.7016 | 1.4239 | 1.7386
2.6625 | 85.132 | 84.1933 | 84.893 | 1.7028 | 1.425 | 1.7399
2.6667 | 85.0675 | 84.1303 | 84.8143 | 1.704 | 1.4261 | 1.7411
2.6708 | 84.9962 | 84.1243 | 84.7855 | 1.7053 | 1.4279 | 1.7429
2.675 | 84.9528 | 84.1171 | 84.7577 | 1.707 | 1.4296 | 1.7446
2.6792 | 84.9513 | 84.0879 | 84.7101 | 1.7087 | 1.4315 | 1.7465
2.6833 | 84.9187 | 84.0621 | 84.6676 | 1.7105 | 1.4333 | 1.7483
2.6875 | 84.852 | 84.0098 | 84.5907 | 1.7128 | 1.4356 | 1.7504
2.6917 | 84.7952 | 83.9564 | 84.5173 | 1.715 | 1.4378 | 1.7525
2.6958 | 84.7526 | 83.9578 | 84.49 | 1.7169 | 1.4399 | 1.7544
2.7 | 84.7352 | 83.9578 | 84.4619 | 1.7189 | 1.442 | 1.7563
2.7042 | 84.7585 | 83.9743 | 84.4494 | 1.7212 | 1.4445 | 1.7586
2.7083 | 84.7678 | 83.9935 | 84.4378 | 1.7236 | 1.447 | 1.7608
2.7125 | 84.7102 | 83.949 | 84.3617 | 1.726 | 1.4495 | 1.763
2.7167 | 84.6558 | 83.905 | 84.2895 | 1.7284 | 1.4519 | 1.7651
2.7208 | 84.6477 | 83.9258 | 84.2793 | 1.7304 | 1.4542 | 1.767
2.725 | 84.6503 | 83.944 | 84.2668 | 1.7324 | 1.4563 | 1.7689
2.7292 | 84.6718 | 83.9674 | 84.2573 | 1.7348 | 1.459 | 1.7712
2.7333 | 84.6841 | 83.9936 | 84.2485 | 1.7373 | 1.4616 | 1.7734
2.7375 | 84.638 | 83.9606 | 84.1841 | 1.7394 | 1.4639 | 1.7754
2.7417 | 84.5929 | 83.9271 | 84.1229 | 1.7415 | 1.4662 | 1.7772
2.7458 | 84.6041 | 83.9563 | 84.1249 | 1.7435 | 1.4685 | 1.7791
2.75 | 84.6181 | 83.9821 | 84.1242 | 1.7454 | 1.4706 | 1.7808
2.7542 | 84.6266 | 83.9956 | 84.1079 | 1.7477 | 1.4731 | 1.7828
2.7583 | 84.6315 | 84.0129 | 84.0933 | 1.7499 | 1.4756 | 1.7848
2.7625 | 84.5996 | 83.9983 | 84.0475 | 1.7517 | 1.4777 | 1.7865
2.7667 | 84.5718 | 83.9849 | 84.0032 | 1.7536 | 1.4797 | 1.7881
2.7708 | 84.583 | 84.0218 | 84.007 | 1.7554 | 1.4818 | 1.7897
2.775 | 84.601 | 84.0575 | 84.0082 | 1.7572 | 1.4838 | 1.7913
2.7792 | 84.5947 | 84.0686 | 83.9859 | 1.7591 | 1.486 | 1.793
2.7833 | 84.5936 | 84.0804 | 83.9652 | 1.761 | 1.488 | 1.7947
2.7875 | 84.5752 | 84.08 | 83.9357 | 1.7627 | 1.4898 | 1.7961
2.7917 | 84.5606 | 84.0783 | 83.9071 | 1.7643 | 1.4915 | 1.7974
2.7958 | 84.5717 | 84.1089 | 83.9076 | 1.7659 | 1.4933 | 1.7989
2.8 | 84.5824 | 84.1396 | 83.9071 | 1.7676 | 1.495 | 1.8003
2.8042 | 84.577 | 84.1474 | 83.8863 | 1.7692 | 1.4967 | 1.8016
2.8083 | 84.5714 | 84.155 | 83.8664 | 1.7708 | 1.4984 | 1.803
2.8125 | 84.5672 | 84.161 | 83.8487 | 1.7722 | 1.4999 | 1.8042
2.8167 | 84.5598 | 84.1651 | 83.8311 | 1.7736 | 1.5013 | 1.8053
2.8208 | 84.5658 | 84.1845 | 83.8261 | 1.7751 | 1.5028 | 1.8065
2.825 | 84.5696 | 84.2045 | 83.8212 | 1.7765 | 1.5042 | 1.8077
2.8292 | 84.5578 | 84.2043 | 83.7977 | 1.7779 | 1.5056 | 1.8089
2.8333 | 84.5473 | 84.2035 | 83.7744 | 1.7793 | 1.507 | 1.81
2.8375 | 84.5446 | 84.209 | 83.7602 | 1.7806 | 1.5083 | 1.811
2.8417 | 84.5406 | 84.213 | 83.746 | 1.7818 | 1.5095 | 1.812
2.8458 | 84.5441 | 84.2277 | 83.7407 | 1.7831 | 1.5108 | 1.8131
2.85 | 84.5475 | 84.2431 | 83.736 | 1.7844 | 1.5121 | 1.8141
2.8542 | 84.5386 | 84.2426 | 83.7166 | 1.7856 | 1.5133 | 1.8151
2.8583 | 84.5291 | 84.2417 | 83.6971 | 1.7868 | 1.5145 | 1.8161
2.8625 | 84.5244 | 84.2438 | 83.6819 | 1.788 | 1.5157 | 1.817
2.8667 | 84.5189 | 84.245 | 83.6667 | 1.7892 | 1.5168 | 1.8179
2.8708 | 84.5149 | 84.2514 | 83.6554 | 1.7904 | 1.518 | 1.8189
2.875 | 84.5148 | 84.2584 | 83.6448 | 1.7915 | 1.5191 | 1.8198
2.8792 | 84.5071 | 84.2601 | 83.6299 | 1.7926 | 1.5202 | 1.8207
2.8833 | 84.502 | 84.2615 | 83.615 | 1.7938 | 1.5213 | 1.8216
2.8875 | 84.4968 | 84.2631 | 83.6008 | 1.7949 | 1.5224 | 1.8224
2.8917 | 84.4881 | 84.2641 | 83.5866 | 1.7959 | 1.5235 | 1.8233
2.8958 | 84.4857 | 84.267 | 83.5734 | 1.7971 | 1.5245 | 1.8241
2.9 | 84.4793 | 84.2703 | 83.5608 | 1.7981 | 1.5256 | 1.825
2.9042 | 84.4775 | 84.2733 | 83.5486 | 1.7992 | 1.5266 | 1.8258
2.9083 | 84.4736 | 84.276 | 83.5366 | 1.8002 | 1.5276 | 1.8266
2.9125 | 84.4685 | 84.2783 | 83.5243 | 1.8012 | 1.5287 | 1.8274
2.9167 | 84.4645 | 84.2804 | 83.5121 | 1.8023 | 1.5297 | 1.8281
2.9208 | 84.4586 | 84.2828 | 83.5 | 1.8032 | 1.5306 | 1.8289
2.925 | 84.4535 | 84.2855 | 83.4882 | 1.8042 | 1.5316 | 1.8297
2.9292 | 84.454 | 84.2891 | 83.478 | 1.8052 | 1.5326 | 1.8304
2.9333 | 84.4497 | 84.2926 | 83.4679 | 1.8062 | 1.5335 | 1.8311
2.9375 | 84.4479 | 84.2955 | 83.4573 | 1.8071 | 1.5345 | 1.8318
2.9417 | 84.4451 | 84.2982 | 83.4468 | 1.808 | 1.5354 | 1.8325
2.9458 | 84.4383 | 84.3007 | 83.4361 | 1.8089 | 1.5363 | 1.8332
2.95 | 84.4354 | 84.3032 | 83.4256 | 1.8098 | 1.5372 | 1.8339
2.9542 | 84.4333 | 84.3068 | 83.4166 | 1.8107 | 1.538 | 1.8345
2.9583 | 84.4331 | 84.3102 | 83.4077 | 1.8116 | 1.5389 | 1.8352
2.9625 | 84.4292 | 84.3134 | 83.3986 | 1.8124 | 1.5397 | 1.8358
2.9667 | 84.4301 | 84.3165 | 83.3896 | 1.8132 | 1.5406 | 1.8364
2.9708 | 84.4246 | 84.3191 | 83.3804 | 1.814 | 1.5414 | 1.837
2.975 | 84.4213 | 84.3217 | 83.3712 | 1.8149 | 1.5422 | 1.8376
2.9792 | 84.4202 | 84.3247 | 83.3629 | 1.8156 | 1.543 | 1.8382
2.9833 | 84.4177 | 84.3277 | 83.3547 | 1.8164 | 1.5438 | 1.8387
2.9875 | 84.4144 | 84.3307 | 83.3466 | 1.8172 | 1.5445 | 1.8393
2.9917 | 84.4165 | 84.3336 | 83.3387 | 1.8179 | 1.5453 | 1.8398
2.9958 | 84.4131 | 84.3363 | 83.3307 | 1.8186 | 1.546 | 1.8404
3 | 84.4105 | 84.3378 | 83.3228 | 1.8193 | 1.5467 | 1.8409
3.0042 | 84.4103 | 84.3388 | 83.3148 | 1.8201 | 1.5475 | 1.8414
3.0083 | 84.4047 | 84.3386 | 83.307 | 1.8207 | 1.5482 | 1.8419
3.0125 | 84.4033 | 84.3385 | 83.2994 | 1.8214 | 1.5489 | 1.8424
3.0167 | 84.4018 | 84.3393 | 83.292 | 1.822 | 1.5496 | 1.8429
3.0208 | 84.4008 | 84.3406 | 83.2849 | 1.8227 | 1.5503 | 1.8433
3.025 | 84.3973 | 84.3422 | 83.2778 | 1.8233 | 1.551 | 1.8438
3.0292 | 84.396 | 84.3444 | 83.2714 | 1.824 | 1.5517 | 1.8442
3.0333 | 84.3941 | 84.3459 | 83.2652 | 1.8246 | 1.5523 | 1.8447
3.0375 | 84.3941 | 84.3468 | 83.2586 | 1.8252 | 1.553 | 1.8451
3.0417 | 84.3913 | 84.3483 | 83.2522 | 1.8258 | 1.5537 | 1.8455
3.0458 | 84.3915 | 84.3493 | 83.2451 | 1.8264 | 1.5543 | 1.846
3.05 | 84.3856 | 84.3507 | 83.2382 | 1.8269 | 1.555 | 1.8464
3.0542 | 84.3834 | 84.3534 | 83.2328 | 1.8275 | 1.5556 | 1.8468
3.0583 | 84.3848 | 84.3558 | 83.2276 | 1.828 | 1.5562 | 1.8472
3.0625 | 84.385 | 84.3582 | 83.2226 | 1.8286 | 1.5568 | 1.8475
3.0667 | 84.3843 | 84.3608 | 83.2177 | 1.8291 | 1.5574 | 1.8479
3.0708 | 84.3825 | 84.3626 | 83.2118 | 1.8296 | 1.558 | 1.8483
3.075 | 84.3811 | 84.3645 | 83.2062 | 1.8301 | 1.5586 | 1.8486
3.0792 | 84.3776 | 84.3666 | 83.2008 | 1.8306 | 1.5592 | 1.849
3.0833 | 84.3787 | 84.3686 | 83.1956 | 1.8311 | 1.5597 | 1.8493
3.0875 | 84.3814 | 84.3712 | 83.1907 | 1.8315 | 1.5603 | 1.8496
3.0917 | 84.3776 | 84.3741 | 83.1865 | 1.832 | 1.5608 | 1.85
3.0958 | 84.3767 | 84.3763 | 83.1821 | 1.8325 | 1.5613 | 1.8503
3.1 | 84.3761 | 84.3787 | 83.1777 | 1.8329 | 1.5619 | 1.8506
3.1042 | 84.3693 | 84.3806 | 83.1734 | 1.8333 | 1.5624 | 1.8509
3.1083 | 84.374 | 84.3824 | 83.1688 | 1.8337 | 1.5629 | 1.8512
3.1125 | 84.3739 | 84.3846 | 83.166 | 1.8341 | 1.5633 | 1.8514
3.1167 | 84.3708 | 84.3868 | 83.1621 | 1.8345 | 1.5638 | 1.8517
3.1208 | 84.3715 | 84.3885 | 83.1568 | 1.8349 | 1.5643 | 1.852
3.125 | 84.3707 | 84.3903 | 83.1526 | 1.8353 | 1.5647 | 1.8523
3.1292 | 84.3664 | 84.3912 | 83.1461 | 1.8357 | 1.5652 | 1.8525
3.1333 | 84.3676 | 84.3921 | 83.1413 | 1.8361 | 1.5656 | 1.8528
3.1375 | 84.3677 | 84.3935 | 83.1391 | 1.8364 | 1.5661 | 1.8531
3.1417 | 84.3607 | 84.395 | 83.1349 | 1.8368 | 1.5665 | 1.8533
3.1458 | 84.3598 | 84.3968 | 83.132 | 1.8371 | 1.5669 | 1.8535
3.15 | 84.363 | 84.3986 | 83.1286 | 1.8375 | 1.5673 | 1.8538
3.1542 | 84.3567 | 84.3994 | 83.1234 | 1.8378 | 1.5677 | 1.854
3.1583 | 84.362 | 84.4002 | 83.1191 | 1.8382 | 1.5681 | 1.8543
3.1625 | 84.3615 | 84.401 | 83.1146 | 1.8385 | 1.5685 | 1.8545
3.1667 | 84.352 | 84.4017 | 83.1104 | 1.8388 | 1.5689 | 1.8547
3.1708 | 84.3525 | 84.4028 | 83.1075 | 1.8392 | 1.5693 | 1.8549
3.175 | 84.3516 | 84.4038 | 83.1037 | 1.8394 | 1.5697 | 1.8552
3.1792 | 84.3461 | 84.4047 | 83.0995 | 1.8398 | 1.5701 | 1.8554
3.1833 | 84.3542 | 84.4056 | 83.0956 | 1.8401 | 1.5704 | 1.8556
3.1875 | 84.3509 | 84.4062 | 83.0909 | 1.8404 | 1.5708 | 1.8558
3.1917 | 84.3447 | 84.4068 | 83.0869 | 1.8407 | 1.5712 | 1.856
3.1958 | 84.3443 | 84.4076 | 83.0839 | 1.841 | 1.5715 | 1.8562
3.2 | 84.3422 | 84.4083 | 83.0803 | 1.8413 | 1.5719 | 1.8565
3.2042 | 84.3407 | 84.4094 | 83.0768 | 1.8416 | 1.5722 | 1.8567
3.2083 | 84.3451 | 84.4104 | 83.0734 | 1.8419 | 1.5726 | 1.8569
3.2125 | 84.3425 | 84.4111 | 83.0693 | 1.8422 | 1.5729 | 1.8571
3.2167 | 84.3376 | 84.4119 | 83.0659 | 1.8425 | 1.5732 | 1.8573
3.2208 | 84.337 | 84.4126 | 83.063 | 1.8428 | 1.5736 | 1.8575
3.225 | 84.3336 | 84.4134 | 83.0595 | 1.843 | 1.5739 | 1.8576
3.2292 | 84.3354 | 84.414 | 83.0561 | 1.8433 | 1.5742 | 1.8578
3.2333 | 84.3357 | 84.4146 | 83.0527 | 1.8436 | 1.5745 | 1.858
3.2375 | 84.3349 | 84.4153 | 83.0491 | 1.8438 | 1.5748 | 1.8582
3.2417 | 84.3296 | 84.4159 | 83.0458 | 1.8441 | 1.5752 | 1.8584
3.2458 | 84.3299 | 84.4168 | 83.043 | 1.8444 | 1.5755 | 1.8586
3.25 | 84.3254 | 84.4177 | 83.0401 | 1.8446 | 1.5758 | 1.8587
3.2542 | 84.3278 | 84.418 | 83.0366 | 1.8449 | 1.5761 | 1.8589
3.2583 | 84.3279 | 84.4183 | 83.0332 | 1.8451 | 1.5764 | 1.8591
3.2625 | 84.3264 | 84.4185 | 83.0295 | 1.8453 | 1.5767 | 1.8593
3.2667 | 84.3245 | 84.4187 | 83.0261 | 1.8456 | 1.5769 | 1.8594
3.2708 | 84.322 | 84.4195 | 83.0233 | 1.8458 | 1.5772 | 1.8596
3.275 | 84.318 | 84.4202 | 83.0204 | 1.8461 | 1.5775 | 1.8598
3.2792 | 84.318 | 84.4207 | 83.0174 | 1.8463 | 1.5778 | 1.86
3.2833 | 84.3183 | 84.4212 | 83.0144 | 1.8466 | 1.5781 | 1.8601
3.2875 | 84.3173 | 84.4213 | 83.0109 | 1.8468 | 1.5784 | 1.8603
3.2917 | 84.3175 | 84.4214 | 83.0076 | 1.847 | 1.5786 | 1.8604
3.2958 | 84.3147 | 84.4218 | 83.0046 | 1.8473 | 1.5789 | 1.8606
3.3 | 84.3094 | 84.422 | 83.0015 | 1.8475 | 1.5792 | 1.8608
3.3042 | 84.3095 | 84.4225 | 82.9986 | 1.8477 | 1.5794 | 1.8609
3.3083 | 84.308 | 84.4231 | 82.9958 | 1.8479 | 1.5797 | 1.8611
3.3125 | 84.3097 | 84.4233 | 82.9928 | 1.8482 | 1.58 | 1.8612
3.3167 | 84.3097 | 84.4236 | 82.9898 | 1.8484 | 1.5802 | 1.8614
3.3208 | 84.3093 | 84.424 | 82.9869 | 1.8486 | 1.5805 | 1.8616
3.325 | 84.3054 | 84.4238 | 82.9841 | 1.8489 | 1.5807 | 1.8617
3.3292 | 84.3054 | 84.4246 | 82.9817 | 1.8491 | 1.581 | 1.8619
3.3333 | 84.3034 | 84.4255 | 82.9793 | 1.8493 | 1.5812 | 1.862
3.3375 | 84.3037 | 84.426 | 82.9766 | 1.8495 | 1.5815 | 1.8621
3.3417 | 84.3025 | 84.4269 | 82.974 | 1.8497 | 1.5817 | 1.8623
3.3458 | 84.2999 | 84.4273 | 82.9713 | 1.8499 | 1.582 | 1.8624
3.35 | 84.2992 | 84.4287 | 82.9686 | 1.8501 | 1.5822 | 1.8626
3.3542 | 84.2965 | 84.4293 | 82.9661 | 1.8503 | 1.5824 | 1.8627
3.3583 | 84.2976 | 84.4289 | 82.9636 | 1.8505 | 1.5827 | 1.8629
3.3625 | 84.295 | 84.4294 | 82.9612 | 1.8507 | 1.5829 | 1.863
3.3667 | 84.2958 | 84.4286 | 82.9588 | 1.8509 | 1.5831 | 1.8631
3.3708 | 84.2926 | 84.4293 | 82.9566 | 1.8511 | 1.5833 | 1.8633
3.375 | 84.2947 | 84.4316 | 82.9544 | 1.8513 | 1.5835 | 1.8634
3.3792 | 84.293 | 84.4322 | 82.9522 | 1.8515 | 1.5838 | 1.8635
3.3833 | 84.2947 | 84.4334 | 82.9501 | 1.8517 | 1.584 | 1.8636
3.3875 | 84.293 | 84.4339 | 82.9479 | 1.8519 | 1.5842 | 1.8638
3.3917 | 84.292 | 84.4335 | 82.9457 | 1.852 | 1.5844 | 1.8639
3.3958 | 84.292 | 84.4346 | 82.9439 | 1.8522 | 1.5846 | 1.864
3.4 | 84.2918 | 84.4355 | 82.9422 | 1.8523 | 1.5847 | 1.8641
3.4042 | 84.3001 | 84.4449 | 82.9487 | 1.8524 | 1.5849 | 1.8642
3.4083 | 84.3081 | 84.4548 | 82.9549 | 1.8525 | 1.585 | 1.8642
3.4125 | 84.3053 | 84.4539 | 82.9506 | 1.8527 | 1.5852 | 1.8643
3.4167 | 84.299 | 84.4527 | 82.9468 | 1.8529 | 1.5854 | 1.8645
3.4208 | 84.3088 | 84.444 | 82.9371 | 1.8528 | 1.5855 | 1.8645
3.425 | 84.2977 | 84.435 | 82.9278 | 1.853 | 1.5856 | 1.8646
3.4292 | 84.2525 | 84.3728 | 82.8648 | 1.8535 | 1.5863 | 1.8652
3.4333 | 84.1938 | 84.3142 | 82.8048 | 1.8542 | 1.587 | 1.8659
3.4375 | 84.1601 | 84.3013 | 82.7853 | 1.8543 | 1.5873 | 1.866
3.4417 | 84.1445 | 84.288 | 82.7654 | 1.8546 | 1.5875 | 1.8662
3.4458 | 84.1015 | 84.3232 | 82.7848 | 1.8558 | 1.5885 | 1.867
3.45 | 84.0664 | 84.3561 | 82.8024 | 1.8572 | 1.5893 | 1.8678
3.4542 | 84.1259 | 84.4756 | 82.9034 | 1.857 | 1.5887 | 1.8671
3.4583 | 84.1698 | 84.5903 | 82.9999 | 1.857 | 1.5882 | 1.8665
3.4625 | 84.2445 | 84.6043 | 83.0098 | 1.8578 | 1.5887 | 1.867
3.4667 | 84.3259 | 84.6182 | 83.0207 | 1.8587 | 1.5892 | 1.8675
3.4708 | 84.3051 | 84.5304 | 82.9399 | 1.8587 | 1.5883 | 1.8668
3.475 | 84.3205 | 84.4462 | 82.8634 | 1.8583 | 1.5875 | 1.8662
3.4792 | 84.2856 | 84.468 | 82.8832 | 1.8586 | 1.5878 | 1.8666
3.4833 | 84.3072 | 84.4877 | 82.8992 | 1.859 | 1.588 | 1.8669
3.4875 | 84.2508 | 84.5301 | 82.9371 | 1.8589 | 1.5875 | 1.8665
3.4917 | 84.2448 | 84.5727 | 82.9741 | 1.8587 | 1.5871 | 1.8661
3.4958 | 84.3259 | 84.644 | 83.0561 | 1.8584 | 1.5865 | 1.8657
3.5 | 84.4289 | 84.7123 | 83.1349 | 1.8579 | 1.586 | 1.8653
3.5042 | 84.5339 | 84.625 | 83.0703 | 1.8581 | 1.5859 | 1.8653
3.5083 | 84.5658 | 84.5423 | 83.0101 | 1.8581 | 1.5858 | 1.8653
3.5125 | 84.578 | 84.5287 | 83.0086 | 1.8581 | 1.5848 | 1.8643
3.5167 | 84.5704 | 84.5179 | 83.0073 | 1.8573 | 1.5838 | 1.8635
3.5208 | 84.5373 | 84.5743 | 83.0668 | 1.8569 | 1.584 | 1.8636
3.525 | 84.5433 | 84.6295 | 83.1228 | 1.8567 | 1.5841 | 1.8637
3.5292 | 84.5366 | 84.5033 | 83.0138 | 1.8566 | 1.5843 | 1.8638
3.5333 | 84.4668 | 84.3831 | 82.914 | 1.8565 | 1.5844 | 1.8638
3.5375 | 84.4182 | 84.3373 | 82.8768 | 1.8568 | 1.5845 | 1.8638
3.5417 | 84.3595 | 84.2884 | 82.839 | 1.8568 | 1.5845 | 1.8638
3.5458 | 84.2626 | 84.3011 | 82.8485 | 1.8569 | 1.5856 | 1.8646
3.55 | 84.19 | 84.3117 | 82.8559 | 1.8572 | 1.5866 | 1.8653
3.5542 | 84.161 | 84.2351 | 82.7912 | 1.8575 | 1.5876 | 1.8659
3.5583 | 84.0975 | 84.1625 | 82.7331 | 1.8579 | 1.5887 | 1.8665
3.5625 | 84.0521 | 84.1097 | 82.6851 | 1.8591 | 1.5901 | 1.8674
3.5667 | 84.013 | 84.0538 | 82.6373 | 1.8602 | 1.5914 | 1.8682
3.5708 | 83.9448 | 84.0527 | 82.6253 | 1.8612 | 1.5931 | 1.8692
3.575 | 83.9096 | 84.0497 | 82.6112 | 1.8624 | 1.5947 | 1.87
3.5792 | 83.9159 | 84.0313 | 82.5885 | 1.8637 | 1.5967 | 1.8711
3.5833 | 83.9029 | 84.0157 | 82.5678 | 1.8651 | 1.5986 | 1.8722
3.5875 | 83.8506 | 83.9642 | 82.5101 | 1.8668 | 1.6006 | 1.8734
3.5917 | 83.8035 | 83.912 | 82.4547 | 1.8685 | 1.6027 | 1.8745
3.5958 | 83.7732 | 83.9216 | 82.4455 | 1.8698 | 1.6047 | 1.8755
3.6 | 83.7621 | 83.9287 | 82.4339 | 1.8713 | 1.6066 | 1.8764
3.6042 | 83.7812 | 83.9393 | 82.4271 | 1.8731 | 1.609 | 1.8777
3.6083 | 83.7887 | 83.9521 | 82.4206 | 1.8749 | 1.6113 | 1.8789
3.6125 | 83.7375 | 83.906 | 82.3627 | 1.8766 | 1.6135 | 1.88
3.6167 | 83.6911 | 83.8589 | 82.308 | 1.8784 | 1.6157 | 1.8811
3.6208 | 83.6883 | 83.8769 | 82.309 | 1.8798 | 1.6178 | 1.8821
3.625 | 83.6926 | 83.891 | 82.307 | 1.8813 | 1.6199 | 1.883
3.6292 | 83.7098 | 83.9025 | 82.2998 | 1.8831 | 1.6224 | 1.8842
3.6333 | 83.7176 | 83.9178 | 82.2933 | 1.8849 | 1.6248 | 1.8854
3.6375 | 83.6789 | 83.8865 | 82.2458 | 1.8865 | 1.627 | 1.8864
3.6417 | 83.6398 | 83.8568 | 82.2011 | 1.8881 | 1.6291 | 1.8873
3.6458 | 83.6476 | 83.8867 | 82.2071 | 1.8894 | 1.6312 | 1.8882
3.65 | 83.6596 | 83.914 | 82.2095 | 1.8909 | 1.6332 | 1.889
3.6542 | 83.6607 | 83.9244 | 82.1957 | 1.8926 | 1.6355 | 1.8901
3.6583 | 83.6648 | 83.9368 | 82.183 | 1.8942 | 1.6377 | 1.8912
3.6625 | 83.6367 | 83.9222 | 82.1493 | 1.8956 | 1.6396 | 1.892
3.6667 | 83.6131 | 83.9077 | 82.1175 | 1.897 | 1.6415 | 1.8928
3.6708 | 83.6216 | 83.9393 | 82.1232 | 1.8983 | 1.6434 | 1.8936
3.675 | 83.6353 | 83.9697 | 82.1266 | 1.8997 | 1.6452 | 1.8944
3.6792 | 83.6321 | 83.9794 | 82.1124 | 1.9011 | 1.6471 | 1.8953
3.6833 | 83.6328 | 83.9897 | 82.0996 | 1.9025 | 1.649 | 1.8961
3.6875 | 83.6187 | 83.9871 | 82.0794 | 1.9037 | 1.6506 | 1.8968
3.6917 | 83.6074 | 83.9834 | 82.0601 | 1.9049 | 1.6522 | 1.8974
3.6958 | 83.6109 | 84.0066 | 82.061 | 1.9061 | 1.6538 | 1.8981
3.7 | 83.6188 | 84.0296 | 82.0609 | 1.9073 | 1.6553 | 1.8988
3.7042 | 83.6108 | 84.0314 | 82.0435 | 1.9085 | 1.6569 | 1.8995
3.7083 | 83.6032 | 84.0333 | 82.0269 | 1.9097 | 1.6584 | 1.9002
3.7125 | 83.5991 | 84.0355 | 82.0144 | 1.9108 | 1.6598 | 1.9008
3.7167 | 83.5924 | 84.0362 | 82.0022 | 1.9118 | 1.6611 | 1.9013
3.7208 | 83.5986 | 84.0547 | 82.003 | 1.9129 | 1.6625 | 1.9019
3.725 | 83.6045 | 84.0735 | 82.0037 | 1.914 | 1.6638 | 1.9025
3.7292 | 83.5946 | 84.072 | 81.9875 | 1.915 | 1.6651 | 1.9031
3.7333 | 83.5849 | 84.0693 | 81.9718 | 1.9161 | 1.6664 | 1.9037
3.7375 | 83.5797 | 84.0687 | 81.961 | 1.917 | 1.6676 | 1.9042
3.7417 | 83.5738 | 84.0662 | 81.9503 | 1.9179 | 1.6687 | 1.9046
3.7458 | 83.576 | 84.0739 | 81.9467 | 1.9189 | 1.6699 | 1.9052
3.75 | 83.5795 | 84.0825 | 81.9432 | 1.9199 | 1.671 | 1.9057
3.7542 | 83.5694 | 84.0796 | 81.9307 | 1.9208 | 1.6721 | 1.9062
3.7583 | 83.5636 | 84.0763 | 81.9183 | 1.9217 | 1.6732 | 1.9067
3.7625 | 83.5569 | 84.0739 | 81.9084 | 1.9226 | 1.6743 | 1.9071
3.7667 | 83.5489 | 84.0706 | 81.8984 | 1.9235 | 1.6753 | 1.9076
3.7708 | 83.55 | 84.0724 | 81.8914 | 1.9244 | 1.6763 | 1.908
3.775 | 83.5454 | 84.0748 | 81.8846 | 1.9252 | 1.6773 | 1.9085
3.7792 | 83.5422 | 84.073 | 81.8751 | 1.9261 | 1.6784 | 1.909
3.7833 | 83.5375 | 84.0708 | 81.8656 | 1.927 | 1.6794 | 1.9094
3.7875 | 83.5315 | 84.0687 | 81.8568 | 1.9278 | 1.6803 | 1.9098
3.7917 | 83.5276 | 84.0662 | 81.848 | 1.9286 | 1.6813 | 1.9103
3.7958 | 83.5238 | 84.0659 | 81.8403 | 1.9295 | 1.6823 | 1.9107
3.8 | 83.5182 | 84.0661 | 81.8329 | 1.9303 | 1.6832 | 1.9111
3.8042 | 83.5177 | 84.0654 | 81.8253 | 1.931 | 1.6841 | 1.9115
3.8083 | 83.5129 | 84.0647 | 81.8179 | 1.9318 | 1.6851 | 1.9119
3.8125 | 83.5093 | 84.0635 | 81.8103 | 1.9326 | 1.686 | 1.9123
3.8167 | 83.5051 | 84.0621 | 81.8028 | 1.9334 | 1.6869 | 1.9127
3.8208 | 83.5017 | 84.0613 | 81.7954 | 1.9341 | 1.6877 | 1.9131
3.825 | 83.4966 | 84.0609 | 81.7882 | 1.9349 | 1.6886 | 1.9134
3.8292 | 83.495 | 84.061 | 81.7819 | 1.9356 | 1.6895 | 1.9138
3.8333 | 83.4955 | 84.0611 | 81.7758 | 1.9363 | 1.6903 | 1.9141
3.8375 | 83.4878 | 84.0607 | 81.7694 | 1.937 | 1.6911 | 1.9145
3.8417 | 83.4879 | 84.0603 | 81.763 | 1.9377 | 1.692 | 1.9148
3.8458 | 83.4828 | 84.0598 | 81.7564 | 1.9384 | 1.6928 | 1.9152
3.85 | 83.4779 | 84.0597 | 81.75 | 1.9391 | 1.6935 | 1.9155
3.8542 | 83.4775 | 84.0606 | 81.7445 | 1.9397 | 1.6943 | 1.9158
3.8583 | 83.4771 | 84.0617 | 81.7391 | 1.9404 | 1.6951 | 1.9161
3.8625 | 83.47 | 84.0626 | 81.7336 | 1.941 | 1.6958 | 1.9165
3.8667 | 83.4738 | 84.0633 | 81.7281 | 1.9416 | 1.6965 | 1.9168
3.8708 | 83.47 | 84.0635 | 81.7226 | 1.9422 | 1.6973 | 1.9171
3.875 | 83.4677 | 84.0628 | 81.717 | 1.9428 | 1.698 | 1.9173
3.8792 | 83.4679 | 84.0617 | 81.7115 | 1.9435 | 1.6987 | 1.9176
3.8833 | 83.4633 | 84.0599 | 81.7061 | 1.944 | 1.6994 | 1.9179
3.8875 | 83.4586 | 84.0582 | 81.7009 | 1.9446 | 1.7 | 1.9182
3.8917 | 83.4597 | 84.0571 | 81.6958 | 1.9451 | 1.7007 | 1.9185
3.8958 | 83.457 | 84.0565 | 81.6911 | 1.9457 | 1.7014 | 1.9187
3.9 | 83.4538 | 84.0558 | 81.6863 | 1.9462 | 1.702 | 1.919
3.9042 | 83.454 | 84.0552 | 81.6817 | 1.9468 | 1.7027 | 1.9192
3.9083 | 83.4505 | 84.0537 | 81.6772 | 1.9472 | 1.7034 | 1.9195
3.9125 | 83.4494 | 84.0517 | 81.6724 | 1.9478 | 1.704 | 1.9197
3.9167 | 83.4492 | 84.0505 | 81.6676 | 1.9483 | 1.7046 | 1.92
3.9208 | 83.4458 | 84.0492 | 81.6627 | 1.9488 | 1.7053 | 1.9202
3.925 | 83.4411 | 84.0482 | 81.6578 | 1.9493 | 1.7059 | 1.9204
3.9292 | 83.4402 | 84.0486 | 81.6541 | 1.9497 | 1.7065 | 1.9207
3.9333 | 83.438 | 84.0483 | 81.6505 | 1.9502 | 1.7071 | 1.9209
3.9375 | 83.4396 | 84.0477 | 81.647 | 1.9507 | 1.7077 | 1.9211
3.9417 | 83.4381 | 84.0477 | 81.6433 | 1.9511 | 1.7083 | 1.9213
3.9458 | 83.435 | 84.0469 | 81.6388 | 1.9516 | 1.7089 | 1.9215
3.95 | 83.4318 | 84.0464 | 81.6345 | 1.952 | 1.7095 | 1.9217
3.9542 | 83.4312 | 84.0466 | 81.6307 | 1.9524 | 1.71 | 1.9219
3.9583 | 83.429 | 84.0465 | 81.6271 | 1.9528 | 1.7106 | 1.9221
3.9625 | 83.4334 | 84.0469 | 81.6231 | 1.9532 | 1.7111 | 1.9223
3.9667 | 83.43 | 84.0475 | 81.6201 | 1.9536 | 1.7117 | 1.9225
3.9708 | 83.4263 | 84.0478 | 81.6171 | 1.954 | 1.7122 | 1.9227
3.975 | 83.4253 | 84.0482 | 81.6138 | 1.9544 | 1.7127 | 1.9229
3.9792 | 83.4199 | 84.0486 | 81.6114 | 1.9547 | 1.7132 | 1.923
3.9833 | 83.4249 | 84.0489 | 81.6084 | 1.9551 | 1.7137 | 1.9232
3.9875 | 83.4273 | 84.0497 | 81.606 | 1.9555 | 1.7142 | 1.9234
3.9917 | 83.4233 | 84.0505 | 81.6034 | 1.9558 | 1.7147 | 1.9235
3.9958 | 83.4252 | 84.0506 | 81.5995 | 1.9562 | 1.7152 | 1.9237
4 | 83.421 | 84.0509 | 81.5965 | 1.9565 | 1.7156 | 1.9238
4.0042 | 83.4185 | 84.0507 | 81.5923 | 1.9568 | 1.7161 | 1.924
4.0083 | 83.4194 | 84.0504 | 81.5891 | 1.9571 | 1.7165 | 1.9241
4.0125 | 83.4202 | 84.0509 | 81.5883 | 1.9574 | 1.7169 | 1.9243
4.0167 | 83.414 | 84.0513 | 81.5857 | 1.9577 | 1.7174 | 1.9244
4.0208 | 83.4126 | 84.0519 | 81.5834 | 1.958 | 1.7178 | 1.9246
4.025 | 83.4157 | 84.0524 | 81.5811 | 1.9583 | 1.7182 | 1.9247
4.0292 | 83.4111 | 84.052 | 81.5772 | 1.9586 | 1.7186 | 1.9248
4.0333 | 83.4141 | 84.0516 | 81.5743 | 1.9589 | 1.719 | 1.925
4.0375 | 83.4154 | 84.0514 | 81.5721 | 1.9592 | 1.7194 | 1.9251
4.0417 | 83.4056 | 84.0513 | 81.5695 | 1.9595 | 1.7198 | 1.9252
4.0458 | 83.4051 | 84.0514 | 81.5677 | 1.9597 | 1.7202 | 1.9253
4.05 | 83.4071 | 84.0515 | 81.5653 | 1.96 | 1.7205 | 1.9255
4.0542 | 83.4001 | 84.0512 | 81.5622 | 1.9602 | 1.7209 | 1.9256
4.0583 | 83.4081 | 84.0509 | 81.5596 | 1.9605 | 1.7213 | 1.9257
4.0625 | 83.4049 | 84.0505 | 81.5566 | 1.9608 | 1.7216 | 1.9258
4.0667 | 83.3987 | 84.0501 | 81.554 | 1.9611 | 1.722 | 1.926
4.0708 | 83.3969 | 84.0499 | 81.5523 | 1.9613 | 1.7223 | 1.9261
4.075 | 83.3977 | 84.0497 | 81.55 | 1.9615 | 1.7227 | 1.9262
4.0792 | 83.393 | 84.0497 | 81.5476 | 1.9618 | 1.723 | 1.9263
4.0833 | 83.399 | 84.0497 | 81.5454 | 1.962 | 1.7234 | 1.9264
4.0875 | 83.3983 | 84.0494 | 81.5425 | 1.9623 | 1.7237 | 1.9265
4.0917 | 83.3913 | 84.0491 | 81.5402 | 1.9625 | 1.724 | 1.9266
4.0958 | 83.3922 | 84.0488 | 81.5385 | 1.9628 | 1.7244 | 1.9267
4.1 | 83.3889 | 84.0486 | 81.5362 | 1.963 | 1.7247 | 1.9268
4.1042 | 83.3875 | 84.0484 | 81.5341 | 1.9632 | 1.725 | 1.927
4.1083 | 83.3912 | 84.0482 | 81.532 | 1.9634 | 1.7253 | 1.9271
4.1125 | 83.3889 | 84.0481 | 81.5295 | 1.9637 | 1.7256 | 1.9272
4.1167 | 83.3864 | 84.0479 | 81.5275 | 1.9639 | 1.7259 | 1.9273
4.1208 | 83.3859 | 84.0479 | 81.526 | 1.9641 | 1.7262 | 1.9274
4.125 | 83.3811 | 84.0478 | 81.5241 | 1.9643 | 1.7265 | 1.9275
4.1292 | 83.3844 | 84.0473 | 81.5218 | 1.9645 | 1.7268 | 1.9276
4.1333 | 83.3837 | 84.0468 | 81.5195 | 1.9647 | 1.7271 | 1.9277
4.1375 | 83.3837 | 84.0464 | 81.5172 | 1.9649 | 1.7274 | 1.9277
4.1417 | 83.3809 | 84.046 | 81.515 | 1.9651 | 1.7276 | 1.9278
4.1458 | 83.3794 | 84.0459 | 81.5136 | 1.9653 | 1.7279 | 1.9279
4.15 | 83.3755 | 84.046 | 81.5119 | 1.9655 | 1.7282 | 1.928
4.1542 | 83.3763 | 84.0457 | 81.5099 | 1.9657 | 1.7285 | 1.9281
4.1583 | 83.3798 | 84.0453 | 81.508 | 1.9659 | 1.7287 | 1.9282
4.1625 | 83.3754 | 84.0447 | 81.5057 | 1.9661 | 1.729 | 1.9283
4.1667 | 83.3767 | 84.044 | 81.5036 | 1.9663 | 1.7293 | 1.9284
4.1708 | 83.3703 | 84.0437 | 81.5018 | 1.9665 | 1.7295 | 1.9285
4.175 | 83.3649 | 84.0435 | 81.4999 | 1.9667 | 1.7298 | 1.9286
4.1792 | 83.3652 | 84.0432 | 81.498 | 1.9668 | 1.73 | 1.9286
4.1833 | 83.3652 | 84.0427 | 81.4962 | 1.967 | 1.7303 | 1.9287
4.1875 | 83.3667 | 84.0422 | 81.4941 | 1.9672 | 1.7305 | 1.9288
4.1917 | 83.3703 | 84.0414 | 81.4921 | 1.9674 | 1.7308 | 1.9289
4.1958 | 83.3657 | 84.0411 | 81.4903 | 1.9676 | 1.731 | 1.929
4.2 | 83.3634 | 84.0399 | 81.4885 | 1.9678 | 1.7313 | 1.9291
4.2042 | 83.3621 | 84.0399 | 81.487 | 1.9679 | 1.7315 | 1.9292
4.2083 | 83.3611 | 84.0403 | 81.4855 | 1.9681 | 1.7318 | 1.9292
4.2125 | 83.3616 | 84.0399 | 81.4837 | 1.9683 | 1.732 | 1.9293
4.2167 | 83.3619 | 84.0404 | 81.4819 | 1.9684 | 1.7323 | 1.9294
4.2208 | 83.359 | 84.04 | 81.4801 | 1.9686 | 1.7325 | 1.9295
4.225 | 83.3563 | 84.0398 | 81.4783 | 1.9688 | 1.7327 | 1.9295
4.2292 | 83.3564 | 84.0397 | 81.4767 | 1.9689 | 1.7329 | 1.9296
4.2333 | 83.3535 | 84.0387 | 81.4752 | 1.9691 | 1.7332 | 1.9297
4.2375 | 83.3537 | 84.0379 | 81.4727 | 1.9693 | 1.7334 | 1.9298
4.2417 | 83.3516 | 84.0364 | 81.4703 | 1.9695 | 1.7336 | 1.9299
4.2458 | 83.3481 | 84.0356 | 81.4677 | 1.9696 | 1.7338 | 1.9299
4.25 | 83.3487 | 84.0367 | 81.4651 | 1.9698 | 1.734 | 1.93
4.2542 | 83.3438 | 84.0341 | 81.4604 | 1.97 | 1.7343 | 1.9301
4.2583 | 83.3407 | 84.0318 | 81.4559 | 1.9702 | 1.7345 | 1.9302
4.2625 | 83.3413 | 84.0329 | 81.4544 | 1.9704 | 1.7347 | 1.9303
4.2667 | 83.3395 | 84.033 | 81.453 | 1.9705 | 1.7349 | 1.9304
4.2708 | 83.3372 | 84.0366 | 81.4534 | 1.9708 | 1.7351 | 1.9305
4.275 | 83.3399 | 84.0406 | 81.4536 | 1.9709 | 1.7353 | 1.9306
4.2792 | 83.3596 | 84.0681 | 81.4774 | 1.9709 | 1.7353 | 1.9305
4.2833 | 83.3863 | 84.0949 | 81.5 | 1.9708 | 1.7353 | 1.9303
4.2875 | 83.3926 | 84.0968 | 81.5009 | 1.971 | 1.7354 | 1.9304
4.2917 | 83.403 | 84.0985 | 81.5027 | 1.9712 | 1.7356 | 1.9305
4.2958 | 83.4286 | 84.08 | 81.4928 | 1.9709 | 1.7355 | 1.9303
4.3 | 83.4381 | 84.0624 | 81.4845 | 1.9707 | 1.7354 | 1.9301
4.3042 | 83.4081 | 83.9742 | 81.4101 | 1.9715 | 1.7362 | 1.9308
4.3083 | 83.3526 | 83.8911 | 81.3396 | 1.9722 | 1.737 | 1.9315
4.3125 | 83.2743 | 83.8741 | 81.3231 | 1.972 | 1.7372 | 1.9314
4.3167 | 83.2427 | 83.8562 | 81.3045 | 1.972 | 1.7374 | 1.9313
4.3208 | 83.1946 | 83.9095 | 81.3375 | 1.9727 | 1.7385 | 1.9322
4.325 | 83.1582 | 83.9589 | 81.366 | 1.9741 | 1.7395 | 1.933
4.3292 | 83.193 | 84.0352 | 81.4175 | 1.9741 | 1.7391 | 1.9324
4.3333 | 83.2036 | 84.1089 | 81.4675 | 1.9742 | 1.7388 | 1.9319
4.3375 | 83.2577 | 84.1042 | 81.4589 | 1.9748 | 1.7395 | 1.9326
4.3417 | 83.313 | 84.0997 | 81.4535 | 1.9759 | 1.7401 | 1.9332
4.3458 | 83.3021 | 84.0119 | 81.3687 | 1.9759 | 1.7399 | 1.9329
4.35 | 83.2398 | 83.9278 | 81.2886 | 1.9762 | 1.7396 | 1.9328
4.3542 | 83.2311 | 84.0016 | 81.3418 | 1.9766 | 1.7397 | 1.9329
4.3583 | 83.2304 | 84.0703 | 81.387 | 1.9769 | 1.7399 | 1.9331
4.3625 | 83.1644 | 84.1131 | 81.4093 | 1.9776 | 1.74 | 1.9333
4.3667 | 83.1655 | 84.1549 | 81.431 | 1.9782 | 1.74 | 1.9335
4.3708 | 83.1856 | 84.1768 | 81.456 | 1.9785 | 1.7394 | 1.933
4.375 | 83.2342 | 84.1978 | 81.4823 | 1.9784 | 1.7388 | 1.9326
4.3792 | 83.3264 | 84.1802 | 81.4759 | 1.9787 | 1.7387 | 1.9328
4.3833 | 83.3778 | 84.164 | 81.4693 | 1.9789 | 1.7386 | 1.9329
4.3875 | 83.4073 | 84.1823 | 81.4865 | 1.9791 | 1.7376 | 1.9322
4.3917 | 83.4538 | 84.2033 | 81.5029 | 1.9789 | 1.7367 | 1.9316
4.3958 | 83.4695 | 84.2614 | 81.5631 | 1.9788 | 1.7363 | 1.9313
4.4 | 83.5468 | 84.3188 | 81.6213 | 1.9787 | 1.7359 | 1.9311
4.4042 | 83.6116 | 84.2173 | 81.5487 | 1.9784 | 1.7357 | 1.931
4.4083 | 83.6168 | 84.1218 | 81.4851 | 1.978 | 1.7354 | 1.931
4.4125 | 83.6405 | 84.1022 | 81.481 | 1.9778 | 1.7347 | 1.9304
4.4167 | 83.6477 | 84.0812 | 81.4745 | 1.9772 | 1.7341 | 1.9299
4.4208 | 83.5837 | 84.1133 | 81.512 | 1.977 | 1.7344 | 1.9302
4.425 | 83.5513 | 84.1435 | 81.5455 | 1.9768 | 1.7347 | 1.9303
4.4292 | 83.5488 | 84.0418 | 81.4802 | 1.9765 | 1.735 | 1.9304
4.4333 | 83.4981 | 83.9461 | 81.4249 | 1.9763 | 1.7353 | 1.9305
4.4375 | 83.4818 | 83.9047 | 81.4084 | 1.9767 | 1.7357 | 1.9305
4.4417 | 83.4437 | 83.86 | 81.39 | 1.9768 | 1.7361 | 1.9306
4.4458 | 83.3599 | 83.8664 | 81.4008 | 1.9769 | 1.7371 | 1.931
4.45 | 83.2948 | 83.8704 | 81.4075 | 1.9771 | 1.7381 | 1.9313
4.4542 | 83.2488 | 83.8139 | 81.3763 | 1.977 | 1.7393 | 1.9317
4.4583 | 83.2216 | 83.762 | 81.3507 | 1.9774 | 1.7404 | 1.932
4.4625 | 83.167 | 83.7115 | 81.3201 | 1.978 | 1.7417 | 1.9325
4.4667 | 83.1309 | 83.6599 | 81.2898 | 1.9789 | 1.7431 | 1.9329
4.4708 | 83.0966 | 83.6641 | 81.2911 | 1.9795 | 1.7445 | 1.9333
4.475 | 83.0638 | 83.6659 | 81.2883 | 1.9803 | 1.746 | 1.9336
4.4792 | 83.0645 | 83.6511 | 81.2806 | 1.9812 | 1.7478 | 1.9342
4.4833 | 83.0621 | 83.6389 | 81.275 | 1.9822 | 1.7495 | 1.9347
4.4875 | 83.013 | 83.5851 | 81.2345 | 1.9834 | 1.7513 | 1.9353
4.4917 | 82.9718 | 83.5302 | 81.197 | 1.9847 | 1.7531 | 1.9358
4.4958 | 82.9582 | 83.5372 | 81.2017 | 1.9855 | 1.7548 | 1.9362
4.5 | 82.9489 | 83.54 | 81.202 | 1.9866 | 1.7565 | 1.9366
4.5042 | 82.9652 | 83.5398 | 81.202 | 1.9878 | 1.7587 | 1.9373
4.5083 | 82.9723 | 83.5437 | 81.2029 | 1.9892 | 1.7607 | 1.9379
4.5125 | 82.9296 | 83.4976 | 81.163 | 1.9903 | 1.7627 | 1.9384
4.5167 | 82.8891 | 83.4528 | 81.1268 | 1.9916 | 1.7646 | 1.9388
4.5208 | 82.8909 | 83.4711 | 81.1361 | 1.9926 | 1.7665 | 1.9392
4.525 | 82.8937 | 83.4855 | 81.1405 | 1.9937 | 1.7683 | 1.9396
4.5292 | 82.9045 | 83.4895 | 81.1362 | 1.995 | 1.7705 | 1.9402
4.5333 | 82.9093 | 83.4969 | 81.1329 | 1.9963 | 1.7726 | 1.9408
4.5375 | 82.8766 | 83.4656 | 81.1003 | 1.9974 | 1.7744 | 1.9412
4.5417 | 82.8433 | 83.4356 | 81.0711 | 1.9986 | 1.7763 | 1.9416
4.5458 | 82.8518 | 83.462 | 81.0822 | 1.9996 | 1.7781 | 1.942
4.55 | 82.8603 | 83.4858 | 81.0889 | 2.0006 | 1.7798 | 1.9424
4.5542 | 82.866 | 83.4932 | 81.083 | 2.0018 | 1.7818 | 1.9429
4.5583 | 82.8689 | 83.5027 | 81.0784 | 2.003 | 1.7837 | 1.9434
4.5625 | 82.8498 | 83.4867 | 81.0569 | 2.004 | 1.7853 | 1.9437
4.5667 | 82.8301 | 83.4708 | 81.0377 | 2.005 | 1.7869 | 1.9441
4.5708 | 82.8338 | 83.4937 | 81.0446 | 2.0059 | 1.7885 | 1.9444
4.575 | 82.8434 | 83.5153 | 81.0487 | 2.0069 | 1.79 | 1.9447
4.5792 | 82.8393 | 83.518 | 81.0389 | 2.0079 | 1.7917 | 1.9452
4.5833 | 82.8363 | 83.5217 | 81.0304 | 2.0089 | 1.7933 | 1.9456
4.5875 | 82.8273 | 83.5163 | 81.0183 | 2.0098 | 1.7947 | 1.9458
4.5917 | 82.8161 | 83.5107 | 81.0072 | 2.0106 | 1.796 | 1.9461
4.5958 | 82.8227 | 83.5323 | 81.0135 | 2.0115 | 1.7973 | 1.9464
4.6 | 82.8323 | 83.5545 | 81.0184 | 2.0124 | 1.7987 | 1.9467
4.6042 | 82.8237 | 83.5555 | 81.0072 | 2.0132 | 1.8 | 1.947
4.6083 | 82.8174 | 83.556 | 80.9969 | 2.0141 | 1.8013 | 1.9474
4.6125 | 82.8093 | 83.5548 | 80.9892 | 2.0149 | 1.8024 | 1.9476
4.6167 | 82.8048 | 83.5522 | 80.9817 | 2.0156 | 1.8035 | 1.9478
4.6208 | 82.8077 | 83.5667 | 80.9848 | 2.0164 | 1.8046 | 1.9481
4.625 | 82.8176 | 83.5819 | 80.9872 | 2.0172 | 1.8058 | 1.9483
4.6292 | 82.8071 | 83.5807 | 80.9777 | 2.0179 | 1.8068 | 1.9486
4.6333 | 82.7994 | 83.5791 | 80.969 | 2.0186 | 1.8079 | 1.9488
4.6375 | 82.7931 | 83.5775 | 80.9628 | 2.0193 | 1.8089 | 1.9491
4.6417 | 82.7842 | 83.5749 | 80.9568 | 2.02 | 1.8098 | 1.9493
4.6458 | 82.7866 | 83.5821 | 80.9562 | 2.0207 | 1.8108 | 1.9495
4.65 | 82.7889 | 83.5899 | 80.9552 | 2.0214 | 1.8118 | 1.9497
4.6542 | 82.7821 | 83.5886 | 80.9483 | 2.0221 | 1.8127 | 1.95
4.6583 | 82.7791 | 83.5869 | 80.9417 | 2.0228 | 1.8137 | 1.9502
4.6625 | 82.7723 | 83.5855 | 80.9366 | 2.0234 | 1.8146 | 1.9504
4.6667 | 82.7692 | 83.5831 | 80.9314 | 2.0241 | 1.8154 | 1.9506
4.6708 | 82.7677 | 83.5861 | 80.9287 | 2.0247 | 1.8163 | 1.9508
4.675 | 82.7656 | 83.5897 | 80.926 | 2.0254 | 1.8172 | 1.951
4.6792 | 82.7621 | 83.5892 | 80.921 | 2.026 | 1.818 | 1.9512
4.6833 | 82.756 | 83.5885 | 80.9162 | 2.0266 | 1.8189 | 1.9514
4.6875 | 82.7544 | 83.5876 | 80.9118 | 2.0272 | 1.8197 | 1.9516
4.6917 | 82.747 | 83.5861 | 80.9074 | 2.0278 | 1.8205 | 1.9518
4.6958 | 82.7477 | 83.5871 | 80.9039 | 2.0284 | 1.8213 | 1.952
4.7 | 82.7424 | 83.5885 | 80.9004 | 2.029 | 1.8221 | 1.9521
4.7042 | 82.7409 | 83.5887 | 80.8967 | 2.0295 | 1.8229 | 1.9523
4.7083 | 82.7396 | 83.5887 | 80.8932 | 2.0301 | 1.8237 | 1.9525
4.7125 | 82.7363 | 83.5883 | 80.8894 | 2.0307 | 1.8245 | 1.9527
4.7167 | 82.7312 | 83.5877 | 80.8858 | 2.0312 | 1.8252 | 1.9528
4.7208 | 82.7304 | 83.5881 | 80.8822 | 2.0318 | 1.826 | 1.953
4.725 | 82.7242 | 83.5892 | 80.8787 | 2.0323 | 1.8267 | 1.9532
4.7292 | 82.7218 | 83.5909 | 80.8759 | 2.0328 | 1.8274 | 1.9533
4.7333 | 82.723 | 83.5931 | 80.8732 | 2.0334 | 1.8281 | 1.9535
4.7375 | 82.7159 | 83.5948 | 80.8702 | 2.0339 | 1.8288 | 1.9536
4.7417 | 82.7176 | 83.596 | 80.8672 | 2.0344 | 1.8295 | 1.9538
4.7458 | 82.7169 | 83.597 | 80.8641 | 2.0348 | 1.8302 | 1.9539
4.75 | 82.7144 | 83.5974 | 80.861 | 2.0353 | 1.8308 | 1.9541
4.7542 | 82.7128 | 83.5976 | 80.858 | 2.0358 | 1.8315 | 1.9542
4.7583 | 82.7115 | 83.5975 | 80.8551 | 2.0363 | 1.8321 | 1.9544
4.7625 | 82.7021 | 83.5974 | 80.8523 | 2.0367 | 1.8327 | 1.9545
4.7667 | 82.7064 | 83.5977 | 80.8496 | 2.0372 | 1.8333 | 1.9546
4.7708 | 82.7036 | 83.5982 | 80.8472 | 2.0376 | 1.8339 | 1.9548
4.775 | 82.6997 | 83.5984 | 80.8448 | 2.0381 | 1.8345 | 1.9549
4.7792 | 82.7034 | 83.5982 | 80.8421 | 2.0385 | 1.8351 | 1.955
4.7833 | 82.6983 | 83.5973 | 80.8395 | 2.0389 | 1.8357 | 1.9551
4.7875 | 82.6959 | 83.596 | 80.8367 | 2.0393 | 1.8363 | 1.9553
4.7917 | 82.6982 | 83.5954 | 80.834 | 2.0397 | 1.8369 | 1.9554
4.7958 | 82.694 | 83.5951 | 80.8314 | 2.0401 | 1.8374 | 1.9555
4.8 | 82.6896 | 83.5947 | 80.8288 | 2.0405 | 1.838 | 1.9556
4.8042 | 82.6892 | 83.5954 | 80.8269 | 2.0409 | 1.8386 | 1.9557
4.8083 | 82.687 | 83.5952 | 80.8251 | 2.0412 | 1.8391 | 1.9558
4.8125 | 82.6847 | 83.5945 | 80.8233 | 2.0417 | 1.8397 | 1.9559
4.8167 | 82.687 | 83.5944 | 80.8211 | 2.042 | 1.8402 | 1.9561
4.8208 | 82.6839 | 83.5938 | 80.8182 | 2.0424 | 1.8408 | 1.9562
4.825 | 82.6795 | 83.5935 | 80.8156 | 2.0427 | 1.8413 | 1.9563
4.8292 | 82.6829 | 83.5941 | 80.8134 | 2.0431 | 1.8418 | 1.9564
4.8333 | 82.6768 | 83.5942 | 80.8115 | 2.0434 | 1.8423 | 1.9565
4.8375 | 82.6814 | 83.5945 | 80.8091 | 2.0437 | 1.8428 | 1.9566
4.8417 | 82.677 | 83.5951 | 80.8074 | 2.0441 | 1.8433 | 1.9567
4.8458 | 82.6745 | 83.5954 | 80.8058 | 2.0444 | 1.8438 | 1.9568
4.85 | 82.6718 | 83.5959 | 80.8038 | 2.0447 | 1.8443 | 1.9568
4.8542 | 82.6679 | 83.5969 | 80.803 | 2.045 | 1.8448 | 1.9569
4.8583 | 82.6724 | 83.5976 | 80.8014 | 2.0453 | 1.8453 | 1.957
4.8625 | 82.6737 | 83.5985 | 80.7996 | 2.0456 | 1.8457 | 1.9571
4.8667 | 82.6708 | 83.5997 | 80.7983 | 2.0459 | 1.8462 | 1.9572
4.8708 | 82.6722 | 83.6 | 80.7959 | 2.0462 | 1.8466 | 1.9573
4.875 | 82.6668 | 83.6005 | 80.7941 | 2.0464 | 1.8471 | 1.9574
4.8792 | 82.6648 | 83.6011 | 80.7921 | 2.0467 | 1.8475 | 1.9574
4.8833 | 82.6672 | 83.6014 | 80.7904 | 2.0469 | 1.8479 | 1.9575
4.8875 | 82.6673 | 83.6025 | 80.7904 | 2.0472 | 1.8483 | 1.9576
4.8917 | 82.6638 | 83.6036 | 80.7891 | 2.0474 | 1.8487 | 1.9576
4.8958 | 82.6632 | 83.6044 | 80.7876 | 2.0477 | 1.8491 | 1.9577
4.9 | 82.6619 | 83.6054 | 80.7863 | 2.0479 | 1.8495 | 1.9578
4.9042 | 82.6611 | 83.6055 | 80.7839 | 2.0481 | 1.8499 | 1.9579
4.9083 | 82.6614 | 83.6056 | 80.7823 | 2.0484 | 1.8503 | 1.9579
4.9125 | 82.6654 | 83.6061 | 80.7819 | 2.0486 | 1.8506 | 1.958
4.9167 | 82.6565 | 83.6068 | 80.7806 | 2.0488 | 1.851 | 1.9581
4.9208 | 82.659 | 83.6074 | 80.7797 | 2.049 | 1.8513 | 1.9581
4.925 | 82.6559 | 83.6081 | 80.7786 | 2.0492 | 1.8517 | 1.9582
4.9292 | 82.653 | 83.6081 | 80.7764 | 2.0494 | 1.852 | 1.9582
4.9333 | 82.6577 | 83.6081 | 80.775 | 2.0497 | 1.8524 | 1.9583
4.9375 | 82.6575 | 83.6082 | 80.7738 | 2.0498 | 1.8527 | 1.9584
4.9417 | 82.6516 | 83.6083 | 80.7724 | 2.0501 | 1.853 | 1.9584
4.9458 | 82.6511 | 83.6087 | 80.7717 | 2.0503 | 1.8533 | 1.9585
4.95 | 82.6509 | 83.609 | 80.7706 | 2.0504 | 1.8537 | 1.9585
4.9542 | 82.6455 | 83.6093 | 80.7691 | 2.0506 | 1.854 | 1.9586
4.9583 | 82.6513 | 83.6095 | 80.7679 | 2.0508 | 1.8543 | 1.9586
4.9625 | 82.6516 | 83.6096 | 80.7663 | 2.051 | 1.8546 | 1.9587
4.9667 | 82.6459 | 83.6096 | 80.7651 | 2.0512 | 1.8549 | 1.9587
4.9708 | 82.6449 | 83.6097 | 80.7644 | 2.0514 | 1.8552 | 1.9588
4.975 | 82.6451 | 83.6098 | 80.7632 | 2.0516 | 1.8555 | 1.9588
4.9792 | 82.6394 | 83.6101 | 80.762 | 2.0517 | 1.8558 | 1.9589
4.9833 | 82.6458 | 83.6104 | 80.7611 | 2.0519 | 1.8561 | 1.959
4.9875 | 82.6435 | 83.6106 | 80.7596 | 2.0521 | 1.8563 | 1.959
4.9917 | 82.6407 | 83.6107 | 80.7587 | 2.0523 | 1.8566 | 1.959
4.9958 | 82.6395 | 83.6109 | 80.7581 | 2.0525 | 1.8569 | 1.9591
5 | 82.6384 | 83.6111 | 80.7571 | 2.0526 | 1.8572 | 1.9591
5.0042 | 82.6355 | 83.611 | 80.7558 | 2.0528 | 1.8574 | 1.9592
5.0083 | 82.6391 | 83.611 | 80.7547 | 2.0529 | 1.8577 | 1.9592
5.0125 | 82.6378 | 83.611 | 80.7533 | 2.0531 | 1.8579 | 1.9593
5.0167 | 82.634 | 83.6111 | 80.7523 | 2.0533 | 1.8582 | 1.9593
5.0208 | 82.6357 | 83.6114 | 80.7519 | 2.0534 | 1.8585 | 1.9594
5.025 | 82.6326 | 83.6117 | 80.7512 | 2.0535 | 1.8587 | 1.9594
5.0292 | 82.6337 | 83.6117 | 80.7501 | 2.0537 | 1.859 | 1.9595
5.0333 | 82.6362 | 83.6117 | 80.7491 | 2.0538 | 1.8592 | 1.9595
5.0375 | 82.6353 | 83.6115 | 80.7479 | 2.054 | 1.8594 | 1.9595
5.0417 | 82.6324 | 83.6113 | 80.7468 | 2.0541 | 1.8597 | 1.9596
5.0458 | 82.63 | 83.6113 | 80.7461 | 2.0543 | 1.8599 | 1.9596
5.05 | 82.6238 | 83.6118 | 80.7453 | 2.0544 | 1.8601 | 1.9597
5.0542 | 82.6253 | 83.6117 | 80.7442 | 2.0546 | 1.8604 | 1.9597
5.0583 | 82.6247 | 83.6113 | 80.7432 | 2.0547 | 1.8606 | 1.9597
5.0625 | 82.6268 | 83.611 | 80.7421 | 2.0548 | 1.8608 | 1.9598
5.0667 | 82.628 | 83.6103 | 80.741 | 2.055 | 1.861 | 1.9598
5.0708 | 82.6261 | 83.6103 | 80.7403 | 2.0551 | 1.8613 | 1.9599
5.075 | 82.6216 | 83.6096 | 80.7394 | 2.0553 | 1.8615 | 1.9599
5.0792 | 82.6227 | 83.6098 | 80.7388 | 2.0554 | 1.8617 | 1.9599
5.0833 | 82.6211 | 83.6105 | 80.7381 | 2.0555 | 1.8619 | 1.96
5.0875 | 82.6206 | 83.6102 | 80.737 | 2.0556 | 1.8621 | 1.96
5.0917 | 82.6245 | 83.6108 | 80.7359 | 2.0558 | 1.8623 | 1.9601
5.0958 | 82.6183 | 83.6106 | 80.7346 | 2.0559 | 1.8625 | 1.9601
5.1 | 82.6164 | 83.6098 | 80.7334 | 2.056 | 1.8627 | 1.9601
5.1042 | 82.6161 | 83.6113 | 80.7335 | 2.0561 | 1.8629 | 1.9602
5.1083 | 82.6154 | 83.6121 | 80.7336 | 2.0563 | 1.8631 | 1.9602
5.1125 | 82.6125 | 83.6115 | 80.7313 | 2.0564 | 1.8633 | 1.9602
5.1167 | 82.6133 | 83.611 | 80.7293 | 2.0566 | 1.8635 | 1.9603
5.1208 | 82.6099 | 83.6095 | 80.727 | 2.0567 | 1.8637 | 1.9603
5.125 | 82.6082 | 83.6092 | 80.7249 | 2.0568 | 1.8639 | 1.9604
5.1292 | 82.597 | 83.599 | 80.7139 | 2.057 | 1.8642 | 1.9605
5.1333 | 82.5866 | 83.5888 | 80.7034 | 2.0572 | 1.8645 | 1.9606
5.1375 | 82.5841 | 83.59 | 80.7025 | 2.0574 | 1.8647 | 1.9607
5.1417 | 82.5848 | 83.5905 | 80.7011 | 2.0575 | 1.8648 | 1.9607
5.1458 | 82.5757 | 83.5992 | 80.703 | 2.0579 | 1.8651 | 1.9609
5.15 | 82.5648 | 83.6085 | 80.7037 | 2.0582 | 1.8654 | 1.961
5.1542 | 82.5939 | 83.6589 | 80.7432 | 2.0581 | 1.8651 | 1.9607
5.1583 | 82.6241 | 83.7068 | 80.7802 | 2.0579 | 1.8649 | 1.9604
5.1625 | 82.6233 | 83.7132 | 80.7841 | 2.0584 | 1.8651 | 1.9605
5.1667 | 82.6402 | 83.7191 | 80.7901 | 2.0587 | 1.8652 | 1.9607
5.1708 | 82.6804 | 83.6884 | 80.7768 | 2.058 | 1.8648 | 1.9602
5.175 | 82.705 | 83.6599 | 80.7676 | 2.0576 | 1.8644 | 1.9598
5.1792 | 82.7566 | 83.5703 | 80.7051 | 2.0582 | 1.8653 | 1.9605
5.1833 | 82.7303 | 83.4861 | 80.6468 | 2.059 | 1.8661 | 1.9611
5.1875 | 82.6802 | 83.4736 | 80.6394 | 2.0592 | 1.866 | 1.9608
5.1917 | 82.6096 | 83.4605 | 80.628 | 2.0588 | 1.8659 | 1.9604
5.1958 | 82.5435 | 83.5276 | 80.6761 | 2.0591 | 1.8669 | 1.9611
5.2 | 82.5096 | 83.5903 | 80.7174 | 2.0597 | 1.8679 | 1.9617
5.2042 | 82.5228 | 83.6086 | 80.7222 | 2.0595 | 1.8677 | 1.9613
5.2083 | 82.5433 | 83.6272 | 80.7298 | 2.0595 | 1.8676 | 1.961
5.2125 | 82.5951 | 83.6061 | 80.7168 | 2.0598 | 1.8682 | 1.9613
5.2167 | 82.639 | 83.5856 | 80.7082 | 2.0604 | 1.8688 | 1.9617
5.2208 | 82.6246 | 83.518 | 80.6423 | 2.0606 | 1.8691 | 1.9618
5.225 | 82.5449 | 83.4532 | 80.5787 | 2.0611 | 1.8693 | 1.9619
5.2292 | 82.5032 | 83.5342 | 80.6284 | 2.0613 | 1.8694 | 1.9619
5.2333 | 82.494 | 83.6099 | 80.6686 | 2.0615 | 1.8695 | 1.9619
5.2375 | 82.4248 | 83.6367 | 80.673 | 2.062 | 1.8701 | 1.9624
5.2417 | 82.4335 | 83.6614 | 80.678 | 2.0629 | 1.8707 | 1.9629
5.2458 | 82.4352 | 83.6414 | 80.6584 | 2.0634 | 1.8703 | 1.9626
5.25 | 82.4019 | 83.6214 | 80.6426 | 2.0639 | 1.8699 | 1.9624
5.2542 | 82.4281 | 83.6635 | 80.6729 | 2.0645 | 1.8699 | 1.9626
5.2583 | 82.4291 | 83.7035 | 80.6968 | 2.0653 | 1.87 | 1.9628
5.2625 | 82.4165 | 83.7363 | 80.7094 | 2.0658 | 1.8695 | 1.9625
5.2667 | 82.4493 | 83.7709 | 80.7213 | 2.0662 | 1.869 | 1.9623
5.2708 | 82.4726 | 83.8087 | 80.7554 | 2.0664 | 1.8684 | 1.962
5.275 | 82.5338 | 83.8464 | 80.7909 | 2.0665 | 1.8678 | 1.9618
5.2792 | 82.6016 | 83.7963 | 80.7573 | 2.0666 | 1.8675 | 1.9618
5.2833 | 82.6422 | 83.7498 | 80.7296 | 2.0666 | 1.8671 | 1.9618
5.2875 | 82.6914 | 83.7561 | 80.7367 | 2.0667 | 1.8662 | 1.9613
5.2917 | 82.7443 | 83.7627 | 80.7409 | 2.0666 | 1.8652 | 1.9608
5.2958 | 82.7534 | 83.8043 | 80.7831 | 2.0668 | 1.865 | 1.9609
5.3 | 82.7894 | 83.8448 | 80.8225 | 2.0667 | 1.8647 | 1.9608
5.3042 | 82.8139 | 83.7504 | 80.7674 | 2.0663 | 1.8645 | 1.9608
5.3083 | 82.83 | 83.6619 | 80.7242 | 2.0659 | 1.8643 | 1.9607
5.3125 | 82.8768 | 83.6421 | 80.7266 | 2.0655 | 1.8639 | 1.9605
5.3167 | 82.884 | 83.62 | 80.7251 | 2.0653 | 1.8635 | 1.9602
5.3208 | 82.866 | 83.6404 | 80.7509 | 2.065 | 1.8639 | 1.9604
5.325 | 82.8273 | 83.6594 | 80.7719 | 2.0648 | 1.8642 | 1.9605
5.3292 | 82.7952 | 83.5809 | 80.7338 | 2.0644 | 1.8646 | 1.9605
5.3333 | 82.7801 | 83.5082 | 80.7058 | 2.0642 | 1.865 | 1.9605
5.3375 | 82.7642 | 83.4724 | 80.6973 | 2.0642 | 1.8655 | 1.9606
5.3417 | 82.7403 | 83.4356 | 80.6869 | 2.0644 | 1.866 | 1.9606
5.3458 | 82.707 | 83.4467 | 80.6986 | 2.0645 | 1.8669 | 1.9608
5.35 | 82.6498 | 83.4567 | 80.7048 | 2.0646 | 1.8678 | 1.9609
5.3542 | 82.6079 | 83.4185 | 80.6902 | 2.0646 | 1.8688 | 1.9611
5.3583 | 82.5569 | 83.3837 | 80.6812 | 2.0645 | 1.8699 | 1.9613
5.3625 | 82.5038 | 83.3372 | 80.6597 | 2.0648 | 1.871 | 1.9615
5.3667 | 82.452 | 83.2891 | 80.6395 | 2.065 | 1.8722 | 1.9617
5.3708 | 82.4411 | 83.2961 | 80.648 | 2.0654 | 1.8734 | 1.9618
5.375 | 82.4283 | 83.3001 | 80.651 | 2.0658 | 1.8746 | 1.9619
5.3792 | 82.4288 | 83.2877 | 80.6512 | 2.0664 | 1.8762 | 1.9622
5.3833 | 82.4223 | 83.2793 | 80.6539 | 2.0671 | 1.8777 | 1.9625
5.3875 | 82.3743 | 83.2315 | 80.6254 | 2.0678 | 1.8793 | 1.9627
5.3917 | 82.3332 | 83.1842 | 80.6004 | 2.0686 | 1.8808 | 1.9629
5.3958 | 82.329 | 83.1972 | 80.6112 | 2.0691 | 1.8823 | 1.963
5.4 | 82.3268 | 83.2065 | 80.6159 | 2.0698 | 1.8837 | 1.9631
5.4042 | 82.3376 | 83.2052 | 80.6168 | 2.0707 | 1.8856 | 1.9635
5.4083 | 82.341 | 83.208 | 80.6191 | 2.0716 | 1.8874 | 1.9638
5.4125 | 82.3055 | 83.1688 | 80.5908 | 2.0725 | 1.8891 | 1.964
5.4167 | 82.2681 | 83.1307 | 80.5668 | 2.0733 | 1.8907 | 1.9642
5.4208 | 82.2732 | 83.1539 | 80.5804 | 2.074 | 1.8923 | 1.9643
5.425 | 82.2778 | 83.1739 | 80.5878 | 2.0747 | 1.8938 | 1.9644
5.4292 | 82.2872 | 83.1808 | 80.5878 | 2.0756 | 1.8957 | 1.9647
5.4333 | 82.2929 | 83.1906 | 80.5892 | 2.0766 | 1.8974 | 1.965
5.4375 | 82.2668 | 83.1649 | 80.5674 | 2.0773 | 1.899 | 1.9652
5.4417 | 82.2414 | 83.1397 | 80.5492 | 2.0781 | 1.9005 | 1.9653
5.4458 | 82.2458 | 83.1629 | 80.5598 | 2.0788 | 1.902 | 1.9655
5.45 | 82.2518 | 83.184 | 80.5656 | 2.0795 | 1.9035 | 1.9656
5.4542 | 82.2555 | 83.1893 | 80.5621 | 2.0804 | 1.9051 | 1.9658
5.4583 | 82.2558 | 83.1967 | 80.56 | 2.0812 | 1.9068 | 1.9661
5.4625 | 82.2428 | 83.1839 | 80.5465 | 2.0819 | 1.9081 | 1.9662
5.4667 | 82.224 | 83.1714 | 80.5353 | 2.0826 | 1.9095 | 1.9663
5.4708 | 82.2338 | 83.1955 | 80.5449 | 2.0832 | 1.9108 | 1.9664
5.475 | 82.2409 | 83.2192 | 80.5513 | 2.0839 | 1.9121 | 1.9666
5.4792 | 82.2391 | 83.2229 | 80.5446 | 2.0846 | 1.9135 | 1.9668
5.4833 | 82.2346 | 83.2269 | 80.5394 | 2.0854 | 1.9148 | 1.967
5.4875 | 82.2248 | 83.2224 | 80.5318 | 2.0859 | 1.916 | 1.967
5.4917 | 82.2185 | 83.2168 | 80.5252 | 2.0865 | 1.9171 | 1.9671
5.4958 | 82.2235 | 83.2366 | 80.5325 | 2.0871 | 1.9182 | 1.9673
5.5 | 82.237 | 83.2568 | 80.5378 | 2.0877 | 1.9193 | 1.9674
5.5042 | 82.2294 | 83.2579 | 80.5309 | 2.0883 | 1.9204 | 1.9675
5.5083 | 82.2209 | 83.2587 | 80.5252 | 2.089 | 1.9215 | 1.9677
5.5125 | 82.2127 | 83.2564 | 80.5205 | 2.0894 | 1.9225 | 1.9677
5.5167 | 82.2048 | 83.253 | 80.5163 | 2.09 | 1.9234 | 1.9678
5.5208 | 82.2074 | 83.2657 | 80.5202 | 2.0905 | 1.9244 | 1.9679
5.525 | 82.2166 | 83.2792 | 80.5228 | 2.0911 | 1.9253 | 1.968
5.5292 | 82.2075 | 83.2789 | 80.5174 | 2.0916 | 1.9262 | 1.9681
5.5333 | 82.2041 | 83.2782 | 80.5127 | 2.0921 | 1.9272 | 1.9682
5.5375 | 82.1978 | 83.2766 | 80.5095 | 2.0926 | 1.928 | 1.9683
5.5417 | 82.1941 | 83.2739 | 80.5065 | 2.0931 | 1.9288 | 1.9684
5.5458 | 82.1938 | 83.281 | 80.5077 | 2.0936 | 1.9297 | 1.9685
5.55 | 82.1987 | 83.2889 | 80.5082 | 2.0941 | 1.9305 | 1.9686
5.5542 | 82.191 | 83.2887 | 80.5045 | 2.0945 | 1.9313 | 1.9687
5.5583 | 82.1858 | 83.2881 | 80.5012 | 2.095 | 1.9321 | 1.9688
5.5625 | 82.1862 | 83.2871 | 80.4987 | 2.0955 | 1.9329 | 1.9689
5.5667 | 82.1778 | 83.2853 | 80.4963 | 2.0959 | 1.9336 | 1.9689
5.5708 | 82.1789 | 83.2889 | 80.4959 | 2.0964 | 1.9344 | 1.969
5.575 | 82.18 | 83.2928 | 80.4951 | 2.0968 | 1.9352 | 1.9691
5.5792 | 82.1736 | 83.2928 | 80.4927 | 2.0972 | 1.9359 | 1.9692
5.5833 | 82.1729 | 83.2924 | 80.4905 | 2.0977 | 1.9366 | 1.9693
5.5875 | 82.1719 | 83.2914 | 80.4885 | 2.0981 | 1.9374 | 1.9693
5.5917 | 82.1654 | 83.2902 | 80.4865 | 2.0986 | 1.9381 | 1.9694
5.5958 | 82.1641 | 83.2917 | 80.4853 | 2.0989 | 1.9388 | 1.9695
5.6 | 82.1629 | 83.2943 | 80.4839 | 2.0994 | 1.9395 | 1.9696
5.6042 | 82.1554 | 83.2962 | 80.4825 | 2.0997 | 1.9401 | 1.9696
5.6083 | 82.1594 | 83.2985 | 80.4812 | 2.1002 | 1.9408 | 1.9697
5.6125 | 82.1551 | 83.3001 | 80.4797 | 2.1005 | 1.9415 | 1.9698
5.6167 | 82.1515 | 83.3011 | 80.4783 | 2.101 | 1.9421 | 1.9699
5.6208 | 82.1545 | 83.3027 | 80.4768 | 2.1013 | 1.9427 | 1.9699
5.625 | 82.1496 | 83.3042 | 80.4753 | 2.1017 | 1.9434 | 1.97
5.6292 | 82.1473 | 83.3054 | 80.474 | 2.1021 | 1.944 | 1.9701
5.6333 | 82.1489 | 83.3066 | 80.4727 | 2.1024 | 1.9446 | 1.9701
5.6375 | 82.14 | 83.3079 | 80.4715 | 2.1028 | 1.9451 | 1.9702
5.6417 | 82.1427 | 83.3089 | 80.4703 | 2.1031 | 1.9457 | 1.9702
5.6458 | 82.1407 | 83.3103 | 80.4693 | 2.1035 | 1.9463 | 1.9703
5.65 | 82.1395 | 83.3114 | 80.4683 | 2.1038 | 1.9468 | 1.9704
5.6542 | 82.1384 | 83.3116 | 80.4669 | 2.1042 | 1.9474 | 1.9704
5.6583 | 82.1372 | 83.3115 | 80.4656 | 2.1045 | 1.9479 | 1.9705
5.6625 | 82.131 | 83.3113 | 80.4641 | 2.1048 | 1.9485 | 1.9705
5.6667 | 82.1348 | 83.3113 | 80.4628 | 2.1051 | 1.949 | 1.9706
5.6708 | 82.1333 | 83.312 | 80.4619 | 2.1054 | 1.9495 | 1.9706
5.675 | 82.1308 | 83.3124 | 80.4608 | 2.1057 | 1.95 | 1.9707
5.6792 | 82.1279 | 83.3131 | 80.46 | 2.106 | 1.9505 | 1.9707
5.6833 | 82.1274 | 83.3132 | 80.4593 | 2.1063 | 1.9511 | 1.9708
5.6875 | 82.1213 | 83.3126 | 80.4587 | 2.1066 | 1.9516 | 1.9708
5.6917 | 82.1269 | 83.3125 | 80.4576 | 2.1069 | 1.9521 | 1.9709
5.6958 | 82.1255 | 83.3124 | 80.4559 | 2.1072 | 1.9526 | 1.9709
5.7 | 82.1232 | 83.3124 | 80.4546 | 2.1074 | 1.953 | 1.971
5.7042 | 82.1221 | 83.3131 | 80.4534 | 2.1077 | 1.9535 | 1.971
5.7083 | 82.118 | 83.3132 | 80.4526 | 2.1079 | 1.954 | 1.971
5.7125 | 82.119 | 83.3133 | 80.4515 | 2.1082 | 1.9545 | 1.9711
5.7167 | 82.1161 | 83.3137 | 80.4506 | 2.1084 | 1.9549 | 1.9711
5.7208 | 82.1176 | 83.3141 | 80.4499 | 2.1087 | 1.9554 | 1.9712
5.725 | 82.1147 | 83.3147 | 80.4488 | 2.109 | 1.9559 | 1.9712
5.7292 | 82.111 | 83.3158 | 80.449 | 2.1092 | 1.9563 | 1.9713
5.7333 | 82.115 | 83.3166 | 80.4483 | 2.1094 | 1.9568 | 1.9713
5.7375 | 82.1148 | 83.3175 | 80.4469 | 2.1096 | 1.9572 | 1.9713
5.7417 | 82.1133 | 83.3186 | 80.4464 | 2.1099 | 1.9576 | 1.9714
5.7458 | 82.1142 | 83.3189 | 80.4452 | 2.1101 | 1.958 | 1.9714
5.75 | 82.1089 | 83.3195 | 80.4442 | 2.1103 | 1.9585 | 1.9715
5.7542 | 82.1066 | 83.3206 | 80.4436 | 2.1105 | 1.9589 | 1.9715
5.7583 | 82.1102 | 83.3213 | 80.4429 | 2.1107 | 1.9593 | 1.9715
5.7625 | 82.1092 | 83.3227 | 80.443 | 2.1109 | 1.9596 | 1.9716
5.7667 | 82.1097 | 83.3241 | 80.4425 | 2.1111 | 1.96 | 1.9716
5.7708 | 82.1079 | 83.325 | 80.4416 | 2.1113 | 1.9604 | 1.9716
5.775 | 82.1047 | 83.326 | 80.441 | 2.1115 | 1.9608 | 1.9717
5.7792 | 82.104 | 83.3267 | 80.4398 | 2.1117 | 1.9611 | 1.9717
5.7833 | 82.1051 | 83.3272 | 80.4391 | 2.1118 | 1.9615 | 1.9717
5.7875 | 82.1078 | 83.3282 | 80.4396 | 2.112 | 1.9618 | 1.9717
5.7917 | 82.1026 | 83.3295 | 80.439 | 2.1122 | 1.9622 | 1.9718
5.7958 | 82.1048 | 83.3305 | 80.4386 | 2.1123 | 1.9625 | 1.9718
5.8 | 82.1012 | 83.3315 | 80.4382 | 2.1125 | 1.9628 | 1.9718
5.8042 | 82.0982 | 83.3318 | 80.4369 | 2.1126 | 1.9632 | 1.9718
5.8083 | 82.1034 | 83.332 | 80.4362 | 2.1128 | 1.9635 | 1.9719
5.8125 | 82.1021 | 83.3326 | 80.4362 | 2.1129 | 1.9638 | 1.9719
5.8167 | 82.0978 | 83.3333 | 80.4356 | 2.1131 | 1.9641 | 1.9719
5.8208 | 82.0979 | 83.3341 | 80.4354 | 2.1133 | 1.9644 | 1.9719
5.825 | 82.0975 | 83.3349 | 80.435 | 2.1134 | 1.9647 | 1.972
5.8292 | 82.095 | 83.3352 | 80.434 | 2.1135 | 1.965 | 1.972
5.8333 | 82.0991 | 83.3356 | 80.4336 | 2.1137 | 1.9653 | 1.972
5.8375 | 82.1011 | 83.3359 | 80.433 | 2.1138 | 1.9656 | 1.972
5.8417 | 82.0929 | 83.3363 | 80.4324 | 2.114 | 1.9658 | 1.972
5.8458 | 82.0936 | 83.3367 | 80.4324 | 2.1141 | 1.9661 | 1.9721
5.85 | 82.0933 | 83.3372 | 80.4318 | 2.1142 | 1.9664 | 1.9721
5.8542 | 82.0894 | 83.3377 | 80.4313 | 2.1143 | 1.9667 | 1.9721
5.8583 | 82.0955 | 83.3382 | 80.431 | 2.1145 | 1.9669 | 1.9721
5.8625 | 82.0966 | 83.3387 | 80.4303 | 2.1146 | 1.9672 | 1.9721
5.8667 | 82.0897 | 83.3391 | 80.43 | 2.1147 | 1.9674 | 1.9722
5.8708 | 82.0921 | 83.3394 | 80.4299 | 2.1149 | 1.9677 | 1.9722
5.875 | 82.089 | 83.3398 | 80.4294 | 2.115 | 1.9679 | 1.9722
5.8792 | 82.085 | 83.34 | 80.4289 | 2.1151 | 1.9682 | 1.9722
5.8833 | 82.0904 | 83.3404 | 80.4284 | 2.1152 | 1.9684 | 1.9722
5.8875 | 82.0878 | 83.3407 | 80.4278 | 2.1153 | 1.9687 | 1.9723
5.8917 | 82.0864 | 83.3411 | 80.4274 | 2.1155 | 1.9689 | 1.9723
5.8958 | 82.0878 | 83.3416 | 80.4276 | 2.1156 | 1.9691 | 1.9723
5.9 | 82.0869 | 83.342 | 80.4273 | 2.1157 | 1.9693 | 1.9723
5.9042 | 82.0839 | 83.3423 | 80.4269 | 2.1158 | 1.9696 | 1.9723
5.9083 | 82.0897 | 83.3427 | 80.4266 | 2.1159 | 1.9698 | 1.9723
5.9125 | 82.086 | 83.3428 | 80.4259 | 2.116 | 1.97 | 1.9724
5.9167 | 82.085 | 83.3431 | 80.4256 | 2.1161 | 1.9702 | 1.9724
5.9208 | 82.0842 | 83.3434 | 80.4256 | 2.1162 | 1.9704 | 1.9724
5.925 | 82.079 | 83.3444 | 80.4253 | 2.1163 | 1.9706 | 1.9724
5.9292 | 82.0795 | 83.3444 | 80.4249 | 2.1164 | 1.9708 | 1.9724
5.9333 | 82.0805 | 83.3441 | 80.4245 | 2.1165 | 1.971 | 1.9724
5.9375 | 82.0826 | 83.3439 | 80.4237 | 2.1166 | 1.9712 | 1.9724
5.9417 | 82.0825 | 83.3432 | 80.4232 | 2.1167 | 1.9714 | 1.9725
5.9458 | 82.0821 | 83.3436 | 80.4229 | 2.1168 | 1.9716 | 1.9725
5.95 | 82.0758 | 83.3436 | 80.4225 | 2.1169 | 1.9718 | 1.9725
5.9542 | 82.0767 | 83.3443 | 80.4222 | 2.117 | 1.972 | 1.9725
5.9583 | 82.0753 | 83.3456 | 80.422 | 2.117 | 1.9722 | 1.9725
5.9625 | 82.0778 | 83.347 | 80.4223 | 2.1171 | 1.9724 | 1.9725
5.9667 | 82.0795 | 83.349 | 80.4227 | 2.1172 | 1.9726 | 1.9725
5.9708 | 82.078 | 83.3498 | 80.4226 | 2.1173 | 1.9727 | 1.9726
5.975 | 82.0726 | 83.3496 | 80.4224 | 2.1174 | 1.9729 | 1.9726
5.9792 | 82.0782 | 83.3547 | 80.4265 | 2.1174 | 1.973 | 1.9725
5.9833 | 82.0811 | 83.3593 | 80.4305 | 2.1175 | 1.9731 | 1.9725
5.9875 | 82.0811 | 83.3581 | 80.4288 | 2.1176 | 1.9733 | 1.9725
5.9917 | 82.0808 | 83.3573 | 80.4276 | 2.1177 | 1.9735 | 1.9726
5.9958 | 82.0823 | 83.3529 | 80.426 | 2.1177 | 1.9736 | 1.9725
6 | 82.0798 | 83.3492 | 80.425 | 2.1177 | 1.9737 | 1.9725
6.0042 | 82.0633 | 83.3255 | 80.4053 | 2.118 | 1.9741 | 1.9727
6.0083 | 82.044 | 83.3024 | 80.3869 | 2.1182 | 1.9744 | 1.9729
6.0125 | 82.0427 | 83.3022 | 80.3862 | 2.1182 | 1.9746 | 1.9728
6.0167 | 82.0398 | 83.3017 | 80.3841 | 2.1182 | 1.9747 | 1.9728
6.0208 | 82.0181 | 83.3181 | 80.3872 | 2.1187 | 1.9751 | 1.973
6.025 | 82.0016 | 83.3347 | 80.3873 | 2.1192 | 1.9755 | 1.9733
6.0292 | 82.0227 | 83.4025 | 80.4328 | 2.119 | 1.9751 | 1.9729
6.0333 | 82.0445 | 83.4665 | 80.4744 | 2.1188 | 1.9747 | 1.9724
6.0375 | 82.0364 | 83.4761 | 80.4776 | 2.1196 | 1.9749 | 1.9727
6.0417 | 82.0453 | 83.4845 | 80.4846 | 2.1201 | 1.9751 | 1.973
6.0458 | 82.0361 | 83.4408 | 80.4632 | 2.1198 | 1.9745 | 1.9724
6.05 | 82.0774 | 83.3999 | 80.4484 | 2.1191 | 1.9739 | 1.9719
6.0542 | 82.1438 | 83.3329 | 80.4118 | 2.1193 | 1.9746 | 1.9725
6.0583 | 82.1896 | 83.2699 | 80.3779 | 2.12 | 1.9753 | 1.973
6.0625 | 82.1956 | 83.2665 | 80.3773 | 2.1202 | 1.975 | 1.9726
6.0667 | 82.1522 | 83.2632 | 80.3711 | 2.1203 | 1.9748 | 1.9722
6.0708 | 82.0983 | 83.3324 | 80.4258 | 2.1205 | 1.9755 | 1.9726
6.075 | 82.0527 | 83.3984 | 80.4738 | 2.1206 | 1.9761 | 1.9729
6.0792 | 82.0415 | 83.3679 | 80.4493 | 2.1203 | 1.9761 | 1.9727
6.0833 | 82.0448 | 83.3398 | 80.4324 | 2.1199 | 1.9762 | 1.9725
6.0875 | 82.1141 | 83.3116 | 80.4248 | 2.1199 | 1.9765 | 1.9725
6.0917 | 82.157 | 83.284 | 80.4211 | 2.12 | 1.9768 | 1.9725
6.0958 | 82.1972 | 83.2491 | 80.3878 | 2.1202 | 1.9773 | 1.9728
6.1 | 82.159 | 83.2164 | 80.3532 | 2.1208 | 1.9779 | 1.973
6.1042 | 82.1311 | 83.2687 | 80.3802 | 2.1211 | 1.978 | 1.9728
6.1083 | 82.0788 | 83.3185 | 80.4008 | 2.1207 | 1.9781 | 1.9727
6.1125 | 82.0168 | 83.3238 | 80.3973 | 2.1209 | 1.9788 | 1.9732
6.1167 | 81.9895 | 83.3265 | 80.3963 | 2.1211 | 1.9796 | 1.9736
6.1208 | 81.9784 | 83.2843 | 80.3574 | 2.1212 | 1.9796 | 1.9735
6.125 | 81.9542 | 83.2423 | 80.3221 | 2.1218 | 1.9796 | 1.9734
6.1292 | 81.9376 | 83.3151 | 80.3662 | 2.1222 | 1.9798 | 1.9735
6.1333 | 81.9101 | 83.3846 | 80.399 | 2.1228 | 1.9799 | 1.9736
6.1375 | 81.8757 | 83.4157 | 80.402 | 2.1233 | 1.98 | 1.9738
6.1417 | 81.8706 | 83.4472 | 80.4056 | 2.124 | 1.9801 | 1.9739
6.1458 | 81.8704 | 83.4561 | 80.409 | 2.1245 | 1.9796 | 1.9736
6.15 | 81.8785 | 83.4641 | 80.4165 | 2.1251 | 1.9791 | 1.9734
6.1542 | 81.8835 | 83.4705 | 80.4169 | 2.1258 | 1.9789 | 1.9735
6.1583 | 81.8853 | 83.4771 | 80.4163 | 2.1264 | 1.9787 | 1.9737
6.1625 | 81.8907 | 83.5001 | 80.421 | 2.1268 | 1.978 | 1.9734
6.1667 | 81.9189 | 83.5242 | 80.4232 | 2.127 | 1.9772 | 1.9731
6.1708 | 81.9403 | 83.5599 | 80.4533 | 2.1274 | 1.9767 | 1.973
6.175 | 81.9795 | 83.5945 | 80.4833 | 2.1276 | 1.9762 | 1.9729
6.1792 | 82.0127 | 83.5322 | 80.4472 | 2.1276 | 1.9758 | 1.9729
6.1833 | 82.0377 | 83.4729 | 80.4208 | 2.1275 | 1.9753 | 1.973
6.1875 | 82.0938 | 83.4735 | 80.4285 | 2.1274 | 1.9745 | 1.9726
6.1917 | 82.1353 | 83.473 | 80.4314 | 2.1273 | 1.9737 | 1.9723
6.1958 | 82.1824 | 83.5011 | 80.4608 | 2.1276 | 1.9736 | 1.9724
6.2 | 82.2088 | 83.5284 | 80.4865 | 2.1277 | 1.9735 | 1.9725
6.2042 | 82.2216 | 83.4463 | 80.4479 | 2.1277 | 1.9733 | 1.9724
6.2083 | 82.2448 | 83.3688 | 80.4217 | 2.1275 | 1.9732 | 1.9724
6.2125 | 82.2708 | 83.3504 | 80.4262 | 2.1271 | 1.973 | 1.9722
6.2167 | 82.3116 | 83.3318 | 80.4263 | 2.1267 | 1.9728 | 1.9721
6.2208 | 82.3305 | 83.3508 | 80.4447 | 2.1265 | 1.9732 | 1.9722
6.225 | 82.3307 | 83.3702 | 80.4575 | 2.1262 | 1.9735 | 1.9722
6.2292 | 82.3009 | 83.3119 | 80.4348 | 2.1259 | 1.974 | 1.9723
6.2333 | 82.267 | 83.2565 | 80.4215 | 2.1256 | 1.9744 | 1.9722
6.2375 | 82.2436 | 83.2224 | 80.4154 | 2.1255 | 1.9748 | 1.9723
6.2417 | 82.2236 | 83.1867 | 80.4082 | 2.1253 | 1.9753 | 1.9723
6.2458 | 82.2153 | 83.1971 | 80.4198 | 2.1252 | 1.9761 | 1.9724
6.25 | 82.2067 | 83.2068 | 80.4254 | 2.1253 | 1.9768 | 1.9724
6.2542 | 82.1921 | 83.1773 | 80.4202 | 2.1253 | 1.9778 | 1.9725
6.2583 | 82.1673 | 83.151 | 80.4202 | 2.1254 | 1.9788 | 1.9725
6.2625 | 82.1193 | 83.1078 | 80.404 | 2.1256 | 1.9798 | 1.9726
6.2667 | 82.0697 | 83.0639 | 80.3901 | 2.1257 | 1.9808 | 1.9727
6.2708 | 82.0224 | 83.0737 | 80.4008 | 2.1255 | 1.9819 | 1.9727
6.275 | 81.9907 | 83.0816 | 80.405 | 2.1255 | 1.983 | 1.9727
6.2792 | 81.9771 | 83.0696 | 80.4059 | 2.1256 | 1.9844 | 1.9729
6.2833 | 81.9641 | 83.0623 | 80.4096 | 2.1258 | 1.9858 | 1.973
6.2875 | 81.9356 | 83.0211 | 80.3881 | 2.1262 | 1.9872 | 1.9731
6.2917 | 81.9062 | 82.9809 | 80.3709 | 2.1266 | 1.9885 | 1.9731
6.2958 | 81.8957 | 83.0023 | 80.3845 | 2.1269 | 1.9898 | 1.9732
6.3 | 81.8893 | 83.0207 | 80.391 | 2.1273 | 1.9912 | 1.9732
6.3042 | 81.8923 | 83.0246 | 80.3936 | 2.1278 | 1.9928 | 1.9733
6.3083 | 81.8955 | 83.032 | 80.3979 | 2.1284 | 1.9944 | 1.9735
6.3125 | 81.8659 | 83.0005 | 80.3776 | 2.1289 | 1.9958 | 1.9735
6.3167 | 81.8427 | 82.9693 | 80.3619 | 2.1294 | 1.9973 | 1.9736
6.3208 | 81.8389 | 82.9935 | 80.3738 | 2.1298 | 1.9987 | 1.9736
6.325 | 81.8431 | 83.0149 | 80.3794 | 2.1303 | 2 | 1.9736
6.3292 | 81.848 | 83.0229 | 80.3803 | 2.1309 | 2.0017 | 1.9738
6.3333 | 81.8515 | 83.0336 | 80.3825 | 2.1315 | 2.0033 | 1.974
6.3375 | 81.8328 | 83.0145 | 80.3676 | 2.132 | 2.0046 | 1.974
6.3417 | 81.8128 | 82.9959 | 80.3564 | 2.1326 | 2.006 | 1.974
6.3458 | 81.8169 | 83.0227 | 80.3674 | 2.133 | 2.0073 | 1.9741
6.35 | 81.823 | 83.0483 | 80.3736 | 2.1335 | 2.0086 | 1.9741
6.3542 | 81.8248 | 83.0564 | 80.3709 | 2.1341 | 2.0101 | 1.9742
6.3583 | 81.8245 | 83.0657 | 80.3698 | 2.1347 | 2.0115 | 1.9743
6.3625 | 81.8126 | 83.0574 | 80.3607 | 2.1351 | 2.0127 | 1.9744
6.3667 | 81.802 | 83.0485 | 80.3538 | 2.1356 | 2.0138 | 1.9744
6.3708 | 81.8108 | 83.0739 | 80.3633 | 2.136 | 2.015 | 1.9744
6.375 | 81.8206 | 83.0992 | 80.3694 | 2.1364 | 2.0161 | 1.9745
6.3792 | 81.8204 | 83.1047 | 80.3648 | 2.1369 | 2.0173 | 1.9746
6.3833 | 81.8109 | 83.1105 | 80.362 | 2.1374 | 2.0185 | 1.9746
6.3875 | 81.8043 | 83.1073 | 80.3568 | 2.1378 | 2.0195 | 1.9746
6.3917 | 81.7924 | 83.1031 | 80.3529 | 2.1382 | 2.0205 | 1.9747
6.3958 | 81.8 | 83.1228 | 80.3596 | 2.1385 | 2.0215 | 1.9747
6.4 | 81.8087 | 83.1429 | 80.364 | 2.139 | 2.0225 | 1.9747
6.4042 | 81.8049 | 83.146 | 80.3597 | 2.1394 | 2.0235 | 1.9748
6.4083 | 81.7974 | 83.1487 | 80.3567 | 2.1398 | 2.0244 | 1.9749
6.4125 | 81.7916 | 83.1475 | 80.3538 | 2.1401 | 2.0253 | 1.9749
6.4167 | 81.7876 | 83.145 | 80.3515 | 2.1405 | 2.0261 | 1.9749
6.4208 | 81.7895 | 83.1584 | 80.3555 | 2.1409 | 2.027 | 1.9749
6.425 | 81.7987 | 83.1725 | 80.358 | 2.1412 | 2.0278 | 1.975
6.4292 | 81.7925 | 83.1746 | 80.3548 | 2.1416 | 2.0286 | 1.975
6.4333 | 81.7844 | 83.1761 | 80.3525 | 2.142 | 2.0295 | 1.975
6.4375 | 81.7848 | 83.176 | 80.3508 | 2.1423 | 2.0302 | 1.9751
6.4417 | 81.7776 | 83.1747 | 80.3494 | 2.1426 | 2.0309 | 1.9751
6.4458 | 81.7802 | 83.1831 | 80.3513 | 2.1429 | 2.0317 | 1.9751
6.45 | 81.785 | 83.1917 | 80.3524 | 2.1433 | 2.0324 | 1.9751
6.4542 | 81.7788 | 83.1928 | 80.3503 | 2.1435 | 2.0332 | 1.9752
6.4583 | 81.775 | 83.1932 | 80.3488 | 2.1439 | 2.0339 | 1.9752
6.4625 | 81.7756 | 83.1925 | 80.3476 | 2.1442 | 2.0346 | 1.9752
6.4667 | 81.769 | 83.1914 | 80.3466 | 2.1445 | 2.0353 | 1.9753
6.4708 | 81.7684 | 83.196 | 80.3472 | 2.1448 | 2.036 | 1.9753
6.475 | 81.7714 | 83.2019 | 80.3473 | 2.1451 | 2.0366 | 1.9753
6.4792 | 81.7626 | 83.2046 | 80.3464 | 2.1454 | 2.0373 | 1.9753
6.4833 | 81.7665 | 83.2074 | 80.3458 | 2.1457 | 2.038 | 1.9754
6.4875 | 81.7633 | 83.2091 | 80.345 | 2.1459 | 2.0386 | 1.9754
6.4917 | 81.7595 | 83.2102 | 80.3444 | 2.1463 | 2.0392 | 1.9754
6.4958 | 81.7615 | 83.2136 | 80.3442 | 2.1465 | 2.0399 | 1.9754
6.5 | 81.759 | 83.2175 | 80.3437 | 2.1468 | 2.0405 | 1.9755
6.5042 | 81.7552 | 83.2203 | 80.3433 | 2.1471 | 2.0411 | 1.9755
6.5083 | 81.7575 | 83.2233 | 80.3429 | 2.1474 | 2.0417 | 1.9755
6.5125 | 81.7512 | 83.2258 | 80.3427 | 2.1476 | 2.0422 | 1.9755
6.5167 | 81.7514 | 83.2279 | 80.3423 | 2.1479 | 2.0428 | 1.9755
6.5208 | 81.7531 | 83.2309 | 80.3422 | 2.1481 | 2.0433 | 1.9756
6.525 | 81.7492 | 83.2338 | 80.342 | 2.1484 | 2.0439 | 1.9756
6.5292 | 81.7491 | 83.2355 | 80.3414 | 2.1486 | 2.0444 | 1.9756
6.5333 | 81.7472 | 83.237 | 80.3409 | 2.1488 | 2.0449 | 1.9756
6.5375 | 81.7437 | 83.2384 | 80.3401 | 2.149 | 2.0454 | 1.9756
6.5417 | 81.7452 | 83.2398 | 80.3398 | 2.1493 | 2.0459 | 1.9757
6.5458 | 81.7484 | 83.2422 | 80.3399 | 2.1495 | 2.0464 | 1.9757
6.55 | 81.7441 | 83.2442 | 80.3397 | 2.1498 | 2.0469 | 1.9757
6.5542 | 81.7415 | 83.2458 | 80.3396 | 2.15 | 2.0474 | 1.9757
6.5583 | 81.7405 | 83.247 | 80.3395 | 2.1502 | 2.0479 | 1.9757
6.5625 | 81.7349 | 83.2475 | 80.3396 | 2.1504 | 2.0484 | 1.9757
6.5667 | 81.7416 | 83.2483 | 80.3392 | 2.1506 | 2.0488 | 1.9757
6.5708 | 81.7417 | 83.2495 | 80.3385 | 2.1508 | 2.0493 | 1.9758
6.575 | 81.7413 | 83.2506 | 80.3381 | 2.151 | 2.0498 | 1.9758
6.5792 | 81.7368 | 83.252 | 80.3375 | 2.1512 | 2.0502 | 1.9758
6.5833 | 81.7343 | 83.2528 | 80.3374 | 2.1514 | 2.0507 | 1.9758
6.5875 | 81.7306 | 83.2534 | 80.3373 | 2.1516 | 2.0511 | 1.9758
6.5917 | 81.7336 | 83.2543 | 80.337 | 2.1518 | 2.0516 | 1.9758
6.5958 | 81.7344 | 83.2555 | 80.3369 | 2.1519 | 2.052 | 1.9758
6.6 | 81.7329 | 83.2567 | 80.3365 | 2.1521 | 2.0524 | 1.9758
6.6042 | 81.7301 | 83.2585 | 80.3371 | 2.1523 | 2.0529 | 1.9758
6.6083 | 81.7304 | 83.2599 | 80.337 | 2.1525 | 2.0533 | 1.9759
6.6125 | 81.7301 | 83.2609 | 80.3361 | 2.1526 | 2.0537 | 1.9759
6.6167 | 81.7315 | 83.2623 | 80.3361 | 2.1528 | 2.0541 | 1.9759
6.6208 | 81.7314 | 83.2632 | 80.3357 | 2.1529 | 2.0545 | 1.9759
6.625 | 81.7281 | 83.2644 | 80.3352 | 2.1531 | 2.0549 | 1.9759
6.6292 | 81.7242 | 83.2663 | 80.3356 | 2.1532 | 2.0553 | 1.9759
6.6333 | 81.7286 | 83.2678 | 80.3355 | 2.1534 | 2.0557 | 1.9759
6.6375 | 81.725 | 83.2695 | 80.3355 | 2.1535 | 2.056 | 1.9759
6.6417 | 81.7307 | 83.2714 | 80.3355 | 2.1537 | 2.0564 | 1.9759
6.6458 | 81.7263 | 83.2727 | 80.3351 | 2.1538 | 2.0568 | 1.9759
6.65 | 81.7266 | 83.2741 | 80.3349 | 2.154 | 2.0571 | 1.9759
6.6542 | 81.7229 | 83.2757 | 80.3347 | 2.1541 | 2.0575 | 1.9759
6.6583 | 81.7258 | 83.2771 | 80.3346 | 2.1542 | 2.0578 | 1.976
6.6625 | 81.7256 | 83.2789 | 80.3353 | 2.1543 | 2.0582 | 1.976
6.6667 | 81.7232 | 83.2809 | 80.3353 | 2.1545 | 2.0585 | 1.976
6.6708 | 81.7266 | 83.2824 | 80.3351 | 2.1546 | 2.0588 | 1.976
6.675 | 81.7219 | 83.284 | 80.3352 | 2.1547 | 2.0591 | 1.976
6.6792 | 81.7207 | 83.2851 | 80.3346 | 2.1548 | 2.0595 | 1.976
6.6833 | 81.7254 | 83.286 | 80.3345 | 2.1549 | 2.0598 | 1.976
6.6875 | 81.7218 | 83.2874 | 80.3351 | 2.155 | 2.0601 | 1.976
6.6917 | 81.7211 | 83.289 | 80.335 | 2.1551 | 2.0603 | 1.976
6.6958 | 81.7207 | 83.2905 | 80.3352 | 2.1552 | 2.0606 | 1.976
6.7 | 81.7222 | 83.2919 | 80.3353 | 2.1553 | 2.0609 | 1.976
6.7042 | 81.7195 | 83.2928 | 80.3348 | 2.1554 | 2.0612 | 1.976
6.7083 | 81.7254 | 83.2936 | 80.3348 | 2.1555 | 2.0615 | 1.976
6.7125 | 81.7237 | 83.2946 | 80.3349 | 2.1556 | 2.0617 | 1.976
6.7167 | 81.7169 | 83.2957 | 80.3349 | 2.1557 | 2.062 | 1.976
6.7208 | 81.7168 | 83.2968 | 80.3352 | 2.1558 | 2.0623 | 1.976
6.725 | 81.7191 | 83.298 | 80.3352 | 2.1558 | 2.0625 | 1.976
6.7292 | 81.7152 | 83.299 | 80.335 | 2.1559 | 2.0628 | 1.976
6.7333 | 81.7243 | 83.3 | 80.3352 | 2.156 | 2.063 | 1.976
6.7375 | 81.7237 | 83.3009 | 80.3352 | 2.1561 | 2.0632 | 1.976
6.7417 | 81.7141 | 83.3018 | 80.3353 | 2.1562 | 2.0635 | 1.976
6.7458 | 81.7187 | 83.3027 | 80.3355 | 2.1563 | 2.0637 | 1.976
6.75 | 81.7138 | 83.3035 | 80.3354 | 2.1563 | 2.0639 | 1.976
6.7542 | 81.7111 | 83.3043 | 80.3354 | 2.1564 | 2.0642 | 1.976
6.7583 | 81.7199 | 83.3051 | 80.3355 | 2.1565 | 2.0644 | 1.976
6.7625 | 81.7171 | 83.306 | 80.3354 | 2.1565 | 2.0646 | 1.976
6.7667 | 81.7132 | 83.3068 | 80.3355 | 2.1567 | 2.0648 | 1.976
6.7708 | 81.7175 | 83.3077 | 80.336 | 2.1567 | 2.065 | 1.976
6.775 | 81.7154 | 83.3084 | 80.3361 | 2.1568 | 2.0652 | 1.976
6.7792 | 81.7129 | 83.3092 | 80.3361 | 2.1568 | 2.0654 | 1.976
6.7833 | 81.7201 | 83.3101 | 80.3363 | 2.1569 | 2.0656 | 1.976
6.7875 | 81.7159 | 83.311 | 80.3362 | 2.157 | 2.0658 | 1.976
6.7917 | 81.7142 | 83.3121 | 80.3365 | 2.157 | 2.066 | 1.976
6.7958 | 81.7128 | 83.3131 | 80.3369 | 2.1571 | 2.0662 | 1.976
6.8 | 81.7125 | 83.3146 | 80.337 | 2.1571 | 2.0664 | 1.976
6.8042 | 81.7107 | 83.3158 | 80.3375 | 2.1572 | 2.0666 | 1.976
6.8083 | 81.7143 | 83.3167 | 80.338 | 2.1573 | 2.0668 | 1.976
6.8125 | 81.7161 | 83.318 | 80.3383 | 2.1573 | 2.0669 | 1.9759
6.8167 | 81.716 | 83.3187 | 80.3388 | 2.1574 | 2.0671 | 1.9759
6.8208 | 81.714 | 83.3194 | 80.3392 | 2.1574 | 2.0672 | 1.9759
6.825 | 81.7125 | 83.3205 | 80.3394 | 2.1575 | 2.0674 | 1.9759
6.8292 | 81.7112 | 83.3204 | 80.3386 | 2.1575 | 2.0676 | 1.9759
6.8333 | 81.7114 | 83.3208 | 80.338 | 2.1576 | 2.0677 | 1.9759
6.8375 | 81.7141 | 83.3233 | 80.3396 | 2.1576 | 2.0678 | 1.9759
6.8417 | 81.7171 | 83.326 | 80.3411 | 2.1576 | 2.068 | 1.9759
6.8458 | 81.7128 | 83.3279 | 80.3414 | 2.1577 | 2.0681 | 1.9759
6.85 | 81.7073 | 83.3287 | 80.3413 | 2.1578 | 2.0682 | 1.9759
6.8542 | 81.7173 | 83.3411 | 80.3512 | 2.1577 | 2.0683 | 1.9758
6.8583 | 81.7268 | 83.3529 | 80.3606 | 2.1576 | 2.0683 | 1.9757
6.8625 | 81.7297 | 83.3515 | 80.3592 | 2.1578 | 2.0684 | 1.9757
6.8667 | 81.7393 | 83.3508 | 80.3589 | 2.1579 | 2.0685 | 1.9757
6.8708 | 81.7472 | 83.342 | 80.3583 | 2.1577 | 2.0685 | 1.9756
6.875 | 81.7578 | 83.3331 | 80.3595 | 2.1576 | 2.0685 | 1.9754
6.8792 | 81.7456 | 83.294 | 80.3328 | 2.158 | 2.069 | 1.9757
6.8833 | 81.7316 | 83.2562 | 80.3087 | 2.1583 | 2.0694 | 1.976
6.8875 | 81.7192 | 83.2537 | 80.3087 | 2.158 | 2.0695 | 1.9758
6.8917 | 81.7143 | 83.2516 | 80.3063 | 2.1578 | 2.0696 | 1.9756
6.8958 | 81.6922 | 83.2781 | 80.3132 | 2.1583 | 2.0701 | 1.976
6.9 | 81.6515 | 83.3045 | 80.3148 | 2.1588 | 2.0707 | 1.9764
6.9042 | 81.663 | 83.3762 | 80.3549 | 2.1586 | 2.0702 | 1.9758
6.9083 | 81.671 | 83.4443 | 80.3905 | 2.1582 | 2.0697 | 1.9754
6.9125 | 81.6665 | 83.4535 | 80.392 | 2.1589 | 2.07 | 1.9757
6.9167 | 81.6658 | 83.4615 | 80.3988 | 2.1596 | 2.0703 | 1.976
6.9208 | 81.6358 | 83.4078 | 80.3681 | 2.1596 | 2.0696 | 1.9755
6.925 | 81.6185 | 83.3568 | 80.3453 | 2.1593 | 2.069 | 1.975
6.9292 | 81.6702 | 83.3279 | 80.3372 | 2.1595 | 2.0695 | 1.9755
6.9333 | 81.7389 | 83.2999 | 80.3282 | 2.1597 | 2.0699 | 1.9759
6.9375 | 81.7532 | 83.3073 | 80.329 | 2.1598 | 2.0696 | 1.9756
6.9417 | 81.7799 | 83.315 | 80.3236 | 2.16 | 2.0694 | 1.9753
6.9458 | 81.7396 | 83.3732 | 80.3718 | 2.1603 | 2.0696 | 1.9753
6.95 | 81.7265 | 83.429 | 80.4158 | 2.1604 | 2.0698 | 1.9754
6.9542 | 81.6754 | 83.3742 | 80.3829 | 2.1604 | 2.0699 | 1.9754
6.9583 | 81.6535 | 83.3223 | 80.3599 | 2.1603 | 2.07 | 1.9754
6.9625 | 81.6715 | 83.2972 | 80.3587 | 2.1602 | 2.0699 | 1.9751
6.9667 | 81.7504 | 83.2729 | 80.3593 | 2.1598 | 2.0699 | 1.9749
6.9708 | 81.8012 | 83.2726 | 80.3581 | 2.1598 | 2.0705 | 1.9752
6.975 | 81.8731 | 83.2735 | 80.353 | 2.1602 | 2.071 | 1.9754
6.9792 | 81.8987 | 83.2814 | 80.3534 | 2.1604 | 2.0711 | 1.9752
6.9833 | 81.8706 | 83.2896 | 80.3538 | 2.1605 | 2.0711 | 1.9749
6.9875 | 81.8581 | 83.2766 | 80.3516 | 2.1606 | 2.0718 | 1.9752
6.9917 | 81.8311 | 83.2609 | 80.3528 | 2.1604 | 2.0725 | 1.9755
6.9958 | 81.8187 | 83.2185 | 80.3176 | 2.1603 | 2.0728 | 1.9755
7 | 81.7983 | 83.177 | 80.2838 | 2.1604 | 2.0731 | 1.9755
7.0042 | 81.7841 | 83.2466 | 80.3224 | 2.1605 | 2.0733 | 1.9755
7.0083 | 81.7417 | 83.3141 | 80.3492 | 2.1606 | 2.0736 | 1.9754
7.0125 | 81.6956 | 83.3324 | 80.3474 | 2.1608 | 2.0741 | 1.9757
7.0167 | 81.6401 | 83.35 | 80.3481 | 2.1608 | 2.0746 | 1.976
7.0208 | 81.6283 | 83.333 | 80.3304 | 2.161 | 2.0744 | 1.9757
7.025 | 81.6003 | 83.3158 | 80.3176 | 2.1612 | 2.0742 | 1.9756
7.0292 | 81.5854 | 83.3646 | 80.3406 | 2.1616 | 2.0742 | 1.9757
7.0333 | 81.5786 | 83.4123 | 80.3558 | 2.1621 | 2.0742 | 1.9758
7.0375 | 81.5543 | 83.4401 | 80.3546 | 2.1625 | 2.0739 | 1.9757
7.0417 | 81.5509 | 83.4696 | 80.3529 | 2.1629 | 2.0737 | 1.9757
7.0458 | 81.5589 | 83.4882 | 80.3645 | 2.1633 | 2.0731 | 1.9755
7.05 | 81.5651 | 83.5056 | 80.3787 | 2.1638 | 2.0726 | 1.9754
7.0542 | 81.5506 | 83.4883 | 80.366 | 2.1645 | 2.0722 | 1.9755
7.0583 | 81.5326 | 83.4712 | 80.3569 | 2.1649 | 2.0718 | 1.9756
7.0625 | 81.5218 | 83.4865 | 80.3614 | 2.1653 | 2.071 | 1.9753
7.0667 | 81.5287 | 83.502 | 80.3622 | 2.1656 | 2.0702 | 1.9751
7.0708 | 81.5654 | 83.5284 | 80.3861 | 2.166 | 2.0697 | 1.9751
7.075 | 81.5892 | 83.5533 | 80.4086 | 2.1664 | 2.0693 | 1.9751
7.0792 | 81.6054 | 83.4879 | 80.3783 | 2.1666 | 2.0688 | 1.9751
7.0833 | 81.6263 | 83.4248 | 80.3589 | 2.1666 | 2.0684 | 1.9751
7.0875 | 81.6521 | 83.4232 | 80.3672 | 2.1665 | 2.0678 | 1.9749
7.0917 | 81.701 | 83.4221 | 80.37 | 2.1663 | 2.0671 | 1.9747
7.0958 | 81.7447 | 83.4462 | 80.3905 | 2.1663 | 2.0671 | 1.9747
7.1 | 81.7987 | 83.4704 | 80.4066 | 2.1665 | 2.067 | 1.9748
7.1042 | 81.8205 | 83.4031 | 80.3799 | 2.1666 | 2.0669 | 1.9747
7.1083 | 81.8348 | 83.3372 | 80.3647 | 2.1667 | 2.0668 | 1.9747
7.1125 | 81.8474 | 83.3185 | 80.3684 | 2.1666 | 2.0667 | 1.9746
7.1167 | 81.8572 | 83.2987 | 80.3685 | 2.1665 | 2.0665 | 1.9745
7.1208 | 81.8737 | 83.315 | 80.3824 | 2.1664 | 2.0669 | 1.9746
7.125 | 81.9033 | 83.3315 | 80.3905 | 2.1662 | 2.0672 | 1.9746
7.1292 | 81.9391 | 83.286 | 80.3786 | 2.1658 | 2.0676 | 1.9746
7.1333 | 81.953 | 83.2419 | 80.3747 | 2.1655 | 2.068 | 1.9745
7.1375 | 81.9538 | 83.2091 | 80.3695 | 2.1653 | 2.0684 | 1.9745
7.1417 | 81.9421 | 83.1741 | 80.3643 | 2.165 | 2.0689 | 1.9745
7.1458 | 81.9133 | 83.1837 | 80.3747 | 2.1647 | 2.0696 | 1.9745
7.15 | 81.8951 | 83.1921 | 80.3788 | 2.1644 | 2.0703 | 1.9745
7.1542 | 81.8954 | 83.1638 | 80.3763 | 2.1643 | 2.0712 | 1.9745
7.1583 | 81.8867 | 83.1393 | 80.3785 | 2.1642 | 2.0722 | 1.9746
7.1625 | 81.8712 | 83.0984 | 80.3654 | 2.1642 | 2.0731 | 1.9746
7.1667 | 81.8497 | 83.0575 | 80.3551 | 2.1643 | 2.0741 | 1.9746
7.1708 | 81.8299 | 83.0737 | 80.3675 | 2.1642 | 2.0751 | 1.9746
7.175 | 81.8032 | 83.0878 | 80.3726 | 2.1642 | 2.0761 | 1.9745
7.1792 | 81.7927 | 83.0793 | 80.3747 | 2.1642 | 2.0775 | 1.9746
7.1833 | 81.7727 | 83.0744 | 80.3796 | 2.1642 | 2.0788 | 1.9746
7.1875 | 81.7453 | 83.0365 | 80.3632 | 2.1643 | 2.08 | 1.9747
7.1917 | 81.715 | 82.9985 | 80.3515 | 2.1644 | 2.0812 | 1.9747
7.1958 | 81.6837 | 83.0184 | 80.3634 | 2.1643 | 2.0825 | 1.9746
7.2 | 81.6572 | 83.0358 | 80.368 | 2.1642 | 2.0837 | 1.9746
7.2042 | 81.6409 | 83.0378 | 80.371 | 2.1642 | 2.0852 | 1.9747
7.2083 | 81.6263 | 83.0434 | 80.3756 | 2.1643 | 2.0866 | 1.9748
7.2125 | 81.6174 | 83.0147 | 80.3608 | 2.1646 | 2.0879 | 1.9748
7.2167 | 81.5958 | 82.9864 | 80.3507 | 2.1648 | 2.0892 | 1.9748
7.2208 | 81.5889 | 83.0104 | 80.3618 | 2.165 | 2.0905 | 1.9747
7.225 | 81.5855 | 83.0325 | 80.3668 | 2.1652 | 2.0918 | 1.9747
7.2292 | 81.5803 | 83.0391 | 80.3675 | 2.1655 | 2.0932 | 1.9748
7.2333 | 81.5807 | 83.0479 | 80.3695 | 2.1658 | 2.0947 | 1.9749
7.2375 | 81.5689 | 83.031 | 80.3591 | 2.1661 | 2.0959 | 1.9748
7.2417 | 81.5566 | 83.014 | 80.3519 | 2.1664 | 2.0971 | 1.9748
7.2458 | 81.5616 | 83.0398 | 80.3624 | 2.1667 | 2.0983 | 1.9748
7.25 | 81.5678 | 83.0649 | 80.368 | 2.1669 | 2.0994 | 1.9748
7.2542 | 81.5666 | 83.0714 | 80.366 | 2.1673 | 2.1007 | 1.9749
7.2583 | 81.5618 | 83.0789 | 80.3657 | 2.1676 | 2.102 | 1.9749
7.2625 | 81.5535 | 83.0702 | 80.3594 | 2.1679 | 2.103 | 1.9749
7.2667 | 81.5415 | 83.0608 | 80.3551 | 2.1681 | 2.1041 | 1.9749
7.2708 | 81.5522 | 83.0837 | 80.3636 | 2.1684 | 2.1051 | 1.9749
7.275 | 81.5587 | 83.1066 | 80.3686 | 2.1687 | 2.1061 | 1.9749
7.2792 | 81.5571 | 83.111 | 80.3656 | 2.169 | 2.1072 | 1.9749
7.2833 | 81.5523 | 83.1154 | 80.3642 | 2.1693 | 2.1082 | 1.9749
7.2875 | 81.5434 | 83.111 | 80.3608 | 2.1695 | 2.1091 | 1.9749
7.2917 | 81.5381 | 83.1055 | 80.3585 | 2.1697 | 2.11 | 1.9749
7.2958 | 81.544 | 83.123 | 80.3646 | 2.17 | 2.1109 | 1.9749
7.3 | 81.5521 | 83.1413 | 80.3683 | 2.1702 | 2.1117 | 1.9749
7.3042 | 81.5475 | 83.1442 | 80.3657 | 2.1705 | 2.1126 | 1.9749
7.3083 | 81.5405 | 83.1469 | 80.3643 | 2.1708 | 2.1135 | 1.9749
7.3125 | 81.5403 | 83.1451 | 80.3626 | 2.171 | 2.1142 | 1.9749
7.3167 | 81.5316 | 83.1421 | 80.3616 | 2.1712 | 2.115 | 1.9749
7.3208 | 81.5414 | 83.1542 | 80.3655 | 2.1714 | 2.1157 | 1.9749
7.325 | 81.5431 | 83.1664 | 80.3679 | 2.1716 | 2.1165 | 1.9749
7.3292 | 81.5403 | 83.1675 | 80.3659 | 2.1718 | 2.1172 | 1.9749
7.3333 | 81.5329 | 83.1677 | 80.365 | 2.1721 | 2.118 | 1.9749
7.3375 | 81.5341 | 83.1655 | 80.3642 | 2.1722 | 2.1187 | 1.9749
7.3417 | 81.5287 | 83.1628 | 80.3637 | 2.1725 | 2.1193 | 1.9749
7.3458 | 81.5325 | 83.17 | 80.3661 | 2.1726 | 2.12 | 1.9749
7.35 | 81.5355 | 83.1783 | 80.3674 | 2.1729 | 2.1207 | 1.9749
7.3542 | 81.5287 | 83.1802 | 80.3665 | 2.173 | 2.1213 | 1.9749
7.3583 | 81.5299 | 83.1818 | 80.3663 | 2.1733 | 2.122 | 1.9749
7.3625 | 81.5271 | 83.1817 | 80.366 | 2.1734 | 2.1226 | 1.9748
7.3667 | 81.5257 | 83.1809 | 80.366 | 2.1737 | 2.1232 | 1.9748
7.3708 | 81.5282 | 83.1855 | 80.367 | 2.1738 | 2.1238 | 1.9748
7.375 | 81.5275 | 83.191 | 80.3675 | 2.174 | 2.1244 | 1.9748
7.3792 | 81.5247 | 83.1936 | 80.3675 | 2.1741 | 2.125 | 1.9748
7.3833 | 81.5257 | 83.1964 | 80.3677 | 2.1744 | 2.1256 | 1.9748
7.3875 | 81.5218 | 83.1982 | 80.3681 | 2.1745 | 2.1262 | 1.9748
7.3917 | 81.5221 | 83.1993 | 80.3683 | 2.1747 | 2.1267 | 1.9748
7.3958 | 81.5234 | 83.2029 | 80.3688 | 2.1748 | 2.1272 | 1.9748
7.4 | 81.5207 | 83.2067 | 80.3693 | 2.175 | 2.1278 | 1.9748
7.4042 | 81.5189 | 83.2085 | 80.3693 | 2.1751 | 2.1283 | 1.9748
7.4083 | 81.5174 | 83.2105 | 80.3695 | 2.1753 | 2.1288 | 1.9748
7.4125 | 81.5136 | 83.2122 | 80.3694 | 2.1754 | 2.1293 | 1.9748
7.4167 | 81.5158 | 83.2136 | 80.3698 | 2.1756 | 2.1298 | 1.9747
7.4208 | 81.5202 | 83.2167 | 80.3709 | 2.1757 | 2.1302 | 1.9747
7.425 | 81.5158 | 83.2195 | 80.3715 | 2.1759 | 2.1307 | 1.9747
7.4292 | 81.5166 | 83.2212 | 80.372 | 2.176 | 2.1312 | 1.9747
7.4333 | 81.5155 | 83.2226 | 80.3724 | 2.1761 | 2.1316 | 1.9747
7.4375 | 81.5095 | 83.2233 | 80.373 | 2.1762 | 2.1321 | 1.9747
7.4417 | 81.5163 | 83.2242 | 80.3734 | 2.1764 | 2.1325 | 1.9747
7.4458 | 81.5183 | 83.2259 | 80.3736 | 2.1765 | 2.1329 | 1.9747
7.45 | 81.5158 | 83.2273 | 80.374 | 2.1766 | 2.1333 | 1.9746
7.4542 | 81.5154 | 83.2285 | 80.3739 | 2.1768 | 2.1338 | 1.9746
7.4583 | 81.513 | 83.2293 | 80.3744 | 2.1769 | 2.1342 | 1.9746
7.4625 | 81.5064 | 83.2295 | 80.3752 | 2.1769 | 2.1346 | 1.9746
7.4667 | 81.5136 | 83.2301 | 80.3756 | 2.1771 | 2.135 | 1.9746
7.4708 | 81.5137 | 83.2315 | 80.376 | 2.1772 | 2.1354 | 1.9746
7.475 | 81.513 | 83.2327 | 80.3764 | 2.1773 | 2.1358 | 1.9746
7.4792 | 81.5124 | 83.2341 | 80.3772 | 2.1774 | 2.1362 | 1.9745
7.4833 | 81.5086 | 83.2351 | 80.3778 | 2.1775 | 2.1366 | 1.9745
7.4875 | 81.5098 | 83.2356 | 80.3777 | 2.1775 | 2.1369 | 1.9745
7.4917 | 81.511 | 83.2364 | 80.3783 | 2.1777 | 2.1373 | 1.9745
7.4958 | 81.5158 | 83.2373 | 80.3787 | 2.1777 | 2.1377 | 1.9745
7.5 | 81.5106 | 83.2383 | 80.379 | 2.1779 | 2.138 | 1.9745
7.5042 | 81.5093 | 83.24 | 80.38 | 2.1779 | 2.1384 | 1.9744
7.5083 | 81.5087 | 83.2413 | 80.3806 | 2.178 | 2.1388 | 1.9744
7.5125 | 81.5073 | 83.2423 | 80.3807 | 2.178 | 2.1391 | 1.9744
7.5167 | 81.5127 | 83.2435 | 80.3812 | 2.1782 | 2.1394 | 1.9744
7.5208 | 81.5138 | 83.2443 | 80.3812 | 2.1782 | 2.1398 | 1.9744
7.525 | 81.5121 | 83.2453 | 80.3815 | 2.1783 | 2.1401 | 1.9744
7.5292 | 81.5101 | 83.247 | 80.3822 | 2.1784 | 2.1404 | 1.9743
7.5333 | 81.5117 | 83.2484 | 80.3827 | 2.1784 | 2.1408 | 1.9743
7.5375 | 81.509 | 83.25 | 80.3836 | 2.1785 | 2.1411 | 1.9743
7.5417 | 81.5102 | 83.2517 | 80.3841 | 2.1786 | 2.1414 | 1.9743
7.5458 | 81.5146 | 83.2529 | 80.3843 | 2.1786 | 2.1417 | 1.9743
7.55 | 81.5073 | 83.2543 | 80.3849 | 2.1787 | 2.142 | 1.9743
7.5542 | 81.5104 | 83.2555 | 80.3851 | 2.1787 | 2.1422 | 1.9742
7.5583 | 81.5109 | 83.2566 | 80.3856 | 2.1788 | 2.1425 | 1.9742
7.5625 | 81.5094 | 83.2582 | 80.3867 | 2.1788 | 2.1428 | 1.9742
7.5667 | 81.5104 | 83.2598 | 80.3872 | 2.1789 | 2.1431 | 1.9742
7.5708 | 81.5121 | 83.2612 | 80.3878 | 2.1789 | 2.1433 | 1.9742
7.575 | 81.5114 | 83.2627 | 80.3885 | 2.179 | 2.1436 | 1.9741
7.5792 | 81.5147 | 83.2636 | 80.3885 | 2.179 | 2.1438 | 1.9741
7.5833 | 81.514 | 83.2644 | 80.3891 | 2.1791 | 2.1441 | 1.9741
7.5875 | 81.515 | 83.2655 | 80.39 | 2.1791 | 2.1443 | 1.9741
7.5917 | 81.507 | 83.2667 | 80.3905 | 2.1792 | 2.1445 | 1.9741
7.5958 | 81.5066 | 83.2679 | 80.3912 | 2.1792 | 2.1448 | 1.974
7.6 | 81.5119 | 83.2692 | 80.3919 | 2.1792 | 2.145 | 1.974
7.6042 | 81.512 | 83.2703 | 80.3922 | 2.1792 | 2.1452 | 1.974
7.6083 | 81.5195 | 83.2712 | 80.3929 | 2.1793 | 2.1454 | 1.974
7.6125 | 81.5196 | 83.2718 | 80.3933 | 2.1793 | 2.1456 | 1.974
7.6167 | 81.5145 | 83.2724 | 80.3936 | 2.1794 | 2.1458 | 1.9739
7.6208 | 81.5166 | 83.273 | 80.394 | 2.1794 | 2.146 | 1.9739
7.625 | 81.5123 | 83.2736 | 80.3942 | 2.1794 | 2.1462 | 1.9739
7.6292 | 81.5144 | 83.2744 | 80.3945 | 2.1795 | 2.1464 | 1.9739
7.6333 | 81.5133 | 83.2751 | 80.3951 | 2.1795 | 2.1466 | 1.9739
7.6375 | 81.5126 | 83.2762 | 80.3957 | 2.1795 | 2.1468 | 1.9738
7.6417 | 81.5116 | 83.2771 | 80.3964 | 2.1795 | 2.147 | 1.9738
7.6458 | 81.5145 | 83.2782 | 80.3973 | 2.1795 | 2.1472 | 1.9738
7.65 | 81.5123 | 83.2789 | 80.3979 | 2.1795 | 2.1474 | 1.9738
7.6542 | 81.5151 | 83.2801 | 80.3985 | 2.1796 | 2.1475 | 1.9738
7.6583 | 81.5175 | 83.2816 | 80.3994 | 2.1796 | 2.1477 | 1.9737
7.6625 | 81.5151 | 83.2831 | 80.4001 | 2.1796 | 2.1479 | 1.9737
7.6667 | 81.5166 | 83.2849 | 80.4011 | 2.1796 | 2.148 | 1.9737
7.6708 | 81.513 | 83.2855 | 80.4015 | 2.1797 | 2.1482 | 1.9737
7.675 | 81.5127 | 83.2863 | 80.4016 | 2.1797 | 2.1483 | 1.9736
7.6792 | 81.5133 | 83.2883 | 80.4033 | 2.1797 | 2.1484 | 1.9736
7.6833 | 81.5151 | 83.2898 | 80.405 | 2.1797 | 2.1486 | 1.9736
7.6875 | 81.519 | 83.2908 | 80.4055 | 2.1797 | 2.1487 | 1.9736
7.6917 | 81.5194 | 83.2912 | 80.4062 | 2.1797 | 2.1488 | 1.9735
7.6958 | 81.5222 | 83.2909 | 80.4068 | 2.1798 | 2.1489 | 1.9735
7.7 | 81.521 | 83.2914 | 80.4072 | 2.1798 | 2.1491 | 1.9735
7.7042 | 81.5191 | 83.2882 | 80.4044 | 2.1798 | 2.1492 | 1.9735
7.7083 | 81.517 | 83.2854 | 80.402 | 2.1799 | 2.1494 | 1.9735
7.7125 | 81.5173 | 83.2887 | 80.4043 | 2.1798 | 2.1494 | 1.9734
7.7167 | 81.5206 | 83.2918 | 80.4064 | 2.1798 | 2.1495 | 1.9734
7.7208 | 81.5127 | 83.2963 | 80.4066 | 2.1799 | 2.1497 | 1.9734
7.725 | 81.5043 | 83.3 | 80.4058 | 2.1801 | 2.1498 | 1.9735
7.7292 | 81.5095 | 83.323 | 80.4221 | 2.1799 | 2.1497 | 1.9733
7.7333 | 81.5201 | 83.3453 | 80.437 | 2.1798 | 2.1495 | 1.9731
7.7375 | 81.523 | 83.3446 | 80.4356 | 2.1801 | 2.1497 | 1.9731
7.7417 | 81.5215 | 83.3444 | 80.4361 | 2.1803 | 2.1498 | 1.9732
7.7458 | 81.5426 | 83.3291 | 80.4357 | 2.1799 | 2.1496 | 1.9729
7.75 | 81.5582 | 83.3133 | 80.4386 | 2.1796 | 2.1494 | 1.9726
7.7542 | 81.5778 | 83.2613 | 80.4098 | 2.18 | 2.1499 | 1.973
7.7583 | 81.5915 | 83.2115 | 80.3848 | 2.1803 | 2.1505 | 1.9733
7.7625 | 81.5867 | 83.2062 | 80.3857 | 2.1801 | 2.1504 | 1.973
7.7667 | 81.5999 | 83.2018 | 80.3831 | 2.1798 | 2.1504 | 1.9727
7.7708 | 81.5834 | 83.2384 | 80.3966 | 2.1801 | 2.1511 | 1.9732
7.775 | 81.5647 | 83.2743 | 80.403 | 2.1807 | 2.1517 | 1.9736
7.7792 | 81.552 | 83.3337 | 80.429 | 2.1804 | 2.1512 | 1.973
7.7833 | 81.5255 | 83.3903 | 80.4516 | 2.1799 | 2.1508 | 1.9726
7.7875 | 81.5116 | 83.3961 | 80.4532 | 2.1803 | 2.1511 | 1.9729
7.7917 | 81.4993 | 83.4008 | 80.4611 | 2.1806 | 2.1514 | 1.9732
7.7958 | 81.4786 | 83.3447 | 80.4252 | 2.1805 | 2.1509 | 1.9728
7.8 | 81.4419 | 83.2913 | 80.3967 | 2.1806 | 2.1504 | 1.9725
7.8042 | 81.4653 | 83.3012 | 80.4105 | 2.1806 | 2.1506 | 1.9727
7.8083 | 81.4999 | 83.31 | 80.4191 | 2.1808 | 2.1508 | 1.9729
7.8125 | 81.5374 | 83.3261 | 80.4183 | 2.1807 | 2.1506 | 1.9728
7.8167 | 81.5297 | 83.342 | 80.4126 | 2.1809 | 2.1505 | 1.9727
7.8208 | 81.5435 | 83.3789 | 80.4446 | 2.1812 | 2.1503 | 1.9726
7.825 | 81.5078 | 83.4142 | 80.4757 | 2.1812 | 2.1501 | 1.9724
7.8292 | 81.4731 | 83.3635 | 80.4511 | 2.1814 | 2.1502 | 1.9726
7.8333 | 81.4302 | 83.315 | 80.4351 | 2.1817 | 2.1503 | 1.9727
7.8375 | 81.413 | 83.3006 | 80.4365 | 2.1818 | 2.15 | 1.9723
7.8417 | 81.422 | 83.2878 | 80.4371 | 2.1818 | 2.1496 | 1.972
7.8458 | 81.4527 | 83.3123 | 80.4574 | 2.1819 | 2.1499 | 1.9722
7.85 | 81.5212 | 83.3374 | 80.4732 | 2.182 | 2.1502 | 1.9723
7.8542 | 81.5475 | 83.3055 | 80.4544 | 2.1821 | 2.1502 | 1.9721
7.8583 | 81.5807 | 83.2752 | 80.4423 | 2.1823 | 2.1502 | 1.9719
7.8625 | 81.5987 | 83.2519 | 80.4445 | 2.1823 | 2.1505 | 1.972
7.8667 | 81.6195 | 83.2265 | 80.4494 | 2.1822 | 2.1509 | 1.972
7.8708 | 81.6461 | 83.1997 | 80.4311 | 2.1821 | 2.1513 | 1.9721
7.875 | 81.6954 | 83.1741 | 80.4112 | 2.1819 | 2.1518 | 1.9721
7.8792 | 81.7181 | 83.2137 | 80.4327 | 2.182 | 2.152 | 1.972
7.8833 | 81.7454 | 83.2526 | 80.4467 | 2.182 | 2.1521 | 1.9718
7.8875 | 81.7392 | 83.2534 | 80.4466 | 2.1821 | 2.1528 | 1.9721
7.8917 | 81.6866 | 83.2524 | 80.4499 | 2.182 | 2.1535 | 1.9723
7.8958 | 81.6716 | 83.2221 | 80.4255 | 2.1819 | 2.1536 | 1.9721
7.9 | 81.6511 | 83.1922 | 80.4049 | 2.1817 | 2.1537 | 1.972
7.9042 | 81.6399 | 83.2576 | 80.4359 | 2.1818 | 2.1538 | 1.972
7.9083 | 81.6325 | 83.3217 | 80.4556 | 2.1819 | 2.154 | 1.972
7.9125 | 81.6059 | 83.3445 | 80.4519 | 2.1819 | 2.1541 | 1.9721
7.9167 | 81.5847 | 83.3684 | 80.45 | 2.182 | 2.1543 | 1.9722
7.9208 | 81.5563 | 83.3679 | 80.4458 | 2.1819 | 2.1539 | 1.9719
7.925 | 81.5318 | 83.367 | 80.4457 | 2.1819 | 2.1535 | 1.9718
7.9292 | 81.4966 | 83.3932 | 80.4538 | 2.1821 | 2.1533 | 1.9719
7.9333 | 81.4538 | 83.4186 | 80.4584 | 2.1822 | 2.1531 | 1.9719
7.9375 | 81.4156 | 83.442 | 80.4579 | 2.1823 | 2.1525 | 1.9718
7.9417 | 81.4115 | 83.4659 | 80.4559 | 2.1825 | 2.1519 | 1.9717
7.9458 | 81.4167 | 83.4831 | 80.4698 | 2.1826 | 2.1513 | 1.9716
7.95 | 81.4249 | 83.4985 | 80.4847 | 2.183 | 2.1508 | 1.9715
7.9542 | 81.4229 | 83.4663 | 80.4693 | 2.1834 | 2.1503 | 1.9715
7.9583 | 81.3962 | 83.4354 | 80.4601 | 2.1838 | 2.1498 | 1.9715
7.9625 | 81.3711 | 83.4479 | 80.4663 | 2.184 | 2.149 | 1.9713
7.9667 | 81.3665 | 83.4615 | 80.4678 | 2.1844 | 2.1482 | 1.9712
7.9708 | 81.3833 | 83.485 | 80.4864 | 2.1846 | 2.1477 | 1.9712
7.975 | 81.4127 | 83.508 | 80.5025 | 2.1849 | 2.1473 | 1.9711
7.9792 | 81.4181 | 83.4477 | 80.4789 | 2.1852 | 2.1469 | 1.9711
7.9833 | 81.4149 | 83.3884 | 80.466 | 2.1855 | 2.1465 | 1.9711
7.9875 | 81.4127 | 83.3854 | 80.4738 | 2.1856 | 2.1459 | 1.9709
7.9917 | 81.4219 | 83.3824 | 80.4766 | 2.1856 | 2.1453 | 1.9708
7.9958 | 81.453 | 83.4034 | 80.4919 | 2.1856 | 2.1452 | 1.9708
8 | 81.4938 | 83.4247 | 80.5025 | 2.1855 | 2.1451 | 1.9708
8.0042 | 81.5362 | 83.3701 | 80.4865 | 2.1855 | 2.145 | 1.9707
8.0083 | 81.582 | 83.3158 | 80.4802 | 2.1855 | 2.1449 | 1.9706
8.0125 | 81.6184 | 83.296 | 80.4828 | 2.1856 | 2.1448 | 1.9706
8.0167 | 81.6485 | 83.2741 | 80.4829 | 2.1857 | 2.1447 | 1.9705
8.0208 | 81.6579 | 83.2853 | 80.493 | 2.1858 | 2.1449 | 1.9705
8.025 | 81.6685 | 83.296 | 80.4977 | 2.1858 | 2.1452 | 1.9704
8.0292 | 81.6785 | 83.2534 | 80.4909 | 2.1856 | 2.1456 | 1.9704
8.0333 | 81.703 | 83.2131 | 80.491 | 2.1854 | 2.146 | 1.9704
8.0375 | 81.7221 | 83.1797 | 80.4862 | 2.1853 | 2.1464 | 1.9703
8.0417 | 81.7359 | 83.1454 | 80.4821 | 2.1851 | 2.1468 | 1.9703
8.0458 | 81.7325 | 83.1588 | 80.493 | 2.1849 | 2.1475 | 1.9703
8.05 | 81.7343 | 83.171 | 80.4973 | 2.1846 | 2.1481 | 1.9702
8.0542 | 81.7464 | 83.1479 | 80.497 | 2.1842 | 2.149 | 1.9702
8.0583 | 81.7606 | 83.1278 | 80.501 | 2.1839 | 2.1498 | 1.9702
8.0625 | 81.7755 | 83.0895 | 80.4904 | 2.1836 | 2.1507 | 1.9702
8.0667 | 81.7758 | 83.0507 | 80.4834 | 2.1834 | 2.1515 | 1.9701
8.0708 | 81.7523 | 83.067 | 80.4945 | 2.1831 | 2.1524 | 1.9701
8.075 | 81.7354 | 83.0812 | 80.4983 | 2.1829 | 2.1533 | 1.97
8.0792 | 81.7261 | 83.0732 | 80.5014 | 2.1826 | 2.1545 | 1.97
8.0833 | 81.7216 | 83.0689 | 80.5069 | 2.1824 | 2.1557 | 1.97
8.0875 | 81.7235 | 83.0341 | 80.4947 | 2.1824 | 2.1568 | 1.97
8.0917 | 81.7062 | 82.9994 | 80.4872 | 2.1824 | 2.1578 | 1.97
8.0958 | 81.6933 | 83.0198 | 80.4979 | 2.1824 | 2.1589 | 1.9699
8.1 | 81.6829 | 83.038 | 80.502 | 2.1823 | 2.16 | 1.9698
8.1042 | 81.6709 | 83.0396 | 80.5048 | 2.1823 | 2.1613 | 1.9699
8.1083 | 81.665 | 83.0441 | 80.5091 | 2.1823 | 2.1626 | 1.9699
8.1125 | 81.6518 | 83.0199 | 80.4995 | 2.1823 | 2.1637 | 1.9698
8.1167 | 81.638 | 82.9958 | 80.4942 | 2.1823 | 2.1648 | 1.9698
8.1208 | 81.6292 | 83.021 | 80.5057 | 2.1823 | 2.1659 | 1.9697
8.125 | 81.6228 | 83.0447 | 80.5115 | 2.1822 | 2.1669 | 1.9697
8.1292 | 81.6138 | 83.0502 | 80.5125 | 2.1822 | 2.1682 | 1.9697
8.1333 | 81.6102 | 83.0575 | 80.5151 | 2.1823 | 2.1694 | 1.9697
8.1375 | 81.5953 | 83.0423 | 80.5085 | 2.1823 | 2.1704 | 1.9696
8.1417 | 81.5816 | 83.027 | 80.5051 | 2.1823 | 2.1714 | 1.9695
8.1458 | 81.5783 | 83.0518 | 80.5152 | 2.1822 | 2.1724 | 1.9695
8.15 | 81.5695 | 83.0759 | 80.5209 | 2.1821 | 2.1733 | 1.9694
8.1542 | 81.5677 | 83.081 | 80.5203 | 2.1822 | 2.1744 | 1.9694
8.1583 | 81.5645 | 83.0868 | 80.5215 | 2.1822 | 2.1754 | 1.9694
8.1625 | 81.5523 | 83.0779 | 80.518 | 2.1823 | 2.1762 | 1.9693
8.1667 | 81.5475 | 83.0684 | 80.5165 | 2.1823 | 2.1771 | 1.9692
8.1708 | 81.5388 | 83.0896 | 80.5248 | 2.1822 | 2.1779 | 1.9692
8.175 | 81.5421 | 83.1113 | 80.5298 | 2.1822 | 2.1787 | 1.9691
8.1792 | 81.5336 | 83.1154 | 80.529 | 2.1823 | 2.1796 | 1.9691
8.1833 | 81.5361 | 83.12 | 80.5296 | 2.1823 | 2.1804 | 1.9691
8.1875 | 81.5263 | 83.1158 | 80.5284 | 2.1823 | 2.1811 | 1.969
8.1917 | 81.5233 | 83.1104 | 80.5284 | 2.1823 | 2.1818 | 1.9689
8.1958 | 81.5237 | 83.1268 | 80.5348 | 2.1823 | 2.1825 | 1.9688
8.2 | 81.5212 | 83.1431 | 80.539 | 2.1823 | 2.1831 | 1.9688
8.2042 | 81.5233 | 83.1451 | 80.5384 | 2.1823 | 2.1838 | 1.9687
8.2083 | 81.5161 | 83.1462 | 80.5391 | 2.1824 | 2.1845 | 1.9687
8.2125 | 81.5174 | 83.1416 | 80.5385 | 2.1824 | 2.1851 | 1.9686
8.2167 | 81.5056 | 83.1362 | 80.5383 | 2.1824 | 2.1857 | 1.9686
8.2208 | 81.5101 | 83.1458 | 80.5422 | 2.1824 | 2.1863 | 1.9685
8.225 | 81.5011 | 83.1563 | 80.5444 | 2.1824 | 2.1868 | 1.9685
8.2292 | 81.5038 | 83.1578 | 80.5444 | 2.1824 | 2.1875 | 1.9684
8.2333 | 81.4961 | 83.1588 | 80.5453 | 2.1825 | 2.188 | 1.9684
8.2375 | 81.4973 | 83.1565 | 80.5456 | 2.1825 | 2.1886 | 1.9683
8.2417 | 81.491 | 83.1534 | 80.5464 | 2.1825 | 2.1891 | 1.9683
8.2458 | 81.4944 | 83.16 | 80.5492 | 2.1825 | 2.1896 | 1.9682
8.25 | 81.4898 | 83.1675 | 80.551 | 2.1825 | 2.1901 | 1.9682
8.2542 | 81.4919 | 83.1701 | 80.552 | 2.1825 | 2.1907 | 1.9681
8.2583 | 81.4908 | 83.1726 | 80.5534 | 2.1825 | 2.1912 | 1.9681
8.2625 | 81.4911 | 83.173 | 80.5548 | 2.1826 | 2.1916 | 1.968
8.2667 | 81.4911 | 83.1726 | 80.5562 | 2.1826 | 2.1921 | 1.9679
8.2708 | 81.493 | 83.1773 | 80.5581 | 2.1826 | 2.1926 | 1.9679
8.275 | 81.492 | 83.1827 | 80.5599 | 2.1826 | 2.193 | 1.9678
8.2792 | 81.4938 | 83.1849 | 80.5609 | 2.1826 | 2.1934 | 1.9678
8.2833 | 81.4923 | 83.1872 | 80.5624 | 2.1827 | 2.1939 | 1.9677
8.2875 | 81.4905 | 83.1887 | 80.5636 | 2.1827 | 2.1943 | 1.9677
8.2917 | 81.4911 | 83.1897 | 80.5652 | 2.1827 | 2.1947 | 1.9676
8.2958 | 81.4943 | 83.1937 | 80.5676 | 2.1827 | 2.195 | 1.9676
8.3 | 81.4919 | 83.1979 | 80.5695 | 2.1827 | 2.1954 | 1.9675
8.3042 | 81.4993 | 83.1998 | 80.5713 | 2.1827 | 2.1958 | 1.9674
8.3083 | 81.4967 | 83.2018 | 80.5729 | 2.1827 | 2.1961 | 1.9674
8.3125 | 81.4993 | 83.203 | 80.5745 | 2.1828 | 2.1965 | 1.9673
8.3167 | 81.5016 | 83.2039 | 80.5762 | 2.1828 | 2.1968 | 1.9673
8.3208 | 81.5066 | 83.2065 | 80.578 | 2.1828 | 2.1971 | 1.9672
8.325 | 81.5061 | 83.209 | 80.5798 | 2.1828 | 2.1974 | 1.9671
8.3292 | 81.515 | 83.2104 | 80.581 | 2.1828 | 2.1977 | 1.9671
8.3333 | 81.511 | 83.2115 | 80.5829 | 2.1828 | 2.198 | 1.967
8.3375 | 81.5152 | 83.2121 | 80.5851 | 2.1829 | 2.1983 | 1.9669
8.3417 | 81.5192 | 83.2128 | 80.5868 | 2.1828 | 2.1986 | 1.9669
8.3458 | 81.522 | 83.2148 | 80.5887 | 2.1828 | 2.1989 | 1.9668
8.35 | 81.5279 | 83.2166 | 80.5906 | 2.1829 | 2.1992 | 1.9667
8.3542 | 81.5306 | 83.2178 | 80.5923 | 2.1829 | 2.1995 | 1.9667
8.3583 | 81.532 | 83.2188 | 80.5942 | 2.1829 | 2.1997 | 1.9666
8.3625 | 81.5371 | 83.2191 | 80.5957 | 2.1829 | 2.2 | 1.9665
8.3667 | 81.5384 | 83.2197 | 80.5976 | 2.1829 | 2.2002 | 1.9665
8.3708 | 81.5491 | 83.2211 | 80.5995 | 2.1829 | 2.2005 | 1.9664
8.375 | 81.5482 | 83.2225 | 80.6013 | 2.1829 | 2.2007 | 1.9663
8.3792 | 81.5567 | 83.2241 | 80.6037 | 2.183 | 2.201 | 1.9663
8.3833 | 81.5554 | 83.2254 | 80.6057 | 2.183 | 2.2012 | 1.9662
8.3875 | 81.5602 | 83.2261 | 80.6072 | 2.183 | 2.2014 | 1.9661
8.3917 | 81.5659 | 83.227 | 80.6092 | 2.1829 | 2.2016 | 1.9661
8.3958 | 81.573 | 83.2281 | 80.611 | 2.1829 | 2.2019 | 1.966
8.4 | 81.5796 | 83.2292 | 80.6128 | 2.1829 | 2.2021 | 1.9659
8.4042 | 81.5855 | 83.2312 | 80.6152 | 2.183 | 2.2023 | 1.9658
8.4083 | 81.5928 | 83.2328 | 80.6173 | 2.1829 | 2.2025 | 1.9658
8.4125 | 81.595 | 83.2347 | 80.6197 | 2.1829 | 2.2027 | 1.9657
8.4167 | 81.6046 | 83.2369 | 80.6223 | 2.1829 | 2.2028 | 1.9656
8.4208 | 81.6109 | 83.2387 | 80.6245 | 2.1829 | 2.203 | 1.9655
8.425 | 81.6148 | 83.2406 | 80.6271 | 2.1829 | 2.2032 | 1.9654
8.4292 | 81.6258 | 83.2424 | 80.6294 | 2.1829 | 2.2033 | 1.9654
8.4333 | 81.6275 | 83.244 | 80.6317 | 2.1829 | 2.2035 | 1.9653
8.4375 | 81.6355 | 83.246 | 80.6346 | 2.1829 | 2.2036 | 1.9652
8.4417 | 81.6439 | 83.2482 | 80.637 | 2.1829 | 2.2037 | 1.9651
8.4458 | 81.6493 | 83.25 | 80.6395 | 2.1829 | 2.2039 | 1.965
8.45 | 81.6613 | 83.2519 | 80.6421 | 2.1828 | 2.204 | 1.9649
8.4542 | 81.6701 | 83.2531 | 80.644 | 2.1828 | 2.2041 | 1.9648
8.4583 | 81.6787 | 83.2541 | 80.6462 | 2.1828 | 2.2042 | 1.9648
8.4625 | 81.6868 | 83.2556 | 80.649 | 2.1828 | 2.2043 | 1.9647
8.4667 | 81.6906 | 83.2573 | 80.6513 | 2.1828 | 2.2044 | 1.9646
8.4708 | 81.6956 | 83.2591 | 80.6541 | 2.1828 | 2.2045 | 1.9645
8.475 | 81.7009 | 83.2611 | 80.6568 | 2.1827 | 2.2045 | 1.9644
8.4792 | 81.7067 | 83.2624 | 80.659 | 2.1827 | 2.2046 | 1.9643
8.4833 | 81.7118 | 83.2637 | 80.6617 | 2.1826 | 2.2047 | 1.9642
8.4875 | 81.7166 | 83.2655 | 80.6649 | 2.1825 | 2.2047 | 1.9641
8.4917 | 81.7225 | 83.2674 | 80.6679 | 2.1824 | 2.2048 | 1.964
8.4958 | 81.7247 | 83.2693 | 80.6712 | 2.1823 | 2.2048 | 1.9639
8.5 | 81.727 | 83.2714 | 80.6743 | 2.1822 | 2.2048 | 1.9638
8.5042 | 81.7312 | 83.2713 | 80.6757 | 2.1821 | 2.2049 | 1.9637
8.5083 | 81.7314 | 83.2709 | 80.6774 | 2.1819 | 2.2049 | 1.9636
8.5125 | 81.7259 | 83.2674 | 80.676 | 2.1818 | 2.205 | 1.9636
8.5167 | 81.7229 | 83.2639 | 80.6747 | 2.1817 | 2.205 | 1.9635
8.5208 | 81.72 | 83.2613 | 80.674 | 2.1816 | 2.2051 | 1.9634
8.525 | 81.7131 | 83.2585 | 80.673 | 2.1815 | 2.2051 | 1.9633
8.5292 | 81.7194 | 83.2604 | 80.6754 | 2.1815 | 2.2052 | 1.9633
8.5333 | 81.7229 | 83.2626 | 80.6778 | 2.1814 | 2.2052 | 1.9632
8.5375 | 81.7238 | 83.2648 | 80.6804 | 2.1813 | 2.2053 | 1.9632
8.5417 | 81.7277 | 83.2674 | 80.6831 | 2.1813 | 2.2054 | 1.9631
8.5458 | 81.7259 | 83.2685 | 80.685 | 2.1812 | 2.2054 | 1.963
8.55 | 81.7244 | 83.2696 | 80.6866 | 2.1811 | 2.2054 | 1.963
8.5542 | 81.7275 | 83.2742 | 80.6915 | 2.181 | 2.2054 | 1.9629
8.5583 | 81.7332 | 83.2783 | 80.6965 | 2.1809 | 2.2054 | 1.9628
8.5625 | 81.7336 | 83.2786 | 80.6975 | 2.1808 | 2.2055 | 1.9627
8.5667 | 81.7341 | 83.2786 | 80.6991 | 2.1807 | 2.2055 | 1.9627
8.5708 | 81.7413 | 83.2776 | 80.7016 | 2.1806 | 2.2055 | 1.9626
8.575 | 81.7457 | 83.2775 | 80.7043 | 2.1804 | 2.2054 | 1.9624
8.5792 | 81.7415 | 83.2696 | 80.6998 | 2.1804 | 2.2055 | 1.9624
8.5833 | 81.7383 | 83.2621 | 80.696 | 2.1803 | 2.2056 | 1.9624
8.5875 | 81.748 | 83.2662 | 80.7003 | 2.1801 | 2.2056 | 1.9623
8.5917 | 81.7466 | 83.2699 | 80.7039 | 2.1798 | 2.2055 | 1.9621
8.5958 | 81.7354 | 83.2795 | 80.7057 | 2.18 | 2.2056 | 1.9622
8.6 | 81.7251 | 83.2887 | 80.7054 | 2.18 | 2.2056 | 1.9622
8.6042 | 81.7285 | 83.3239 | 80.7276 | 2.1797 | 2.2053 | 1.9619
8.6083 | 81.7377 | 83.3579 | 80.7475 | 2.1794 | 2.2049 | 1.9616
8.6125 | 81.734 | 83.3587 | 80.7466 | 2.1798 | 2.2049 | 1.9617
8.6167 | 81.7192 | 83.3594 | 80.7483 | 2.18 | 2.2049 | 1.9618
8.6208 | 81.7151 | 83.3358 | 80.7465 | 2.1797 | 2.2044 | 1.9614
8.625 | 81.7192 | 83.312 | 80.7497 | 2.1792 | 2.204 | 1.9609
8.6292 | 81.7404 | 83.2572 | 80.7267 | 2.1793 | 2.2044 | 1.9613
8.6333 | 81.7537 | 83.2047 | 80.708 | 2.1796 | 2.2048 | 1.9616
8.6375 | 81.7666 | 83.1977 | 80.7099 | 2.1792 | 2.2046 | 1.9612
8.6417 | 81.7882 | 83.1918 | 80.7074 | 2.1787 | 2.2044 | 1.9608
8.6458 | 81.7921 | 83.2354 | 80.7293 | 2.1787 | 2.2049 | 1.9611
8.65 | 81.8107 | 83.2773 | 80.7434 | 2.1787 | 2.2054 | 1.9614
8.6542 | 81.8012 | 83.3122 | 80.754 | 2.1784 | 2.205 | 1.9609
8.6583 | 81.7731 | 83.3458 | 80.7638 | 2.1779 | 2.2046 | 1.9605
8.6625 | 81.7737 | 83.3469 | 80.7693 | 2.1779 | 2.2047 | 1.9606
8.6667 | 81.7697 | 83.3473 | 80.7809 | 2.1778 | 2.2049 | 1.9608
8.6708 | 81.7496 | 83.2996 | 80.749 | 2.1777 | 2.2045 | 1.9605
8.675 | 81.7442 | 83.2542 | 80.7224 | 2.1775 | 2.2042 | 1.9603
8.6792 | 81.738 | 83.2902 | 80.7474 | 2.1775 | 2.2041 | 1.9603
8.6833 | 81.7823 | 83.324 | 80.7647 | 2.1772 | 2.2039 | 1.9602
8.6875 | 81.8016 | 83.3433 | 80.7644 | 2.177 | 2.2038 | 1.9602
8.6917 | 81.8054 | 83.3617 | 80.7612 | 2.177 | 2.2037 | 1.9603
8.6958 | 81.8143 | 83.3732 | 80.7744 | 2.1769 | 2.2032 | 1.9599
8.7 | 81.7794 | 83.384 | 80.7893 | 2.1766 | 2.2027 | 1.9597
8.7042 | 81.7411 | 83.3606 | 80.7838 | 2.1766 | 2.2026 | 1.9598
8.7083 | 81.7205 | 83.338 | 80.7817 | 2.1767 | 2.2026 | 1.9599
8.7125 | 81.6996 | 83.3399 | 80.7845 | 2.1766 | 2.2019 | 1.9595
8.7167 | 81.6587 | 83.3437 | 80.7848 | 2.1766 | 2.2013 | 1.9591
8.7208 | 81.6606 | 83.38 | 80.8153 | 2.1766 | 2.2012 | 1.9591
8.725 | 81.6422 | 83.4164 | 80.8423 | 2.1764 | 2.201 | 1.959
8.7292 | 81.6467 | 83.3672 | 80.8199 | 2.1764 | 2.2008 | 1.9589
8.7333 | 81.6498 | 83.32 | 80.8073 | 2.1764 | 2.2005 | 1.9587
8.7375 | 81.6511 | 83.2991 | 80.8145 | 2.1764 | 2.2002 | 1.9585
8.7417 | 81.6562 | 83.2775 | 80.8226 | 2.1764 | 2.1999 | 1.9582
8.7458 | 81.6647 | 83.2742 | 80.826 | 2.1763 | 2.2001 | 1.9583
8.75 | 81.7118 | 83.2718 | 80.8261 | 2.176 | 2.2003 | 1.9582
8.7542 | 81.7482 | 83.2717 | 80.8304 | 2.1758 | 2.2002 | 1.9579
8.7583 | 81.8236 | 83.2719 | 80.8343 | 2.1759 | 2.2001 | 1.9576
8.7625 | 81.8384 | 83.26 | 80.8416 | 2.1757 | 2.2004 | 1.9577
8.7667 | 81.8417 | 83.2459 | 80.8517 | 2.1756 | 2.2007 | 1.9576
8.7708 | 81.8439 | 83.218 | 80.8352 | 2.1752 | 2.2008 | 1.9575
8.775 | 81.8395 | 83.1909 | 80.8205 | 2.1747 | 2.2009 | 1.9573
8.7792 | 81.8695 | 83.2442 | 80.8488 | 2.1741 | 2.2009 | 1.9571
8.7833 | 81.9155 | 83.2966 | 80.8672 | 2.1738 | 2.2008 | 1.9569
8.7875 | 81.9277 | 83.3083 | 80.8688 | 2.1733 | 2.2011 | 1.9569
8.7917 | 81.9356 | 83.3201 | 80.8735 | 2.1728 | 2.2013 | 1.9569
8.7958 | 81.9275 | 83.3067 | 80.8635 | 2.1722 | 2.201 | 1.9566
8.8 | 81.9084 | 83.2939 | 80.8577 | 2.1717 | 2.2006 | 1.9563
8.8042 | 81.9065 | 83.3474 | 80.8814 | 2.1712 | 2.2003 | 1.9562
8.8083 | 81.8953 | 83.3995 | 80.8967 | 2.1708 | 2.2 | 1.9561
8.8125 | 81.8774 | 83.4226 | 80.897 | 2.1705 | 2.1996 | 1.9559
8.8167 | 81.8792 | 83.4458 | 80.8985 | 2.1702 | 2.1992 | 1.9558
8.8208 | 81.8822 | 83.4514 | 80.9056 | 2.1698 | 2.1984 | 1.9555
8.825 | 81.8768 | 83.4559 | 80.9156 | 2.1696 | 2.1977 | 1.9552
8.8292 | 81.8775 | 83.464 | 80.9205 | 2.1694 | 2.197 | 1.9551
8.8333 | 81.8564 | 83.4725 | 80.9253 | 2.1693 | 2.1963 | 1.955
8.8375 | 81.8317 | 83.4929 | 80.931 | 2.1691 | 2.1954 | 1.9547
8.8417 | 81.8287 | 83.5146 | 80.9343 | 2.169 | 2.1944 | 1.9544
8.8458 | 81.8405 | 83.5325 | 80.952 | 2.1687 | 2.1935 | 1.9542
8.85 | 81.8522 | 83.5495 | 80.9694 | 2.1687 | 2.1927 | 1.954
8.8542 | 81.8529 | 83.5139 | 80.9591 | 2.1687 | 2.1918 | 1.9538
8.8583 | 81.8418 | 83.4794 | 80.9558 | 2.1687 | 2.191 | 1.9536
8.8625 | 81.8274 | 83.4901 | 80.9669 | 2.1686 | 2.1899 | 1.9533
8.8667 | 81.8122 | 83.5018 | 80.9734 | 2.1685 | 2.1888 | 1.9529
8.8708 | 81.8113 | 83.5249 | 80.9932 | 2.1685 | 2.1881 | 1.9528
8.875 | 81.8107 | 83.5482 | 81.0099 | 2.1684 | 2.1874 | 1.9526
8.8792 | 81.8188 | 83.5002 | 80.9994 | 2.1683 | 2.1866 | 1.9523
8.8833 | 81.8326 | 83.4521 | 80.9983 | 2.1682 | 2.1858 | 1.9521
8.8875 | 81.8597 | 83.45 | 81.0071 | 2.1681 | 2.1849 | 1.9518
8.8917 | 81.8767 | 83.4464 | 81.0153 | 2.168 | 2.184 | 1.9515
8.8958 | 81.8868 | 83.4622 | 81.0312 | 2.1679 | 2.1835 | 1.9513
8.9 | 81.8999 | 83.4779 | 81.0434 | 2.1676 | 2.183 | 1.951
8.9042 | 81.9111 | 83.431 | 81.0424 | 2.1672 | 2.1826 | 1.9508
8.9083 | 81.9357 | 83.3852 | 81.0465 | 2.1669 | 2.1821 | 1.9505
8.9125 | 81.9486 | 83.3566 | 81.0454 | 2.1665 | 2.1817 | 1.9503
8.9167 | 81.9547 | 83.3269 | 81.0435 | 2.1662 | 2.1813 | 1.9501
8.9208 | 81.9508 | 83.3299 | 81.0501 | 2.1657 | 2.1812 | 1.9499
8.925 | 81.9531 | 83.3322 | 81.0513 | 2.1653 | 2.1811 | 1.9496
8.9292 | 81.9704 | 83.2983 | 81.0529 | 2.1647 | 2.1812 | 1.9495
8.9333 | 81.9942 | 83.2663 | 81.0589 | 2.1642 | 2.1813 | 1.9493
8.9375 | 82.0121 | 83.234 | 81.0558 | 2.1637 | 2.1815 | 1.9492
8.9417 | 82.0191 | 83.2006 | 81.0545 | 2.1633 | 2.1816 | 1.949
8.9458 | 82.0036 | 83.2121 | 81.0653 | 2.1628 | 2.1819 | 1.9488
8.95 | 81.9943 | 83.2222 | 81.0698 | 2.1623 | 2.1822 | 1.9486
8.9542 | 81.9953 | 83.2048 | 81.0757 | 2.1617 | 2.1827 | 1.9485
8.9583 | 82.0058 | 83.1905 | 81.0845 | 2.1612 | 2.1832 | 1.9483
8.9625 | 82.0188 | 83.1578 | 81.0795 | 2.1607 | 2.1837 | 1.9482
8.9667 | 82.0254 | 83.1248 | 81.0783 | 2.1604 | 2.1842 | 1.948
8.9708 | 82.019 | 83.1415 | 81.0903 | 2.1599 | 2.1847 | 1.9478
8.975 | 82.0142 | 83.1562 | 81.0959 | 2.1594 | 2.1852 | 1.9476
8.9792 | 82.0197 | 83.1509 | 81.1027 | 2.1589 | 2.186 | 1.9475
8.9833 | 82.033 | 83.1452 | 81.1113 | 2.1584 | 2.1868 | 1.9474
8.9875 | 82.0384 | 83.1181 | 81.1064 | 2.158 | 2.1874 | 1.9472
8.9917 | 82.0397 | 83.091 | 81.1057 | 2.1576 | 2.188 | 1.947
8.9958 | 82.039 | 83.114 | 81.1193 | 2.1571 | 2.1886 | 1.9468
9 | 82.034 | 83.1388 | 81.1269 | 2.1567 | 2.1893 | 1.9466
9.0042 | 82.0444 | 83.1411 | 81.1329 | 2.1562 | 2.1901 | 1.9465
9.0083 | 82.0598 | 83.145 | 81.1405 | 2.1558 | 2.1908 | 1.9463
9.0125 | 82.0575 | 83.1255 | 81.1371 | 2.1554 | 2.1914 | 1.9461
9.0167 | 82.0576 | 83.1061 | 81.1375 | 2.155 | 2.192 | 1.9459
9.0208 | 82.0566 | 83.1314 | 81.1509 | 2.1545 | 2.1926 | 1.9457
9.025 | 82.0488 | 83.1565 | 81.1592 | 2.1541 | 2.1931 | 1.9455
9.0292 | 82.0658 | 83.1611 | 81.1637 | 2.1536 | 2.1938 | 1.9453
9.0333 | 82.0734 | 83.1667 | 81.1701 | 2.1532 | 2.1945 | 1.9451
9.0375 | 82.0747 | 83.1542 | 81.1695 | 2.1529 | 2.1949 | 1.9449
9.0417 | 82.072 | 83.1414 | 81.1717 | 2.1525 | 2.1954 | 1.9447
9.0458 | 82.0737 | 83.1658 | 81.1843 | 2.152 | 2.1958 | 1.9445
9.05 | 82.0728 | 83.1904 | 81.1929 | 2.1516 | 2.1962 | 1.9443
9.0542 | 82.08 | 83.1944 | 81.196 | 2.1512 | 2.1968 | 1.9441
9.0583 | 82.0919 | 83.1993 | 81.2007 | 2.1509 | 2.1972 | 1.9439
9.0625 | 82.0831 | 83.1923 | 81.2023 | 2.1505 | 2.1975 | 1.9437
9.0667 | 82.0877 | 83.1844 | 81.2054 | 2.1501 | 2.1978 | 1.9434
9.0708 | 82.0867 | 83.2059 | 81.217 | 2.1497 | 2.1981 | 1.9432
9.075 | 82.0947 | 83.2271 | 81.2257 | 2.1493 | 2.1984 | 1.943
9.0792 | 82.1014 | 83.23 | 81.2292 | 2.149 | 2.1987 | 1.9428
9.0833 | 82.1109 | 83.2327 | 81.2343 | 2.1485 | 2.199 | 1.9426
9.0875 | 82.1084 | 83.2274 | 81.2376 | 2.1482 | 2.1992 | 1.9424
9.0917 | 82.1109 | 83.2215 | 81.2418 | 2.1478 | 2.1994 | 1.9421
9.0958 | 82.1134 | 83.2366 | 81.2515 | 2.1474 | 2.1995 | 1.9419
9.1 | 82.1199 | 83.252 | 81.259 | 2.1469 | 2.1997 | 1.9417
9.1042 | 82.1258 | 83.2538 | 81.2631 | 2.1466 | 2.1999 | 1.9415
9.1083 | 82.1315 | 83.255 | 81.2685 | 2.1462 | 2.2001 | 1.9413
9.1125 | 82.131 | 83.2519 | 81.2732 | 2.1458 | 2.2002 | 1.941
9.1167 | 82.1338 | 83.2481 | 81.2785 | 2.1454 | 2.2002 | 1.9408
9.1208 | 82.1361 | 83.2588 | 81.2871 | 2.145 | 2.2003 | 1.9405
9.125 | 82.1396 | 83.2704 | 81.2942 | 2.1446 | 2.2004 | 1.9403
9.1292 | 82.1459 | 83.2731 | 81.2995 | 2.1442 | 2.2005 | 1.9401
9.1333 | 82.1491 | 83.2755 | 81.3058 | 2.1438 | 2.2006 | 1.9398
9.1375 | 82.1537 | 83.2753 | 81.312 | 2.1435 | 2.2006 | 1.9396
9.1417 | 82.1577 | 83.2745 | 81.3182 | 2.143 | 2.2006 | 1.9393
9.1458 | 82.1615 | 83.2823 | 81.3258 | 2.1427 | 2.2006 | 1.9391
9.15 | 82.167 | 83.2911 | 81.333 | 2.1422 | 2.2005 | 1.9389
9.1542 | 82.1736 | 83.2941 | 81.3389 | 2.1418 | 2.2005 | 1.9386
9.1583 | 82.1778 | 83.297 | 81.3456 | 2.1414 | 2.2005 | 1.9383
9.1625 | 82.1785 | 83.299 | 81.3521 | 2.1411 | 2.2004 | 1.9381
9.1667 | 82.185 | 83.3003 | 81.359 | 2.1406 | 2.2003 | 1.9378
9.1708 | 82.1831 | 83.3069 | 81.367 | 2.1402 | 2.2002 | 1.9376
9.175 | 82.1917 | 83.3141 | 81.3744 | 2.1398 | 2.2001 | 1.9373
9.1792 | 82.1993 | 83.3174 | 81.3816 | 2.1394 | 2.2 | 1.937
9.1833 | 82.2009 | 83.3206 | 81.3889 | 2.1389 | 2.1998 | 1.9368
9.1875 | 82.2041 | 83.3233 | 81.396 | 2.1386 | 2.1997 | 1.9365
9.1917 | 82.211 | 83.3255 | 81.4035 | 2.1381 | 2.1995 | 1.9362
9.1958 | 82.2101 | 83.3307 | 81.4114 | 2.1377 | 2.1993 | 1.9359
9.2 | 82.2216 | 83.336 | 81.4193 | 2.1373 | 2.1991 | 1.9356
9.2042 | 82.2286 | 83.339 | 81.4266 | 2.1368 | 2.1989 | 1.9353
9.2083 | 82.2293 | 83.3419 | 81.4344 | 2.1364 | 2.1987 | 1.9351
9.2125 | 82.2331 | 83.3444 | 81.4427 | 2.136 | 2.1984 | 1.9348
9.2167 | 82.2388 | 83.3467 | 81.4507 | 2.1355 | 2.1982 | 1.9345
9.2208 | 82.2408 | 83.351 | 81.459 | 2.135 | 2.1979 | 1.9342
9.225 | 82.2537 | 83.3554 | 81.4673 | 2.1346 | 2.1976 | 1.9339
9.2292 | 82.2575 | 83.3581 | 81.4752 | 2.1341 | 2.1973 | 1.9335
9.2333 | 82.2613 | 83.3606 | 81.4836 | 2.1337 | 2.197 | 1.9332
9.2375 | 82.2627 | 83.3629 | 81.4921 | 2.1332 | 2.1967 | 1.9329
9.2417 | 82.2684 | 83.3652 | 81.5007 | 2.1327 | 2.1964 | 1.9326
9.2458 | 82.276 | 83.3689 | 81.5095 | 2.1322 | 2.196 | 1.9323
9.25 | 82.2843 | 83.3727 | 81.5183 | 2.1317 | 2.1957 | 1.9319
9.2542 | 82.2929 | 83.3761 | 81.5277 | 2.1313 | 2.1953 | 1.9316
9.2583 | 82.2927 | 83.3794 | 81.5369 | 2.1308 | 2.195 | 1.9313
9.2625 | 82.2965 | 83.3821 | 81.546 | 2.1303 | 2.1946 | 1.9309
9.2667 | 82.3017 | 83.3849 | 81.5555 | 2.1298 | 2.1942 | 1.9306
9.2708 | 82.3112 | 83.3881 | 81.5647 | 2.1293 | 2.1938 | 1.9302
9.275 | 82.319 | 83.3911 | 81.5739 | 2.1288 | 2.1934 | 1.9299
9.2792 | 82.3285 | 83.3949 | 81.5839 | 2.1283 | 2.1929 | 1.9295
9.2833 | 82.3302 | 83.3983 | 81.5936 | 2.1277 | 2.1925 | 1.9292
9.2875 | 82.3329 | 83.4018 | 81.6036 | 2.1272 | 2.192 | 1.9288
9.2917 | 82.344 | 83.4056 | 81.6138 | 2.1266 | 2.1916 | 1.9284
9.2958 | 82.3473 | 83.4094 | 81.6239 | 2.1261 | 2.1911 | 1.928
9.3 | 82.3573 | 83.4133 | 81.6342 | 2.1256 | 2.1906 | 1.9277
9.3042 | 82.3651 | 83.4175 | 81.6449 | 2.125 | 2.1901 | 1.9273
9.3083 | 82.3656 | 83.4214 | 81.6554 | 2.1244 | 2.1895 | 1.9269
9.3125 | 82.3758 | 83.4256 | 81.6665 | 2.1239 | 2.189 | 1.9265
9.3167 | 82.3825 | 83.4301 | 81.6775 | 2.1233 | 2.1884 | 1.9261
9.3208 | 82.3871 | 83.434 | 81.6883 | 2.1227 | 2.1879 | 1.9257
9.325 | 82.3992 | 83.4381 | 81.6994 | 2.1221 | 2.1873 | 1.9253
9.3292 | 82.4049 | 83.4416 | 81.7101 | 2.1215 | 2.1867 | 1.9248
9.3333 | 82.4135 | 83.4449 | 81.721 | 2.1209 | 2.1861 | 1.9244
9.3375 | 82.4291 | 83.451 | 81.7346 | 2.1203 | 2.1854 | 1.924
9.3417 | 82.4393 | 83.4572 | 81.7479 | 2.1196 | 2.1848 | 1.9235
9.3458 | 82.4544 | 83.4648 | 81.763 | 2.1189 | 2.1841 | 1.9231
9.35 | 82.4709 | 83.4724 | 81.7783 | 2.1182 | 2.1834 | 1.9226
9.3542 | 82.4704 | 83.4636 | 81.7798 | 2.1175 | 2.1828 | 1.9222
9.3583 | 82.47 | 83.4551 | 81.782 | 2.1169 | 2.1822 | 1.9218
9.3625 | 82.4485 | 83.4265 | 81.7662 | 2.1164 | 2.1817 | 1.9215
9.3667 | 82.4278 | 83.399 | 81.7508 | 2.1158 | 2.1811 | 1.9212
9.3708 | 82.4154 | 83.384 | 81.7438 | 2.1153 | 2.1807 | 1.921
9.375 | 82.4078 | 83.3697 | 81.7366 | 2.1148 | 2.1803 | 1.9208
9.3792 | 82.4182 | 83.3741 | 81.7449 | 2.1144 | 2.18 | 1.9206
9.3833 | 82.4272 | 83.3781 | 81.753 | 2.114 | 2.1797 | 1.9205
9.3875 | 82.4327 | 83.3797 | 81.7597 | 2.1136 | 2.1794 | 1.9203
9.3917 | 82.4369 | 83.3811 | 81.7663 | 2.1132 | 2.179 | 1.9201
9.3958 | 82.4499 | 83.3885 | 81.7773 | 2.1127 | 2.1786 | 1.9199
9.4 | 82.4583 | 83.3953 | 81.7879 | 2.1122 | 2.1782 | 1.9196
9.4042 | 82.4765 | 83.4052 | 81.8003 | 2.1117 | 2.1778 | 1.9194
9.4083 | 82.4909 | 83.415 | 81.8127 | 2.1112 | 2.1774 | 1.9192
9.4125 | 82.4956 | 83.4185 | 81.8207 | 2.1106 | 2.177 | 1.9189
9.4167 | 82.5048 | 83.4226 | 81.8289 | 2.1101 | 2.1765 | 1.9186
9.4208 | 82.5111 | 83.4303 | 81.8397 | 2.1095 | 2.1759 | 1.9183
9.425 | 82.5196 | 83.4378 | 81.8502 | 2.1089 | 2.1754 | 1.9179
9.4292 | 82.5343 | 83.4488 | 81.8641 | 2.1082 | 2.1748 | 1.9176
9.4333 | 82.5495 | 83.4595 | 81.878 | 2.1076 | 2.1742 | 1.9172
9.4375 | 82.5539 | 83.4606 | 81.8845 | 2.107 | 2.1736 | 1.9169
9.4417 | 82.561 | 83.4616 | 81.8921 | 2.1063 | 2.173 | 1.9166
9.4458 | 82.5791 | 83.4638 | 81.9046 | 2.1055 | 2.1723 | 1.9161
9.45 | 82.5949 | 83.4666 | 81.9177 | 2.1047 | 2.1716 | 1.9157
9.4542 | 82.5987 | 83.4543 | 81.9175 | 2.1041 | 2.1711 | 1.9154
9.4583 | 82.6066 | 83.4427 | 81.9189 | 2.1035 | 2.1706 | 1.9152
9.4625 | 82.617 | 83.4477 | 81.9306 | 2.1025 | 2.1698 | 1.9147
9.4667 | 82.6295 | 83.4521 | 81.9414 | 2.1016 | 2.1691 | 1.9142
9.4708 | 82.6323 | 83.4724 | 81.9547 | 2.1011 | 2.1685 | 1.914
9.475 | 82.6341 | 83.4927 | 81.9647 | 2.1005 | 2.168 | 1.9138
9.4792 | 82.6392 | 83.536 | 81.9945 | 2.0995 | 2.1668 | 1.9131
9.4833 | 82.6544 | 83.5778 | 82.0214 | 2.0985 | 2.1657 | 1.9124
9.4875 | 82.6605 | 83.5871 | 82.0319 | 2.0979 | 2.1649 | 1.9122
9.4917 | 82.6548 | 83.5959 | 82.0456 | 2.0975 | 2.1641 | 1.9119
9.4958 | 82.6575 | 83.5727 | 82.051 | 2.0966 | 2.1628 | 1.9111
9.5 | 82.6589 | 83.5501 | 82.062 | 2.0955 | 2.1616 | 1.9104
9.5042 | 82.6865 | 83.5091 | 82.0594 | 2.0949 | 2.161 | 1.9103
9.5083 | 82.7189 | 83.4701 | 82.0606 | 2.0943 | 2.1605 | 1.9101
9.5125 | 82.7373 | 83.4639 | 82.0706 | 2.0933 | 2.1595 | 1.9093
9.5167 | 82.7606 | 83.4584 | 82.0767 | 2.0922 | 2.1584 | 1.9086
9.5208 | 82.7782 | 83.5017 | 82.1125 | 2.0913 | 2.1579 | 1.9084
9.525 | 82.8042 | 83.5431 | 82.1419 | 2.0904 | 2.1573 | 1.9081
9.5292 | 82.8156 | 83.5554 | 82.1509 | 2.0893 | 2.1563 | 1.9074
9.5333 | 82.8008 | 83.568 | 82.1618 | 2.0882 | 2.1552 | 1.9067
9.5375 | 82.8127 | 83.5705 | 82.1813 | 2.0873 | 2.1543 | 1.9062
9.5417 | 82.8192 | 83.5731 | 82.2052 | 2.0862 | 2.1534 | 1.9057
9.5458 | 82.8189 | 83.5494 | 82.198 | 2.0852 | 2.1524 | 1.9052
9.55 | 82.835 | 83.5274 | 82.1938 | 2.0843 | 2.1514 | 1.9047
9.5542 | 82.8521 | 83.5654 | 82.2259 | 2.0832 | 2.1502 | 1.904
9.5583 | 82.8944 | 83.6014 | 82.2524 | 2.0819 | 2.149 | 1.9033
9.5625 | 82.926 | 83.6232 | 82.2691 | 2.0808 | 2.1481 | 1.9029
9.5667 | 82.9544 | 83.6437 | 82.2855 | 2.0797 | 2.1471 | 1.9025
9.5708 | 82.9754 | 83.6401 | 82.2955 | 2.0784 | 2.1456 | 1.9016
9.575 | 82.9734 | 83.6365 | 82.3081 | 2.077 | 2.1442 | 1.9009
9.5792 | 82.9767 | 83.6505 | 82.3336 | 2.0758 | 2.1429 | 1.9003
9.5833 | 83.0071 | 83.6638 | 82.3576 | 2.0743 | 2.1417 | 1.8998
9.5875 | 83.0099 | 83.6772 | 82.3716 | 2.0731 | 2.1402 | 1.899
9.5917 | 83.0094 | 83.6921 | 82.384 | 2.0719 | 2.1386 | 1.8983
9.5958 | 83.0186 | 83.7231 | 82.4218 | 2.0708 | 2.137 | 1.8975
9.6 | 82.9981 | 83.7542 | 82.4581 | 2.0695 | 2.1355 | 1.8968
9.6042 | 83.0024 | 83.7255 | 82.4613 | 2.0683 | 2.1341 | 1.8961
9.6083 | 83.0122 | 83.6983 | 82.4716 | 2.0672 | 2.1326 | 1.8955
9.6125 | 83.0132 | 83.6872 | 82.4898 | 2.0661 | 2.1309 | 1.8945
9.6167 | 82.9975 | 83.6766 | 82.508 | 2.0653 | 2.1292 | 1.8936
9.6208 | 83.0124 | 83.691 | 82.5388 | 2.0642 | 2.1279 | 1.8929
9.625 | 83.0206 | 83.7059 | 82.5669 | 2.0631 | 2.1266 | 1.8922
9.6292 | 83.0512 | 83.6823 | 82.5746 | 2.0618 | 2.1251 | 1.8914
9.6333 | 83.1158 | 83.6599 | 82.5872 | 2.0608 | 2.1237 | 1.8905
9.6375 | 83.1374 | 83.6513 | 82.6146 | 2.0595 | 2.1224 | 1.8897
9.6417 | 83.1479 | 83.6412 | 82.643 | 2.0584 | 2.121 | 1.8888
9.6458 | 83.1706 | 83.6315 | 82.6568 | 2.0569 | 2.1199 | 1.8881
9.65 | 83.1888 | 83.6225 | 82.6711 | 2.0553 | 2.1187 | 1.8873
9.6542 | 83.2336 | 83.644 | 82.7012 | 2.0537 | 2.1173 | 1.8863
9.6583 | 83.3036 | 83.6654 | 82.7279 | 2.0522 | 2.1159 | 1.8853
9.6625 | 83.3362 | 83.6771 | 82.7554 | 2.0505 | 2.1147 | 1.8845
9.6667 | 83.3525 | 83.6884 | 82.7847 | 2.0489 | 2.1136 | 1.8837
9.6708 | 83.3652 | 83.6793 | 82.7939 | 2.047 | 2.1121 | 1.8827
9.675 | 83.3732 | 83.6715 | 82.8064 | 2.0451 | 2.1105 | 1.8817
9.6792 | 83.397 | 83.7235 | 82.8484 | 2.0432 | 2.1089 | 1.8807
9.6833 | 83.4276 | 83.7739 | 82.8832 | 2.0414 | 2.1072 | 1.8797
9.6875 | 83.44 | 83.7966 | 82.9068 | 2.0396 | 2.1056 | 1.8788
9.6917 | 83.4507 | 83.8189 | 82.9326 | 2.0378 | 2.104 | 1.8778
9.6958 | 83.4654 | 83.8213 | 82.9528 | 2.0359 | 2.1019 | 1.8767
9.7 | 83.4783 | 83.8238 | 82.9763 | 2.034 | 2.0998 | 1.8755
9.7042 | 83.5013 | 83.8628 | 83.0152 | 2.0322 | 2.0977 | 1.8745
9.7083 | 83.5169 | 83.9008 | 83.05 | 2.0304 | 2.0956 | 1.8734
9.7125 | 83.5192 | 83.9202 | 83.0746 | 2.0286 | 2.0933 | 1.8723
9.7167 | 83.5373 | 83.9401 | 83.1003 | 2.0268 | 2.091 | 1.8711
9.7208 | 83.5607 | 83.9536 | 83.1346 | 2.0248 | 2.0885 | 1.8699
9.725 | 83.5904 | 83.9669 | 83.17 | 2.0229 | 2.086 | 1.8686
9.7292 | 83.6147 | 83.9706 | 83.1951 | 2.0211 | 2.0836 | 1.8675
9.7333 | 83.6333 | 83.975 | 83.2253 | 2.0193 | 2.0812 | 1.8663
9.7375 | 83.6322 | 83.9866 | 83.2545 | 2.0174 | 2.0785 | 1.865
9.7417 | 83.6437 | 83.9995 | 83.2835 | 2.0155 | 2.0757 | 1.8636
9.7458 | 83.6579 | 84.022 | 83.3289 | 2.0136 | 2.0731 | 1.8623
9.75 | 83.6745 | 84.0446 | 83.3704 | 2.0117 | 2.0705 | 1.861
9.7542 | 83.6899 | 84.0201 | 83.3884 | 2.0099 | 2.0679 | 1.8597
9.7583 | 83.7041 | 83.9957 | 83.4127 | 2.0081 | 2.0653 | 1.8584
9.7625 | 83.7316 | 84.003 | 83.4473 | 2.0061 | 2.0624 | 1.8569
9.7667 | 83.7575 | 84.01 | 83.4815 | 2.0042 | 2.0595 | 1.8555
9.7708 | 83.7986 | 84.0387 | 83.5316 | 2.0021 | 2.0569 | 1.8541
9.775 | 83.839 | 84.0675 | 83.5796 | 2.0001 | 2.0543 | 1.8526
9.7792 | 83.8681 | 84.0387 | 83.6075 | 1.998 | 2.0516 | 1.8511
9.7833 | 83.9046 | 84.0107 | 83.641 | 1.9958 | 2.0489 | 1.8496
9.7875 | 83.9375 | 84.0075 | 83.6791 | 1.9935 | 2.0461 | 1.848
9.7917 | 83.9661 | 84.0039 | 83.7164 | 1.9912 | 2.0433 | 1.8464
9.7958 | 83.9975 | 84.0164 | 83.7595 | 1.9889 | 2.0408 | 1.8448
9.8 | 84.0307 | 84.0288 | 83.8002 | 1.9864 | 2.0382 | 1.8432
9.8042 | 84.0658 | 84.0017 | 83.8338 | 1.9839 | 2.0357 | 1.8416
9.8083 | 84.1075 | 83.9752 | 83.8715 | 1.9814 | 2.0331 | 1.8399
9.8125 | 84.1509 | 83.97 | 83.9126 | 1.9787 | 2.0305 | 1.8382
9.8167 | 84.1825 | 83.9642 | 83.9537 | 1.9761 | 2.0279 | 1.8364
9.8208 | 84.2076 | 83.9778 | 83.9996 | 1.9735 | 2.0255 | 1.8347
9.825 | 84.2293 | 83.988 | 84.0432 | 1.9707 | 2.023 | 1.8329
9.8292 | 84.2596 | 83.9753 | 84.0857 | 1.9679 | 2.0206 | 1.8311
9.8333 | 84.2932 | 83.9634 | 84.1316 | 1.9651 | 2.0181 | 1.8292
9.8375 | 84.3357 | 83.9586 | 84.1748 | 1.9623 | 2.0156 | 1.8273
9.8417 | 84.369 | 83.9573 | 84.2198 | 1.9595 | 2.0131 | 1.8254
9.8458 | 84.3928 | 83.9745 | 84.2698 | 1.9566 | 2.0107 | 1.8234
9.85 | 84.419 | 83.9915 | 84.3173 | 1.9537 | 2.0082 | 1.8214
9.8542 | 84.4523 | 83.9922 | 84.367 | 1.9506 | 2.0057 | 1.8193
9.8583 | 84.4933 | 83.9937 | 84.4189 | 1.9476 | 2.0032 | 1.8173
9.8625 | 84.5347 | 83.9914 | 84.465 | 1.9446 | 2.0006 | 1.8151
9.8667 | 84.5696 | 83.9901 | 84.5139 | 1.9416 | 1.998 | 1.813
9.8708 | 84.5991 | 84.0143 | 84.5704 | 1.9385 | 1.9953 | 1.8107
9.875 | 84.6286 | 84.0388 | 84.6239 | 1.9352 | 1.9926 | 1.8085
9.8792 | 84.6702 | 84.0496 | 84.6793 | 1.932 | 1.99 | 1.8062
9.8833 | 84.7162 | 84.0622 | 84.7365 | 1.9287 | 1.9872 | 1.8038
9.8875 | 84.7542 | 84.0635 | 84.7859 | 1.9255 | 1.9844 | 1.8014
9.8917 | 84.7902 | 84.0654 | 84.839 | 1.9221 | 1.9814 | 1.799
9.8958 | 84.8212 | 84.0962 | 84.9002 | 1.9187 | 1.9785 | 1.7965
9.9 | 84.8535 | 84.1279 | 84.9596 | 1.9152 | 1.9754 | 1.7939
9.9042 | 84.9015 | 84.1475 | 85.0191 | 1.9117 | 1.9725 | 1.7914
9.9083 | 84.9465 | 84.1682 | 85.08 | 1.9082 | 1.9695 | 1.7887
9.9125 | 84.9881 | 84.1799 | 85.1374 | 1.9046 | 1.9663 | 1.786
9.9167 | 85.025 | 84.1913 | 85.1964 | 1.901 | 1.963 | 1.7832
9.9208 | 85.0635 | 84.2295 | 85.2642 | 1.8972 | 1.9596 | 1.7804
9.925 | 85.1034 | 84.2697 | 85.3306 | 1.8935 | 1.9563 | 1.7775
9.9292 | 85.1526 | 84.2925 | 85.3929 | 1.8896 | 1.9529 | 1.7746
9.9333 | 85.2011 | 84.3166 | 85.4579 | 1.8859 | 1.9494 | 1.7717
9.9375 | 85.2377 | 84.3347 | 85.5211 | 1.8819 | 1.9458 | 1.7686
9.9417 | 85.2799 | 84.3525 | 85.5858 | 1.878 | 1.942 | 1.7655
9.9458 | 85.3207 | 84.3925 | 85.6582 | 1.8739 | 1.9383 | 1.7623
9.95 | 85.3702 | 84.4333 | 85.7295 | 1.8698 | 1.9344 | 1.7591
9.9542 | 85.4199 | 84.4571 | 85.7966 | 1.8657 | 1.9305 | 1.7558
9.9583 | 85.4717 | 84.4809 | 85.8661 | 1.8616 | 1.9266 | 1.7525
9.9625 | 85.5131 | 84.5032 | 85.9358 | 1.8573 | 1.9225 | 1.7491
9.9667 | 85.5563 | 84.5254 | 86.0066 | 1.853 | 1.9183 | 1.7456
9.9708 | 85.6064 | 84.5632 | 86.0826 | 1.8486 | 1.9141 | 1.742
9.975 | 85.6578 | 84.6017 | 86.1578 | 1.8441 | 1.9098 | 1.7384
9.9792 | 85.7115 | 84.6259 | 86.2299 | 1.8396 | 1.9055 | 1.7347
9.9833 | 85.7619 | 84.65 | 86.3038 | 1.8351 | 1.9011 | 1.731
9.9875 | 85.8104 | 84.677 | 86.3795 | 1.8305 | 1.8965 | 1.7271
9.9917 | 85.8559 | 84.7042 | 86.456 | 1.8257 | 1.8919 | 1.7232
9.9958 | 85.9092 | 84.7407 | 86.5355 | 1.8209 | 1.8872 | 1.7192
10 | 85.9651 | 84.7781 | 86.6147 | 1.8161 | 1.8825 | 1.7152
10.0042 | 86.0181 | 84.8058 | 86.6919 | 1.8112 | 1.8777 | 1.711
10.0083 | 86.0675 | 84.8324 | 86.7692 | 1.8063 | 1.8729 | 1.7068
10.0125 | 85.6632 | 84.4155 | 86.4372 | 1.805 | 1.8715 | 1.7059
10.0167 | 85.2521 | 83.9933 | 86.099 | 1.8036 | 1.8702 | 1.705
10.0208 | 84.9792 | 83.7127 | 85.8698 | 1.8009 | 1.8676 | 1.7027
10.025 | 84.7049 | 83.4298 | 85.6372 | 1.7982 | 1.865 | 1.7004
10.0292 | 84.7244 | 83.5222 | 85.7306 | 1.7988 | 1.8663 | 1.7015
10.0333 | 84.8216 | 83.6152 | 85.8256 | 1.8 | 1.8677 | 1.7026
10.0375 | 84.6616 | 83.4288 | 85.6584 | 1.8009 | 1.8689 | 1.7035
10.0417 | 84.471 | 83.2401 | 85.4871 | 1.8019 | 1.8701 | 1.7044
10.0458 | 84.5304 | 83.3445 | 85.5669 | 1.8018 | 1.8698 | 1.7039
10.05 | 84.6329 | 83.4507 | 85.65 | 1.8013 | 1.8695 | 1.7034
10.0542 | 84.6231 | 83.5433 | 85.7203 | 1.8021 | 1.8714 | 1.7049
10.0583 | 84.707 | 83.6367 | 85.7912 | 1.8039 | 1.8733 | 1.7065
10.0625 | 84.6567 | 83.5204 | 85.6824 | 1.8036 | 1.8731 | 1.7062
10.0667 | 84.5485 | 83.4023 | 85.569 | 1.8034 | 1.8728 | 1.7059
10.0708 | 84.5971 | 83.5419 | 85.6817 | 1.8036 | 1.8728 | 1.7058
10.075 | 84.744 | 83.6836 | 85.7994 | 1.8037 | 1.8728 | 1.7057
10.0792 | 84.709 | 83.6347 | 85.7548 | 1.8042 | 1.8739 | 1.7067
10.0833 | 84.6832 | 83.5843 | 85.7065 | 1.8055 | 1.8751 | 1.7076
10.0875 | 84.6482 | 83.5329 | 85.6618 | 1.8051 | 1.8743 | 1.707
10.0917 | 84.6219 | 83.4806 | 85.6158 | 1.8047 | 1.8736 | 1.7064
10.0958 | 84.6261 | 83.5813 | 85.6969 | 1.8048 | 1.8743 | 1.7069
10.1 | 84.7182 | 83.6838 | 85.7828 | 1.8053 | 1.875 | 1.7075
10.1042 | 84.682 | 83.587 | 85.7008 | 1.8056 | 1.8754 | 1.7079
10.1083 | 84.632 | 83.4882 | 85.6134 | 1.8062 | 1.8759 | 1.7083
10.1125 | 84.59 | 83.5189 | 85.6366 | 1.8061 | 1.8755 | 1.708
10.1167 | 84.6359 | 83.5507 | 85.6631 | 1.806 | 1.8751 | 1.7076
10.1208 | 84.6262 | 83.5889 | 85.6901 | 1.8061 | 1.876 | 1.7083
10.125 | 84.6549 | 83.6272 | 85.7184 | 1.8069 | 1.877 | 1.7092
10.1292 | 84.6314 | 83.5496 | 85.6533 | 1.8072 | 1.877 | 1.7091
10.1333 | 84.5819 | 83.4692 | 85.5835 | 1.8071 | 1.8769 | 1.7091
10.1375 | 84.5732 | 83.537 | 85.6344 | 1.8074 | 1.877 | 1.7092
10.1417 | 84.6161 | 83.607 | 85.6908 | 1.8075 | 1.877 | 1.7092
10.1458 | 84.6267 | 83.5856 | 85.6697 | 1.8079 | 1.8778 | 1.7098
10.15 | 84.6029 | 83.564 | 85.6459 | 1.8084 | 1.8786 | 1.7105
10.1542 | 84.5969 | 83.5334 | 85.6195 | 1.8087 | 1.8783 | 1.7103
10.1583 | 84.5726 | 83.5019 | 85.5916 | 1.8086 | 1.8781 | 1.7101
10.1625 | 84.5788 | 83.5599 | 85.6326 | 1.8089 | 1.8785 | 1.7105
10.1667 | 84.6121 | 83.6198 | 85.6782 | 1.8093 | 1.879 | 1.7109
10.1708 | 84.6113 | 83.5703 | 85.6363 | 1.8096 | 1.8794 | 1.7113
10.175 | 84.5761 | 83.5194 | 85.5896 | 1.81 | 1.8798 | 1.7116
10.1792 | 84.5653 | 83.5316 | 85.5955 | 1.8102 | 1.8797 | 1.7116
10.1833 | 84.5704 | 83.5442 | 85.6034 | 1.8103 | 1.8795 | 1.7115
10.1875 | 84.5825 | 83.5756 | 85.6246 | 1.8105 | 1.88 | 1.712
10.1917 | 84.5981 | 83.6076 | 85.6468 | 1.811 | 1.8806 | 1.7124
10.1958 | 84.6171 | 83.5885 | 85.6376 | 1.8111 | 1.8805 | 1.7124
10.2 | 84.6138 | 83.5669 | 85.6233 | 1.8111 | 1.8804 | 1.7123
10.2042 | 84.5589 | 83.5501 | 85.5942 | 1.8117 | 1.8808 | 1.7128
10.2083 | 84.5331 | 83.5371 | 85.5711 | 1.8122 | 1.8812 | 1.7133
10.2125 | 84.3928 | 83.3833 | 85.4064 | 1.8134 | 1.8825 | 1.7146
10.2167 | 84.2445 | 83.2359 | 85.2468 | 1.8146 | 1.8838 | 1.7159
10.2208 | 84.1944 | 83.1728 | 85.1705 | 1.8159 | 1.8848 | 1.717
10.225 | 84.1386 | 83.1106 | 85.0972 | 1.8169 | 1.8858 | 1.718
10.2292 | 84.1566 | 83.1631 | 85.1237 | 1.8189 | 1.8878 | 1.72
10.2333 | 84.1895 | 83.2172 | 85.156 | 1.8208 | 1.8898 | 1.722
10.2375 | 84.1821 | 83.1898 | 85.1239 | 1.8224 | 1.8915 | 1.7235
10.2417 | 84.1566 | 83.1614 | 85.0892 | 1.8239 | 1.8931 | 1.7251
10.2458 | 84.2085 | 83.2307 | 85.1468 | 1.825 | 1.8941 | 1.726
10.25 | 84.2689 | 83.2959 | 85.2014 | 1.826 | 1.8951 | 1.7269
10.2542 | 84.2796 | 83.3244 | 85.213 | 1.8274 | 1.8967 | 1.7283
10.2583 | 84.295 | 83.3533 | 85.2251 | 1.8288 | 1.8983 | 1.7297
10.2625 | 84.2723 | 83.3127 | 85.1808 | 1.8296 | 1.899 | 1.7303
10.2667 | 84.2354 | 83.2715 | 85.1338 | 1.8303 | 1.8997 | 1.7309
10.2708 | 84.2683 | 83.3281 | 85.1722 | 1.8312 | 1.9005 | 1.7317
10.275 | 84.3088 | 83.3838 | 85.2107 | 1.8321 | 1.9014 | 1.7324
10.2792 | 84.2837 | 83.3541 | 85.1669 | 1.8331 | 1.9026 | 1.7335
10.2833 | 84.2484 | 83.3266 | 85.1244 | 1.8343 | 1.9039 | 1.7347
10.2875 | 84.2374 | 83.3146 | 85.1032 | 1.8349 | 1.9043 | 1.7351
10.2917 | 84.2255 | 83.3007 | 85.0807 | 1.8354 | 1.9048 | 1.7356
10.2958 | 84.242 | 83.3472 | 85.1072 | 1.8364 | 1.9058 | 1.7366
10.3 | 84.2744 | 83.3936 | 85.1346 | 1.8375 | 1.9069 | 1.7376
10.3042 | 84.2407 | 83.3558 | 85.0865 | 1.8384 | 1.9077 | 1.7384
10.3083 | 84.2032 | 83.3189 | 85.0383 | 1.8392 | 1.9086 | 1.7393
10.3125 | 84.2153 | 83.344 | 85.0504 | 1.8399 | 1.909 | 1.7398
10.3167 | 84.2336 | 83.3668 | 85.0621 | 1.8405 | 1.9095 | 1.7403
10.3208 | 84.2414 | 83.3787 | 85.0633 | 1.8414 | 1.9105 | 1.7413
10.325 | 84.2513 | 83.3922 | 85.0664 | 1.8424 | 1.9115 | 1.7423
10.3292 | 84.2295 | 83.3454 | 85.022 | 1.843 | 1.9121 | 1.7429
10.3333 | 84.2018 | 83.2993 | 84.9784 | 1.8436 | 1.9127 | 1.7435
10.3375 | 84.217 | 83.3255 | 84.9951 | 1.8443 | 1.9134 | 1.7441
10.3417 | 84.244 | 83.3506 | 85.0118 | 1.8449 | 1.914 | 1.7448
10.3458 | 84.2318 | 83.3496 | 84.9934 | 1.8457 | 1.915 | 1.7457
10.35 | 84.216 | 83.3498 | 84.973 | 1.8466 | 1.9159 | 1.7466
10.3542 | 84.1999 | 83.3644 | 84.9612 | 1.8471 | 1.9162 | 1.7471
10.3583 | 84.1834 | 83.3773 | 84.946 | 1.8476 | 1.9166 | 1.7475
10.3625 | 84.1895 | 83.4263 | 84.9659 | 1.8484 | 1.9171 | 1.7482
10.3667 | 84.1996 | 83.4738 | 84.9863 | 1.8492 | 1.9176 | 1.749
10.3708 | 84.1754 | 83.4392 | 84.9507 | 1.85 | 1.9181 | 1.7497
10.375 | 84.1376 | 83.4055 | 84.9186 | 1.8508 | 1.9186 | 1.7503
10.3792 | 84.1423 | 83.3848 | 84.9091 | 1.8514 | 1.9189 | 1.7508
10.3833 | 84.1541 | 83.3638 | 84.9025 | 1.8519 | 1.9192 | 1.7513
10.3875 | 84.1654 | 83.3537 | 84.896 | 1.8527 | 1.92 | 1.7521
10.3917 | 84.1842 | 83.345 | 84.8891 | 1.8536 | 1.9208 | 1.753
10.3958 | 84.1718 | 83.3328 | 84.8701 | 1.8542 | 1.9213 | 1.7535
10.4 | 84.1563 | 83.3207 | 84.8467 | 1.8547 | 1.9219 | 1.7541
10.4042 | 84.1677 | 83.3505 | 84.8565 | 1.8552 | 1.9225 | 1.7547
10.4083 | 84.1748 | 83.3797 | 84.8654 | 1.8558 | 1.9231 | 1.7553
10.4125 | 84.1641 | 83.3718 | 84.848 | 1.8565 | 1.9238 | 1.756
10.4167 | 84.1375 | 83.3651 | 84.8327 | 1.8572 | 1.9245 | 1.7567
10.4208 | 84.1193 | 83.351 | 84.8144 | 1.8578 | 1.9249 | 1.7572
10.425 | 84.1071 | 83.3366 | 84.7973 | 1.8583 | 1.9254 | 1.7578
10.4292 | 84.109 | 83.3543 | 84.7958 | 1.859 | 1.926 | 1.7584
10.4333 | 84.1294 | 83.3718 | 84.7939 | 1.8597 | 1.9265 | 1.7591
10.4375 | 84.1256 | 83.3747 | 84.7793 | 1.8604 | 1.9271 | 1.7598
10.4417 | 84.1237 | 83.3767 | 84.7628 | 1.8609 | 1.9276 | 1.7604
10.4458 | 84.1313 | 83.3782 | 84.7515 | 1.8614 | 1.928 | 1.761
10.45 | 84.1375 | 83.3786 | 84.7414 | 1.8619 | 1.9284 | 1.7616
10.4542 | 84.1364 | 83.3874 | 84.735 | 1.8625 | 1.9288 | 1.7622
10.4583 | 84.1408 | 83.3958 | 84.7279 | 1.863 | 1.9293 | 1.7629
10.4625 | 84.123 | 83.3962 | 84.7105 | 1.8635 | 1.9297 | 1.7636
10.4667 | 84.1065 | 83.3963 | 84.6908 | 1.864 | 1.93 | 1.7642
10.4708 | 84.1014 | 83.4111 | 84.6851 | 1.8646 | 1.9303 | 1.7648
10.475 | 84.0821 | 83.4264 | 84.6793 | 1.8651 | 1.9305 | 1.7654
10.4792 | 84.0676 | 83.4252 | 84.6704 | 1.8658 | 1.9309 | 1.7661
10.4833 | 84.0458 | 83.4243 | 84.6624 | 1.8665 | 1.9312 | 1.7668
10.4875 | 84.0259 | 83.4034 | 84.6413 | 1.8672 | 1.9315 | 1.7674
10.4917 | 84.0004 | 83.383 | 84.6218 | 1.8681 | 1.9318 | 1.7681
10.4958 | 83.9934 | 83.3904 | 84.6206 | 1.8689 | 1.9321 | 1.7687
10.5 | 83.976 | 83.3985 | 84.618 | 1.8698 | 1.9324 | 1.7693
10.5042 | 83.9681 | 83.3826 | 84.6021 | 1.8706 | 1.9329 | 1.77
10.5083 | 83.9771 | 83.3671 | 84.5872 | 1.8715 | 1.9334 | 1.7708
10.5125 | 83.9735 | 83.3418 | 84.5682 | 1.8722 | 1.9339 | 1.7714
10.5167 | 83.9775 | 83.3164 | 84.5516 | 1.8732 | 1.9343 | 1.7719
10.5208 | 83.978 | 83.3145 | 84.5467 | 1.874 | 1.935 | 1.7727
10.525 | 83.9689 | 83.3123 | 84.5405 | 1.8748 | 1.9357 | 1.7734
10.5292 | 83.9739 | 83.2999 | 84.5206 | 1.8754 | 1.9364 | 1.7741
10.5333 | 83.9975 | 83.2879 | 84.5004 | 1.876 | 1.9371 | 1.7748
10.5375 | 84.0084 | 83.2924 | 84.4931 | 1.8766 | 1.9377 | 1.7754
10.5417 | 84.0181 | 83.2969 | 84.4855 | 1.8773 | 1.9383 | 1.7761
10.5458 | 84.0126 | 83.2956 | 84.4718 | 1.8778 | 1.9391 | 1.7769
10.55 | 83.9977 | 83.2946 | 84.4587 | 1.8783 | 1.9399 | 1.7777
10.5542 | 83.9907 | 83.2991 | 84.4403 | 1.8788 | 1.9404 | 1.7783
10.5583 | 83.9975 | 83.304 | 84.4208 | 1.8793 | 1.941 | 1.779
10.5625 | 83.9947 | 83.3345 | 84.4196 | 1.8798 | 1.9415 | 1.7797
10.5667 | 83.9806 | 83.3644 | 84.4163 | 1.8805 | 1.942 | 1.7804
10.5708 | 83.9674 | 83.3598 | 84.3942 | 1.8811 | 1.9425 | 1.7812
10.575 | 83.9478 | 83.3549 | 84.3746 | 1.8816 | 1.943 | 1.7819
10.5792 | 83.9415 | 83.3676 | 84.3615 | 1.8821 | 1.9432 | 1.7826
10.5833 | 83.94 | 83.3792 | 84.3474 | 1.8828 | 1.9434 | 1.7832
10.5875 | 83.9272 | 83.4053 | 84.3404 | 1.8835 | 1.9437 | 1.784
10.5917 | 83.9096 | 83.4306 | 84.3328 | 1.8843 | 1.944 | 1.7848
10.5958 | 83.8964 | 83.4216 | 84.3101 | 1.8849 | 1.9442 | 1.7855
10.6 | 83.8933 | 83.4125 | 84.2888 | 1.8856 | 1.9443 | 1.7863
10.6042 | 83.9003 | 83.425 | 84.2836 | 1.8862 | 1.9443 | 1.787
10.6083 | 83.9033 | 83.4369 | 84.2773 | 1.887 | 1.9443 | 1.7876
10.6125 | 83.8985 | 83.4497 | 84.2676 | 1.8877 | 1.9444 | 1.7884
10.6167 | 83.8897 | 83.4633 | 84.2597 | 1.8884 | 1.9445 | 1.7892
10.6208 | 83.8776 | 83.4659 | 84.249 | 1.889 | 1.9444 | 1.7898
10.625 | 83.8786 | 83.4689 | 84.2366 | 1.8897 | 1.9443 | 1.7904
10.6292 | 83.8698 | 83.4695 | 84.2273 | 1.8904 | 1.9443 | 1.7912
10.6333 | 83.8549 | 83.4695 | 84.2177 | 1.8912 | 1.9443 | 1.7919
10.6375 | 83.8392 | 83.4536 | 84.1932 | 1.8919 | 1.9443 | 1.7926
10.6417 | 83.8221 | 83.4377 | 84.1715 | 1.8926 | 1.9443 | 1.7933
10.6458 | 83.8231 | 83.4481 | 84.1647 | 1.8933 | 1.9442 | 1.7939
10.65 | 83.826 | 83.458 | 84.1546 | 1.8941 | 1.9441 | 1.7946
10.6542 | 83.8278 | 83.4504 | 84.1414 | 1.8948 | 1.9443 | 1.7954
10.6583 | 83.8244 | 83.4431 | 84.1305 | 1.8956 | 1.9444 | 1.7962
10.6625 | 83.8182 | 83.4169 | 84.106 | 1.8962 | 1.9445 | 1.7969
10.6667 | 83.8164 | 83.391 | 84.0836 | 1.8969 | 1.9445 | 1.7976
10.6708 | 83.8176 | 83.401 | 84.0772 | 1.8976 | 1.9447 | 1.7983
10.675 | 83.8171 | 83.4092 | 84.0662 | 1.8983 | 1.9449 | 1.7991
10.6792 | 83.8105 | 83.386 | 84.0445 | 1.8989 | 1.9453 | 1.7999
10.6833 | 83.8079 | 83.3619 | 84.0255 | 1.8995 | 1.9457 | 1.8007
10.6875 | 83.8065 | 83.3356 | 84.0033 | 1.9001 | 1.946 | 1.8015
10.6917 | 83.8105 | 83.3101 | 83.9813 | 1.9007 | 1.9463 | 1.8023
10.6958 | 83.8081 | 83.3203 | 83.972 | 1.9014 | 1.9468 | 1.8031
10.7 | 83.7975 | 83.3291 | 83.9586 | 1.902 | 1.9474 | 1.804
10.7042 | 83.7829 | 83.305 | 83.9343 | 1.9026 | 1.9481 | 1.8049
10.7083 | 83.7732 | 83.2794 | 83.9129 | 1.9032 | 1.9488 | 1.8057
10.7125 | 83.7711 | 83.2637 | 83.8946 | 1.9038 | 1.9493 | 1.8066
10.7167 | 83.7701 | 83.2499 | 83.8761 | 1.9045 | 1.9499 | 1.8074
10.7208 | 83.7594 | 83.2572 | 83.8613 | 1.9052 | 1.9507 | 1.8083
10.725 | 83.7467 | 83.2653 | 83.844 | 1.9059 | 1.9515 | 1.8093
10.7292 | 83.7276 | 83.247 | 83.8201 | 1.9065 | 1.9523 | 1.8102
10.7333 | 83.7246 | 83.2284 | 83.7977 | 1.9072 | 1.9531 | 1.8111
10.7375 | 83.7226 | 83.2205 | 83.779 | 1.9079 | 1.9538 | 1.812
10.7417 | 83.719 | 83.2139 | 83.7603 | 1.9086 | 1.9546 | 1.813
10.7458 | 83.7081 | 83.2172 | 83.7395 | 1.9095 | 1.9555 | 1.8139
10.75 | 83.6918 | 83.2204 | 83.7176 | 1.9102 | 1.9564 | 1.8149
10.7542 | 83.6834 | 83.212 | 83.6969 | 1.9109 | 1.9573 | 1.8159
10.7583 | 83.6807 | 83.2043 | 83.6758 | 1.9116 | 1.9581 | 1.8168
10.7625 | 83.6805 | 83.1969 | 83.6545 | 1.9124 | 1.959 | 1.8179
10.7667 | 83.6738 | 83.1904 | 83.6341 | 1.9132 | 1.9599 | 1.8189
10.7708 | 83.6575 | 83.1874 | 83.6094 | 1.914 | 1.9609 | 1.8199
10.775 | 83.6401 | 83.1834 | 83.5841 | 1.9148 | 1.9618 | 1.8209
10.7792 | 83.6347 | 83.1817 | 83.5641 | 1.9155 | 1.9627 | 1.822
10.7833 | 83.6304 | 83.1805 | 83.5428 | 1.9163 | 1.9637 | 1.823
10.7875 | 83.6275 | 83.1728 | 83.5177 | 1.9171 | 1.9646 | 1.8241
10.7917 | 83.6169 | 83.1647 | 83.4933 | 1.9181 | 1.9656 | 1.8252
10.7958 | 83.5998 | 83.1662 | 83.4694 | 1.9188 | 1.9665 | 1.8263
10.8 | 83.585 | 83.1674 | 83.4438 | 1.9197 | 1.9674 | 1.8274
10.8042 | 83.5812 | 83.1723 | 83.4226 | 1.9205 | 1.9684 | 1.8285
10.8083 | 83.5795 | 83.1791 | 83.4008 | 1.9214 | 1.9694 | 1.8296
10.8125 | 83.568 | 83.1694 | 83.371 | 1.9223 | 1.9703 | 1.8308
10.8167 | 83.5567 | 83.1592 | 83.3429 | 1.9232 | 1.9713 | 1.832
10.8208 | 83.5379 | 83.1648 | 83.3194 | 1.9241 | 1.9721 | 1.8331
10.825 | 83.5275 | 83.1706 | 83.2939 | 1.925 | 1.9729 | 1.8342
10.8292 | 83.5233 | 83.1747 | 83.2694 | 1.9259 | 1.9739 | 1.8355
10.8333 | 83.5213 | 83.1794 | 83.2452 | 1.9268 | 1.9748 | 1.8367
10.8375 | 83.5066 | 83.1673 | 83.2134 | 1.9278 | 1.9757 | 1.8379
10.8417 | 83.491 | 83.1534 | 83.1831 | 1.9288 | 1.9766 | 1.8391
10.8458 | 83.478 | 83.1601 | 83.1597 | 1.9297 | 1.9774 | 1.8403
10.85 | 83.4671 | 83.1676 | 83.134 | 1.9306 | 1.9783 | 1.8415
10.8542 | 83.4655 | 83.166 | 83.1056 | 1.9317 | 1.9792 | 1.8428
10.8583 | 83.4591 | 83.1649 | 83.0786 | 1.9327 | 1.9802 | 1.8441
10.8625 | 83.7332 | 83.4343 | 83.3067 | 1.9314 | 1.9787 | 1.8433
10.8667 | 84.0059 | 83.7064 | 83.54 | 1.93 | 1.9772 | 1.8424
10.8708 | 84.4838 | 84.0981 | 83.8902 | 1.9286 | 1.975 | 1.8409
10.875 | 84.8777 | 84.4954 | 84.2439 | 1.9264 | 1.9728 | 1.8395
10.8792 | 84.9739 | 84.5134 | 84.298 | 1.9238 | 1.9691 | 1.8369
10.8833 | 85.0121 | 84.5304 | 84.3537 | 1.9203 | 1.9653 | 1.8343
10.8875 | 84.9762 | 84.4237 | 84.333 | 1.9158 | 1.9609 | 1.8312
10.8917 | 84.8969 | 84.3147 | 84.3102 | 1.9116 | 1.9564 | 1.8281
10.8958 | 84.7233 | 84.0142 | 84.1202 | 1.9102 | 1.9552 | 1.8276
10.9 | 84.4493 | 83.7125 | 83.9252 | 1.909 | 1.9539 | 1.827
10.9042 | 84.1649 | 83.4579 | 83.7591 | 1.9075 | 1.9525 | 1.8259
10.9083 | 83.9382 | 83.2009 | 83.5918 | 1.9061 | 1.9512 | 1.8249
10.9125 | 83.9102 | 83.2055 | 83.6245 | 1.9056 | 1.9523 | 1.8256
10.9167 | 83.8855 | 83.2101 | 83.654 | 1.9063 | 1.9535 | 1.8264
10.9208 | 83.8075 | 83.0765 | 83.5323 | 1.9073 | 1.9553 | 1.8276
10.925 | 83.6218 | 82.9432 | 83.4091 | 1.9082 | 1.957 | 1.8287
10.9292 | 83.6381 | 83.0672 | 83.4921 | 1.9081 | 1.9571 | 1.8283
10.9333 | 83.7226 | 83.1934 | 83.5794 | 1.9079 | 1.9571 | 1.8279
10.9375 | 83.79 | 83.291 | 83.6388 | 1.9088 | 1.9592 | 1.8293
10.9417 | 83.8285 | 83.3891 | 83.6954 | 1.9108 | 1.9612 | 1.8307
10.9458 | 83.7873 | 83.2988 | 83.5967 | 1.9109 | 1.9609 | 1.8304
10.95 | 83.6712 | 83.2064 | 83.4993 | 1.9108 | 1.9607 | 1.83
10.9542 | 83.7654 | 83.3795 | 83.6336 | 1.9104 | 1.9605 | 1.8298
10.9583 | 83.9404 | 83.5546 | 83.7706 | 1.9106 | 1.9602 | 1.8295
10.9625 | 83.978 | 83.4694 | 83.6983 | 1.9115 | 1.9614 | 1.8305
10.9667 | 83.9252 | 83.3805 | 83.6212 | 1.9131 | 1.9627 | 1.8316
10.9708 | 83.8969 | 83.3331 | 83.5814 | 1.9128 | 1.9614 | 1.8306
10.975 | 83.801 | 83.2848 | 83.545 | 1.9117 | 1.9602 | 1.8296
10.9792 | 83.8798 | 83.4141 | 83.6531 | 1.9114 | 1.961 | 1.8302
10.9833 | 83.9691 | 83.5463 | 83.761 | 1.9118 | 1.9618 | 1.8309
10.9875 | 83.9928 | 83.3819 | 83.6288 | 1.9125 | 1.9623 | 1.8313
10.9917 | 83.8965 | 83.2133 | 83.4933 | 1.9134 | 1.9628 | 1.8317
10.9958 | 83.8527 | 83.2926 | 83.5549 | 1.9132 | 1.962 | 1.8309
11 | 83.8563 | 83.3756 | 83.6215 | 1.9123 | 1.9611 | 1.8302
11.0042 | 83.8658 | 83.4155 | 83.6507 | 1.9121 | 1.9626 | 1.8313
11.0083 | 83.9001 | 83.4547 | 83.6767 | 1.9127 | 1.9641 | 1.8325
11.0125 | 83.877 | 83.3217 | 83.5685 | 1.9132 | 1.9637 | 1.8321
11.0167 | 83.8149 | 83.1844 | 83.4599 | 1.9134 | 1.9632 | 1.8317
11.0208 | 83.7584 | 83.3322 | 83.5715 | 1.9132 | 1.9631 | 1.8316
11.025 | 83.8297 | 83.4864 | 83.6871 | 1.9132 | 1.9631 | 1.8316
11.0292 | 83.8419 | 83.4136 | 83.6265 | 1.9133 | 1.9643 | 1.8325
11.0333 | 83.8189 | 83.3366 | 83.5611 | 1.9141 | 1.9656 | 1.8335
11.0375 | 83.7933 | 83.3011 | 83.5324 | 1.9144 | 1.9646 | 1.8327
11.0417 | 83.777 | 83.2653 | 83.5063 | 1.9141 | 1.9636 | 1.8319
11.0458 | 83.7678 | 83.3955 | 83.6038 | 1.914 | 1.9644 | 1.8325
11.05 | 83.8331 | 83.5307 | 83.702 | 1.9144 | 1.9652 | 1.8331
11.0542 | 83.8309 | 83.375 | 83.5742 | 1.9149 | 1.9658 | 1.8336
11.0583 | 83.7663 | 83.2134 | 83.4434 | 1.9156 | 1.9663 | 1.8341
11.0625 | 83.6961 | 83.2557 | 83.465 | 1.9158 | 1.9657 | 1.8336
11.0667 | 83.7135 | 83.3033 | 83.4917 | 1.9158 | 1.965 | 1.8331
11.0708 | 83.765 | 83.3945 | 83.5665 | 1.9155 | 1.9661 | 1.8339
11.075 | 83.8339 | 83.4842 | 83.6367 | 1.9161 | 1.9672 | 1.8347
11.0792 | 83.8375 | 83.374 | 83.5601 | 1.9168 | 1.9671 | 1.8347
11.0833 | 83.8105 | 83.2579 | 83.4812 | 1.9171 | 1.967 | 1.8346
11.0875 | 83.6853 | 83.2738 | 83.4759 | 1.9174 | 1.9672 | 1.8348
11.0917 | 83.6408 | 83.2999 | 83.4747 | 1.9178 | 1.9674 | 1.8351
11.0958 | 83.6043 | 83.1815 | 83.3684 | 1.9187 | 1.9691 | 1.8364
11.1 | 83.5119 | 83.0622 | 83.2591 | 1.9197 | 1.9709 | 1.8377
11.1042 | 83.4585 | 82.9835 | 83.183 | 1.9213 | 1.9716 | 1.8384
11.1083 | 83.4119 | 82.9075 | 83.1129 | 1.9223 | 1.9722 | 1.839
11.1125 | 83.3916 | 82.9939 | 83.1571 | 1.9235 | 1.9741 | 1.8404
11.1167 | 83.4036 | 83.088 | 83.2037 | 1.925 | 1.976 | 1.8418
11.1208 | 83.463 | 83.0397 | 83.1609 | 1.9264 | 1.9777 | 1.843
11.125 | 83.4586 | 82.9833 | 83.1132 | 1.9276 | 1.9793 | 1.8442
11.1292 | 83.4605 | 83.0591 | 83.1564 | 1.9287 | 1.9799 | 1.8445
11.1333 | 83.511 | 83.137 | 83.2033 | 1.9295 | 1.9804 | 1.8449
11.1375 | 83.5265 | 83.1873 | 83.2244 | 1.9302 | 1.982 | 1.8459
11.1417 | 83.5366 | 83.237 | 83.2426 | 1.9312 | 1.9836 | 1.847
11.1458 | 83.5558 | 83.1763 | 83.1917 | 1.9321 | 1.984 | 1.8473
11.15 | 83.5386 | 83.109 | 83.1388 | 1.9325 | 1.9844 | 1.8475
11.1542 | 83.5221 | 83.1902 | 83.1816 | 1.9331 | 1.9849 | 1.8479
11.1583 | 83.551 | 83.2773 | 83.2281 | 1.9337 | 1.9854 | 1.8483
11.1625 | 83.5513 | 83.2321 | 83.1806 | 1.9343 | 1.9867 | 1.8492
11.1667 | 83.5078 | 83.1836 | 83.1303 | 1.9352 | 1.988 | 1.8501
11.1708 | 83.5043 | 83.163 | 83.1094 | 1.9358 | 1.9881 | 1.8502
11.175 | 83.5033 | 83.1406 | 83.0898 | 1.9362 | 1.988 | 1.8502
11.1792 | 83.4901 | 83.209 | 83.1215 | 1.9368 | 1.9891 | 1.851
11.1833 | 83.5126 | 83.2825 | 83.1547 | 1.9377 | 1.9902 | 1.8519
11.1875 | 83.5066 | 83.2141 | 83.0938 | 1.9384 | 1.991 | 1.8524
11.1917 | 83.4651 | 83.1401 | 83.0301 | 1.939 | 1.9918 | 1.853
11.1958 | 83.47 | 83.1912 | 83.0587 | 1.9396 | 1.9919 | 1.8531
11.2 | 83.5027 | 83.2443 | 83.089 | 1.94 | 1.9919 | 1.8533
11.2042 | 83.4985 | 83.2605 | 83.0859 | 1.9406 | 1.9931 | 1.8542
11.2083 | 83.4946 | 83.2788 | 83.0834 | 1.9415 | 1.9944 | 1.8551
11.2125 | 83.4896 | 83.2065 | 83.0307 | 1.942 | 1.9946 | 1.8553
11.2167 | 83.4618 | 83.1298 | 82.9786 | 1.9423 | 1.9949 | 1.8555
11.2208 | 83.4672 | 83.1942 | 83.0173 | 1.9428 | 1.9954 | 1.8559
11.225 | 83.5061 | 83.2633 | 83.0574 | 1.9434 | 1.9959 | 1.8564
11.2292 | 83.4957 | 83.2392 | 83.0215 | 1.944 | 1.997 | 1.8571
11.2333 | 83.4657 | 83.214 | 82.9823 | 1.9447 | 1.9981 | 1.8579
11.2375 | 83.4604 | 83.2256 | 82.9739 | 1.9451 | 1.998 | 1.858
11.2417 | 83.4537 | 83.2343 | 82.9633 | 1.9453 | 1.9979 | 1.858
11.2458 | 83.4499 | 83.3111 | 82.998 | 1.946 | 1.9985 | 1.8586
11.25 | 83.4629 | 83.3904 | 83.0337 | 1.9467 | 1.9992 | 1.8593
11.2542 | 83.4468 | 83.312 | 82.9735 | 1.9473 | 1.9996 | 1.8597
11.2583 | 83.3961 | 83.2303 | 82.9166 | 1.9479 | 2.0001 | 1.8602
11.2625 | 83.4047 | 83.2365 | 82.9285 | 1.9484 | 2.0001 | 1.8603
11.2667 | 83.437 | 83.2438 | 82.9426 | 1.9487 | 2 | 1.8604
11.2708 | 83.4372 | 83.2495 | 82.941 | 1.9494 | 2.0011 | 1.8612
11.275 | 83.4491 | 83.2577 | 82.9377 | 1.9502 | 2.0021 | 1.8621
11.2792 | 83.4447 | 83.2135 | 82.8992 | 1.9506 | 2.0024 | 1.8622
11.2833 | 83.4169 | 83.1664 | 82.8581 | 1.9508 | 2.0027 | 1.8624
11.2875 | 83.4329 | 83.2309 | 82.8935 | 1.9513 | 2.0032 | 1.8628
11.2917 | 83.4598 | 83.2977 | 82.9286 | 1.9517 | 2.0036 | 1.8632
11.2958 | 83.4421 | 83.2648 | 82.8928 | 1.9522 | 2.0045 | 1.8639
11.3 | 83.4008 | 83.2323 | 82.8591 | 1.953 | 2.0054 | 1.8645
11.3042 | 83.3876 | 83.2232 | 82.8454 | 1.9533 | 2.0055 | 1.8646
11.3083 | 83.3842 | 83.2124 | 82.831 | 1.9535 | 2.0055 | 1.8647
11.3125 | 83.3909 | 83.2681 | 82.8508 | 1.9541 | 2.0062 | 1.8653
11.3167 | 83.4223 | 83.326 | 82.8699 | 1.9548 | 2.0069 | 1.8659
11.3208 | 83.4115 | 83.2845 | 82.8285 | 1.9553 | 2.0073 | 1.8664
11.325 | 83.379 | 83.2403 | 82.7881 | 1.9557 | 2.0078 | 1.8668
11.3292 | 83.3855 | 83.2624 | 82.7971 | 1.9561 | 2.0079 | 1.867
11.3333 | 83.4162 | 83.2836 | 82.806 | 1.9562 | 2.0079 | 1.8673
11.3375 | 83.4124 | 83.3007 | 82.7995 | 1.9568 | 2.0086 | 1.8679
11.3417 | 83.4113 | 83.3191 | 82.7921 | 1.9574 | 2.0092 | 1.8686
11.3458 | 83.3954 | 83.2966 | 82.765 | 1.9578 | 2.0093 | 1.8688
11.35 | 83.3561 | 83.2718 | 82.736 | 1.958 | 2.0094 | 1.8691
11.3542 | 83.3604 | 83.3076 | 82.7498 | 1.9585 | 2.0096 | 1.8695
11.3583 | 83.3806 | 83.3454 | 82.7645 | 1.959 | 2.0098 | 1.87
11.3625 | 83.3587 | 83.3218 | 82.7406 | 1.9596 | 2.0103 | 1.8705
11.3667 | 83.3152 | 83.2983 | 82.718 | 1.9604 | 2.0108 | 1.871
11.3708 | 83.2991 | 83.2844 | 82.706 | 1.9609 | 2.0108 | 1.8713
11.375 | 83.272 | 83.2697 | 82.6931 | 1.9614 | 2.0108 | 1.8716
11.3792 | 83.2748 | 83.2936 | 82.7008 | 1.962 | 2.0113 | 1.8721
11.3833 | 83.3044 | 83.3203 | 82.7088 | 1.9629 | 2.0117 | 1.8726
11.3875 | 83.2843 | 83.2764 | 82.6798 | 1.9635 | 2.0122 | 1.8731
11.3917 | 83.2614 | 83.2308 | 82.6525 | 1.9643 | 2.0127 | 1.8735
11.3958 | 83.2607 | 83.2238 | 82.6472 | 1.9648 | 2.013 | 1.8739
11.4 | 83.2681 | 83.217 | 82.6426 | 1.9654 | 2.0133 | 1.8742
11.4042 | 83.2757 | 83.2297 | 82.6404 | 1.966 | 2.0141 | 1.8748
11.4083 | 83.2975 | 83.2434 | 82.6364 | 1.9667 | 2.0149 | 1.8753
11.4125 | 83.2966 | 83.2166 | 82.6125 | 1.9672 | 2.0155 | 1.8758
11.4167 | 83.2888 | 83.188 | 82.589 | 1.9676 | 2.016 | 1.8762
11.4208 | 83.301 | 83.2033 | 82.5891 | 1.968 | 2.0166 | 1.8766
11.425 | 83.3166 | 83.2202 | 82.5897 | 1.9684 | 2.0171 | 1.877
11.4292 | 83.3092 | 83.2288 | 82.5771 | 1.9688 | 2.0178 | 1.8776
11.4333 | 83.3029 | 83.2373 | 82.5627 | 1.9693 | 2.0186 | 1.8781
11.4375 | 83.2939 | 83.241 | 82.5466 | 1.9697 | 2.0189 | 1.8785
11.4417 | 83.2839 | 83.2443 | 82.5306 | 1.97 | 2.0193 | 1.8789
11.4458 | 83.2855 | 83.274 | 82.5325 | 1.9704 | 2.0197 | 1.8794
11.45 | 83.283 | 83.3046 | 82.5337 | 1.9709 | 2.0201 | 1.8799
11.4542 | 83.2709 | 83.2994 | 82.5123 | 1.9713 | 2.0205 | 1.8804
11.4583 | 83.248 | 83.2924 | 82.4917 | 1.9718 | 2.0209 | 1.8809
11.4625 | 83.2395 | 83.3134 | 82.4845 | 1.9723 | 2.0209 | 1.8813
11.4667 | 83.2356 | 83.3344 | 82.4773 | 1.9728 | 2.0209 | 1.8816
11.4708 | 83.2255 | 83.3548 | 82.474 | 1.9733 | 2.0212 | 1.8822
11.475 | 83.2158 | 83.3752 | 82.4691 | 1.974 | 2.0214 | 1.8827
11.4792 | 83.2076 | 83.3512 | 82.4428 | 1.9745 | 2.0215 | 1.8832
11.4833 | 83.1981 | 83.3257 | 82.4191 | 1.975 | 2.0215 | 1.8837
11.4875 | 83.204 | 83.3526 | 82.4211 | 1.9755 | 2.0214 | 1.8841
11.4917 | 83.2129 | 83.3808 | 82.4224 | 1.9762 | 2.0213 | 1.8845
11.4958 | 83.2073 | 83.3926 | 82.4176 | 1.9767 | 2.0214 | 1.885
11.5 | 83.2021 | 83.4048 | 82.4115 | 1.9773 | 2.0215 | 1.8856
11.5042 | 83.1915 | 83.3828 | 82.3928 | 1.9777 | 2.0214 | 1.8859
11.5083 | 83.1904 | 83.3605 | 82.3762 | 1.9782 | 2.0212 | 1.8863
11.5125 | 83.1822 | 83.3744 | 82.3744 | 1.9788 | 2.0211 | 1.8868
11.5167 | 83.1739 | 83.3887 | 82.3713 | 1.9794 | 2.0211 | 1.8872
11.5208 | 83.1603 | 83.3794 | 82.3539 | 1.98 | 2.0212 | 1.8877
11.525 | 83.1459 | 83.3688 | 82.336 | 1.9806 | 2.0212 | 1.8882
11.5292 | 83.1474 | 83.3579 | 82.3254 | 1.9811 | 2.0211 | 1.8886
11.5333 | 83.1568 | 83.3473 | 82.3157 | 1.9816 | 2.021 | 1.889
11.5375 | 83.1573 | 83.3468 | 82.3079 | 1.9822 | 2.0212 | 1.8896
11.5417 | 83.1525 | 83.3473 | 82.3002 | 1.9829 | 2.0214 | 1.8901
11.5458 | 83.1442 | 83.3308 | 82.2808 | 1.9834 | 2.0215 | 1.8906
11.55 | 83.1385 | 83.3123 | 82.2608 | 1.9838 | 2.0217 | 1.891
11.5542 | 83.1422 | 83.3099 | 82.2558 | 1.9843 | 2.0218 | 1.8915
11.5583 | 83.1501 | 83.3067 | 82.25 | 1.9849 | 2.022 | 1.892
11.5625 | 83.1466 | 83.285 | 82.2316 | 1.9854 | 2.0225 | 1.8926
11.5667 | 83.14 | 83.264 | 82.2148 | 1.9859 | 2.0229 | 1.8931
11.5708 | 83.1349 | 83.2536 | 82.1991 | 1.9863 | 2.0232 | 1.8936
11.575 | 83.1338 | 83.242 | 82.1809 | 1.9868 | 2.0236 | 1.8941
11.5792 | 83.1334 | 83.246 | 82.1757 | 1.9872 | 2.0241 | 1.8947
11.5833 | 83.1268 | 83.2491 | 82.1697 | 1.9878 | 2.0247 | 1.8952
11.5875 | 83.1183 | 83.219 | 82.1448 | 1.9882 | 2.0254 | 1.8958
11.5917 | 83.1042 | 83.1893 | 82.1234 | 1.9887 | 2.026 | 1.8964
11.5958 | 83.1012 | 83.1966 | 82.1146 | 1.9892 | 2.0265 | 1.8969
11.6 | 83.0989 | 83.2048 | 82.1021 | 1.9897 | 2.027 | 1.8974
11.6042 | 83.0877 | 83.2073 | 82.0916 | 1.9902 | 2.0279 | 1.8981
11.6083 | 83.0822 | 83.2105 | 82.0813 | 1.9908 | 2.0287 | 1.8987
11.6125 | 83.0658 | 83.1814 | 82.0553 | 1.9914 | 2.0294 | 1.8993
11.6167 | 83.0632 | 83.1527 | 82.0324 | 1.9919 | 2.0301 | 1.8999
11.6208 | 83.0595 | 83.1724 | 82.0262 | 1.9925 | 2.0307 | 1.9005
11.625 | 83.0553 | 83.1929 | 82.0159 | 1.9931 | 2.0314 | 1.9011
11.6292 | 83.0462 | 83.1881 | 81.9981 | 1.9937 | 2.0324 | 1.9018
11.6333 | 83.0363 | 83.1837 | 81.9817 | 1.9943 | 2.0333 | 1.9025
11.6375 | 83.0312 | 83.1651 | 81.9605 | 1.9948 | 2.034 | 1.903
11.6417 | 83.0297 | 83.1469 | 81.9405 | 1.9954 | 2.0346 | 1.9036
11.6458 | 83.0278 | 83.1667 | 81.9323 | 1.996 | 2.0354 | 1.9043
11.65 | 83.0147 | 83.1872 | 81.9212 | 1.9967 | 2.0363 | 1.905
11.6542 | 83.0056 | 83.1728 | 81.8977 | 1.9973 | 2.0372 | 1.9057
11.6583 | 82.9918 | 83.1577 | 81.8764 | 1.9979 | 2.0381 | 1.9064
11.6625 | 82.9932 | 83.1519 | 81.86 | 1.9985 | 2.0388 | 1.907
11.6667 | 82.9889 | 83.1457 | 81.8425 | 1.9992 | 2.0395 | 1.9076
11.6708 | 82.9838 | 83.1607 | 81.8295 | 1.9998 | 2.0404 | 1.9084
11.675 | 82.9676 | 83.1757 | 81.8145 | 2.0006 | 2.0413 | 1.9091
11.6792 | 82.9568 | 83.1641 | 81.791 | 2.0011 | 2.0422 | 1.9098
11.6833 | 82.9494 | 83.1526 | 81.7691 | 2.0018 | 2.043 | 1.9105
11.6875 | 82.9481 | 83.158 | 81.7545 | 2.0025 | 2.0438 | 1.9112
11.6917 | 82.9443 | 83.1644 | 81.7387 | 2.0032 | 2.0445 | 1.9119
11.6958 | 82.9229 | 83.1647 | 81.7142 | 2.004 | 2.0454 | 1.9127
11.7 | 82.9064 | 83.1651 | 81.6898 | 2.0048 | 2.0464 | 1.9135
11.7042 | 82.8852 | 83.1529 | 81.6621 | 2.0055 | 2.0472 | 1.9143
11.7083 | 82.8815 | 83.141 | 81.6348 | 2.0062 | 2.0479 | 1.9151
11.7125 | 82.963 | 83.2347 | 81.6981 | 2.0064 | 2.0481 | 1.9153
11.7167 | 83.0488 | 83.3291 | 81.7618 | 2.0065 | 2.0483 | 1.9155
11.7208 | 83.032 | 83.3306 | 81.7474 | 2.0074 | 2.0491 | 1.9163
11.725 | 83.0292 | 83.3306 | 81.7349 | 2.0082 | 2.05 | 1.9173
11.7292 | 82.8747 | 83.222 | 81.6185 | 2.0089 | 2.0503 | 1.9178
11.7333 | 82.7635 | 83.1126 | 81.5008 | 2.0092 | 2.0506 | 1.9183
11.7375 | 82.7958 | 83.2299 | 81.5619 | 2.0099 | 2.0505 | 1.9186
11.7417 | 82.8917 | 83.3485 | 81.6228 | 2.0098 | 2.0504 | 1.9188
11.7458 | 83.0958 | 83.5872 | 81.7751 | 2.0099 | 2.0496 | 1.9187
11.75 | 83.3149 | 83.8285 | 81.9327 | 2.0093 | 2.0488 | 1.9186
11.7542 | 83.6766 | 84.0896 | 82.1284 | 2.0078 | 2.0456 | 1.9168
11.7583 | 83.9479 | 84.3528 | 82.3307 | 2.0052 | 2.0424 | 1.915
11.7625 | 84.1124 | 84.395 | 82.4 | 2.0037 | 2.0394 | 1.9136
11.7667 | 84.1821 | 84.4341 | 82.4753 | 2.0013 | 2.0363 | 1.9122
11.7708 | 84.122 | 84.22 | 82.3775 | 1.9979 | 2.0327 | 1.9104
11.775 | 83.9666 | 84.0033 | 82.2831 | 1.9947 | 2.0291 | 1.9086
11.7792 | 83.9117 | 83.8053 | 82.2211 | 1.9927 | 2.0273 | 1.9078
11.7833 | 83.8213 | 83.6068 | 82.1566 | 1.9909 | 2.0256 | 1.9069
11.7875 | 83.5709 | 83.3528 | 82.0312 | 1.9904 | 2.0258 | 1.9073
11.7917 | 83.3834 | 83.0958 | 81.9003 | 1.9903 | 2.0261 | 1.9076
11.7958 | 83.2947 | 82.9951 | 81.8561 | 1.9895 | 2.0268 | 1.9077
11.8 | 83.1597 | 82.8953 | 81.8063 | 1.9891 | 2.0274 | 1.9077
11.8042 | 83.1044 | 82.9276 | 81.8248 | 1.99 | 2.0295 | 1.9088
11.8083 | 83.0948 | 82.9634 | 81.8389 | 1.991 | 2.0316 | 1.9097
11.8125 | 82.9912 | 82.9987 | 81.8319 | 1.9908 | 2.0328 | 1.91
11.8167 | 82.9645 | 83.0353 | 81.8231 | 1.9916 | 2.034 | 1.9103
11.8208 | 83.0497 | 83.1561 | 81.8775 | 1.9922 | 2.0348 | 1.9105
11.825 | 83.0613 | 83.2785 | 81.9326 | 1.993 | 2.0356 | 1.9107
11.8292 | 83.01 | 83.3136 | 81.9249 | 1.9941 | 2.0362 | 1.911
11.8333 | 83.0415 | 83.3486 | 81.9194 | 1.9947 | 2.0368 | 1.9113
11.8375 | 83.0713 | 83.3863 | 81.9356 | 1.9943 | 2.0364 | 1.911
11.8417 | 83.1654 | 83.4223 | 81.9527 | 1.9942 | 2.0359 | 1.9106
11.8458 | 83.2281 | 83.4242 | 81.9527 | 1.9951 | 2.0362 | 1.9109
11.85 | 83.2595 | 83.4238 | 81.9539 | 1.9957 | 2.0365 | 1.9113
11.8542 | 83.1768 | 83.377 | 81.9218 | 1.996 | 2.0361 | 1.9111
11.8583 | 83.1426 | 83.3293 | 81.8904 | 1.9959 | 2.0357 | 1.9108
11.8625 | 83.2081 | 83.3606 | 81.9263 | 1.9952 | 2.0357 | 1.9109
11.8667 | 83.2871 | 83.392 | 81.9608 | 1.9949 | 2.0358 | 1.9109
11.8708 | 83.3414 | 83.3274 | 81.9137 | 1.9957 | 2.0363 | 1.9113
11.875 | 83.3207 | 83.2621 | 81.8679 | 1.9964 | 2.0368 | 1.9117
11.8792 | 83.281 | 83.2826 | 81.884 | 1.9964 | 2.0364 | 1.9113
11.8833 | 83.2203 | 83.305 | 81.8989 | 1.996 | 2.0361 | 1.9109
11.8875 | 83.2651 | 83.3333 | 81.921 | 1.9953 | 2.0369 | 1.9115
11.8917 | 83.2736 | 83.36 | 81.9419 | 1.9952 | 2.0377 | 1.912
11.8958 | 83.3149 | 83.2931 | 81.8846 | 1.9959 | 2.0377 | 1.9119
11.9 | 83.271 | 83.2257 | 81.8295 | 1.9963 | 2.0377 | 1.9119
11.9042 | 83.2165 | 83.3018 | 81.8803 | 1.9964 | 2.0376 | 1.9118
11.9083 | 83.1695 | 83.3816 | 81.9292 | 1.9961 | 2.0376 | 1.9117
11.9125 | 83.1934 | 83.3431 | 81.8978 | 1.9956 | 2.0385 | 1.9123
11.9167 | 83.177 | 83.3004 | 81.8669 | 1.9957 | 2.0393 | 1.9128
11.9208 | 83.208 | 83.3063 | 81.8741 | 1.9961 | 2.0386 | 1.9123
11.925 | 83.1767 | 83.3134 | 81.8815 | 1.9962 | 2.0379 | 1.9117
11.9292 | 83.1553 | 83.3724 | 81.9205 | 1.9963 | 2.0386 | 1.9122
11.9333 | 83.1068 | 83.4339 | 81.9581 | 1.9964 | 2.0393 | 1.9127
11.9375 | 83.1066 | 83.2853 | 81.8372 | 1.9966 | 2.0398 | 1.913
11.9417 | 83.0659 | 83.133 | 81.7202 | 1.9971 | 2.0402 | 1.9134
11.9458 | 83.0424 | 83.2232 | 81.7837 | 1.9974 | 2.0397 | 1.913
11.95 | 83.0559 | 83.3186 | 81.8442 | 1.9977 | 2.0391 | 1.9125
11.9542 | 83.0903 | 83.3701 | 81.8857 | 1.9976 | 2.0404 | 1.9134
11.9583 | 83.1466 | 83.4179 | 81.9258 | 1.9979 | 2.0417 | 1.9142
11.9625 | 83.1219 | 83.2859 | 81.8337 | 1.9986 | 2.0415 | 1.914
11.9667 | 83.0942 | 83.1504 | 81.7448 | 1.9989 | 2.0412 | 1.9139
11.9708 | 83.0046 | 83.2119 | 81.7855 | 1.9993 | 2.0416 | 1.914
11.975 | 82.9597 | 83.2812 | 81.8227 | 1.9995 | 2.0419 | 1.9141
11.9792 | 82.9485 | 83.157 | 81.7291 | 2.0003 | 2.0438 | 1.9153
11.9833 | 82.9051 | 83.0283 | 81.6395 | 2.0012 | 2.0457 | 1.9165
11.9875 | 82.8444 | 82.9579 | 81.5798 | 2.0027 | 2.0461 | 1.9166
11.9917 | 82.7857 | 82.8935 | 81.5221 | 2.0037 | 2.0464 | 1.9167
11.9958 | 82.7862 | 83.0141 | 81.5914 | 2.0044 | 2.0483 | 1.9178
12 | 82.8012 | 83.1405 | 81.6552 | 2.0054 | 2.0503 | 1.9188
12.0042 | 82.8674 | 83.063 | 81.5883 | 2.0066 | 2.0519 | 1.9197
12.0083 | 82.8845 | 82.9764 | 81.5247 | 2.0078 | 2.0534 | 1.9205
12.0125 | 82.8559 | 83.0687 | 81.5689 | 2.0086 | 2.0536 | 1.9204
12.0167 | 82.867 | 83.1676 | 81.6109 | 2.0092 | 2.0537 | 1.9203
12.0208 | 82.9151 | 83.2376 | 81.6449 | 2.0094 | 2.0553 | 1.9212
12.025 | 82.9509 | 83.3032 | 81.676 | 2.01 | 2.057 | 1.9221
12.0292 | 82.9647 | 83.2117 | 81.6048 | 2.0109 | 2.0572 | 1.9221
12.0333 | 82.9552 | 83.1141 | 81.5389 | 2.0115 | 2.0573 | 1.9222
12.0375 | 82.9063 | 83.2206 | 81.5963 | 2.0116 | 2.0575 | 1.9222
12.0417 | 82.9028 | 83.3358 | 81.6505 | 2.0119 | 2.0577 | 1.9223
12.0458 | 82.947 | 83.2812 | 81.6105 | 2.0122 | 2.0591 | 1.9231
12.05 | 82.9395 | 83.2179 | 81.572 | 2.0128 | 2.0605 | 1.9239
12.0542 | 82.9062 | 83.1728 | 81.5367 | 2.0136 | 2.0602 | 1.9237
12.0583 | 82.8864 | 83.1301 | 81.5048 | 2.014 | 2.0598 | 1.9235
12.0625 | 82.8654 | 83.2242 | 81.5547 | 2.0141 | 2.0608 | 1.9241
12.0667 | 82.876 | 83.3239 | 81.6 | 2.0147 | 2.0619 | 1.9246
12.0708 | 82.9117 | 83.2319 | 81.5359 | 2.0153 | 2.0627 | 1.9251
12.075 | 82.9005 | 83.1301 | 81.4745 | 2.0159 | 2.0635 | 1.9256
12.0792 | 82.8615 | 83.1883 | 81.5006 | 2.0164 | 2.0633 | 1.9254
12.0833 | 82.8673 | 83.2547 | 81.5255 | 2.0167 | 2.063 | 1.9253
12.0875 | 82.8804 | 83.2852 | 81.5357 | 2.0169 | 2.0644 | 1.9261
12.0917 | 82.8837 | 83.3139 | 81.5447 | 2.0175 | 2.0658 | 1.9268
12.0958 | 82.8945 | 83.2155 | 81.4856 | 2.0182 | 2.0659 | 1.9268
12.1 | 82.8796 | 83.1114 | 81.4319 | 2.0186 | 2.0659 | 1.9269
12.1042 | 82.8487 | 83.1988 | 81.4772 | 2.0188 | 2.0663 | 1.9271
12.1083 | 82.8673 | 83.2969 | 81.5193 | 2.0192 | 2.0666 | 1.9273
12.1125 | 82.8911 | 83.2653 | 81.4876 | 2.0195 | 2.0678 | 1.9279
12.1167 | 82.8825 | 83.2262 | 81.4545 | 2.02 | 2.069 | 1.9285
12.1208 | 82.8629 | 83.228 | 81.4429 | 2.0206 | 2.0686 | 1.9284
12.125 | 82.856 | 83.2297 | 81.4308 | 2.0209 | 2.0682 | 1.9282
12.1292 | 82.8364 | 83.3223 | 81.4713 | 2.0211 | 2.0689 | 1.9287
12.1333 | 82.837 | 83.42 | 81.5096 | 2.0216 | 2.0696 | 1.9291
12.1375 | 82.8549 | 83.312 | 81.4468 | 2.0222 | 2.0701 | 1.9295
12.1417 | 82.8277 | 83.1946 | 81.3909 | 2.0226 | 2.0706 | 1.9299
12.1458 | 82.8052 | 83.2191 | 81.4096 | 2.0231 | 2.0703 | 1.9297
12.15 | 82.8256 | 83.2507 | 81.4275 | 2.0234 | 2.0699 | 1.9296
12.1542 | 82.8349 | 83.2712 | 81.4338 | 2.0237 | 2.0711 | 1.9303
12.1583 | 82.8433 | 83.2917 | 81.437 | 2.0242 | 2.0724 | 1.931
12.1625 | 82.8603 | 83.2167 | 81.3903 | 2.0247 | 2.0725 | 1.931
12.1667 | 82.8405 | 83.136 | 81.3463 | 2.0249 | 2.0726 | 1.9311
12.1708 | 82.8282 | 83.2238 | 81.3917 | 2.0252 | 2.0729 | 1.9312
12.175 | 82.8422 | 83.3202 | 81.4336 | 2.0255 | 2.0733 | 1.9314
12.1792 | 82.8431 | 83.275 | 81.3959 | 2.0258 | 2.0744 | 1.932
12.1833 | 82.8173 | 83.2246 | 81.3609 | 2.0264 | 2.0755 | 1.9326
12.1875 | 82.8063 | 83.2158 | 81.3483 | 2.0268 | 2.0752 | 1.9324
12.1917 | 82.8023 | 83.2068 | 81.3354 | 2.027 | 2.0748 | 1.9323
12.1958 | 82.7985 | 83.2909 | 81.3701 | 2.0273 | 2.0755 | 1.9328
12.2 | 82.8165 | 83.3802 | 81.4016 | 2.0278 | 2.0764 | 1.9333
12.2042 | 82.8216 | 83.2943 | 81.3441 | 2.0282 | 2.0768 | 1.9336
12.2083 | 82.7986 | 83.2002 | 81.2929 | 2.0285 | 2.0772 | 1.9339
12.2125 | 82.7903 | 83.2485 | 81.3172 | 2.0289 | 2.0769 | 1.9338
12.2167 | 82.8121 | 83.3003 | 81.3376 | 2.029 | 2.0766 | 1.9338
12.2208 | 82.8121 | 83.3269 | 81.3363 | 2.0293 | 2.0775 | 1.9344
12.225 | 82.8042 | 83.3546 | 81.3337 | 2.0299 | 2.0785 | 1.935
12.2292 | 82.8021 | 83.2915 | 81.2935 | 2.0303 | 2.0783 | 1.935
12.2333 | 82.7799 | 83.2231 | 81.2566 | 2.0304 | 2.0781 | 1.9351
12.2375 | 82.7679 | 83.2935 | 81.2925 | 2.0307 | 2.0783 | 1.9353
12.2417 | 82.781 | 83.3702 | 81.3246 | 2.0312 | 2.0784 | 1.9356
12.2458 | 82.7712 | 83.3242 | 81.289 | 2.0316 | 2.0791 | 1.9361
12.25 | 82.7194 | 83.2752 | 81.2569 | 2.0324 | 2.0798 | 1.9366
12.2542 | 82.7141 | 83.2619 | 81.2519 | 2.0327 | 2.0795 | 1.9365
12.2583 | 82.7151 | 83.2478 | 81.2457 | 2.0331 | 2.0791 | 1.9364
12.2625 | 82.7076 | 83.2923 | 81.2655 | 2.0335 | 2.0798 | 1.937
12.2667 | 82.7303 | 83.3422 | 81.2844 | 2.0344 | 2.0806 | 1.9374
12.2708 | 82.7197 | 83.2579 | 81.2379 | 2.0348 | 2.0811 | 1.9377
12.275 | 82.6799 | 83.1677 | 81.1967 | 2.0354 | 2.0815 | 1.9379
12.2792 | 82.6802 | 83.2019 | 81.216 | 2.0358 | 2.0816 | 1.938
12.2833 | 82.72 | 83.2388 | 81.2306 | 2.0361 | 2.0816 | 1.9381
12.2875 | 82.723 | 83.248 | 81.2244 | 2.0366 | 2.0827 | 1.9387
12.2917 | 82.733 | 83.2588 | 81.219 | 2.0373 | 2.0838 | 1.9392
12.2958 | 82.7383 | 83.2002 | 81.1874 | 2.0376 | 2.0841 | 1.9393
12.3 | 82.7126 | 83.1367 | 81.1585 | 2.0377 | 2.0843 | 1.9394
12.3042 | 82.7186 | 83.2012 | 81.182 | 2.0381 | 2.0848 | 1.9397
12.3083 | 82.7601 | 83.2711 | 81.201 | 2.0383 | 2.0852 | 1.94
12.3125 | 82.7508 | 83.2588 | 81.1761 | 2.0386 | 2.0861 | 1.9404
12.3167 | 82.7242 | 83.2445 | 81.1532 | 2.0391 | 2.087 | 1.9408
12.3208 | 82.7218 | 83.2389 | 81.144 | 2.0394 | 2.0869 | 1.9409
12.325 | 82.7068 | 83.2317 | 81.1342 | 2.0394 | 2.0869 | 1.941
12.3292 | 82.7072 | 83.286 | 81.1454 | 2.0398 | 2.0874 | 1.9414
12.3333 | 82.7266 | 83.3442 | 81.1551 | 2.0403 | 2.0879 | 1.9418
12.3375 | 82.7124 | 83.3184 | 81.1264 | 2.0406 | 2.0881 | 1.9421
12.3417 | 82.6698 | 83.2877 | 81.1005 | 2.041 | 2.0884 | 1.9424
12.3458 | 82.6622 | 83.3203 | 81.1088 | 2.0414 | 2.0882 | 1.9425
12.35 | 82.6719 | 83.3545 | 81.1144 | 2.0416 | 2.0879 | 1.9427
12.3542 | 82.6642 | 83.3639 | 81.1059 | 2.0421 | 2.0883 | 1.9432
12.3583 | 82.6611 | 83.3739 | 81.0986 | 2.0428 | 2.0887 | 1.9436
12.3625 | 82.6571 | 83.3412 | 81.0741 | 2.0432 | 2.0885 | 1.9438
12.3667 | 82.6275 | 83.3046 | 81.052 | 2.0436 | 2.0883 | 1.944
12.3708 | 82.6346 | 83.3566 | 81.0699 | 2.044 | 2.0882 | 1.9443
12.375 | 82.6659 | 83.4132 | 81.0837 | 2.0444 | 2.088 | 1.9445
12.3792 | 82.6618 | 83.3914 | 81.0667 | 2.0448 | 2.0883 | 1.9449
12.3833 | 82.646 | 83.3684 | 81.0526 | 2.0454 | 2.0885 | 1.9453
12.3875 | 82.6385 | 83.3486 | 81.0398 | 2.0458 | 2.0881 | 1.9454
12.3917 | 82.6283 | 83.3277 | 81.0279 | 2.046 | 2.0877 | 1.9456
12.3958 | 82.621 | 83.3678 | 81.0384 | 2.0464 | 2.0878 | 1.9459
12.4 | 82.6328 | 83.4104 | 81.0446 | 2.047 | 2.0879 | 1.9462
12.4042 | 82.6262 | 83.365 | 81.0193 | 2.0474 | 2.088 | 1.9466
12.4083 | 82.5988 | 83.3161 | 80.9981 | 2.0479 | 2.0882 | 1.9469
12.4125 | 82.6 | 83.3156 | 80.9955 | 2.0483 | 2.088 | 1.947
12.4167 | 82.616 | 83.3172 | 80.9926 | 2.0486 | 2.0877 | 1.9472
12.4208 | 82.6114 | 83.3354 | 80.9924 | 2.049 | 2.0881 | 1.9476
12.425 | 82.6094 | 83.3536 | 80.9893 | 2.0497 | 2.0885 | 1.948
12.4292 | 82.6067 | 83.3078 | 80.9664 | 2.05 | 2.0886 | 1.9483
12.4333 | 82.5903 | 83.2579 | 80.9471 | 2.0503 | 2.0887 | 1.9485
12.4375 | 82.5948 | 83.2683 | 80.95 | 2.0507 | 2.0889 | 1.9488
12.4417 | 82.6162 | 83.2819 | 80.9511 | 2.0511 | 2.089 | 1.9491
12.4458 | 82.6106 | 83.273 | 80.9389 | 2.0514 | 2.0896 | 1.9495
12.45 | 82.5952 | 83.2626 | 80.9253 | 2.0519 | 2.0902 | 1.9499
12.4542 | 82.5918 | 83.2348 | 80.9106 | 2.0522 | 2.0905 | 1.9501
12.4583 | 82.5911 | 83.2046 | 80.8972 | 2.0524 | 2.0908 | 1.9504
12.4625 | 82.5906 | 83.2169 | 80.8978 | 2.0528 | 2.0913 | 1.9508
12.4667 | 82.5933 | 83.2317 | 80.8972 | 2.0533 | 2.0919 | 1.9512
12.4708 | 82.5879 | 83.2105 | 80.8779 | 2.0537 | 2.0926 | 1.9515
12.475 | 82.5579 | 83.1878 | 80.8592 | 2.054 | 2.0933 | 1.9519
12.4792 | 82.558 | 83.189 | 80.8548 | 2.0544 | 2.0937 | 1.9522
12.4833 | 82.5644 | 83.1913 | 80.8495 | 2.0547 | 2.0942 | 1.9525
12.4875 | 82.557 | 83.1932 | 80.8421 | 2.0552 | 2.095 | 1.9529
12.4917 | 82.5505 | 83.1969 | 80.8355 | 2.0558 | 2.0958 | 1.9533
12.4958 | 82.5402 | 83.1763 | 80.8154 | 2.0562 | 2.0964 | 1.9537
12.5 | 82.5222 | 83.1543 | 80.7964 | 2.0565 | 2.097 | 1.954
12.5042 | 82.5221 | 83.175 | 80.7972 | 2.057 | 2.0977 | 1.9544
12.5083 | 82.5333 | 83.1977 | 80.7952 | 2.0575 | 2.0983 | 1.9547
12.5125 | 82.5253 | 83.1833 | 80.779 | 2.058 | 2.0992 | 1.9552
12.5167 | 82.5132 | 83.1687 | 80.765 | 2.0585 | 2.1001 | 1.9556
12.5208 | 82.5063 | 83.1613 | 80.7513 | 2.0589 | 2.1006 | 1.9559
12.525 | 82.4995 | 83.1535 | 80.737 | 2.0593 | 2.1011 | 1.9563
12.5292 | 82.4996 | 83.1755 | 80.7361 | 2.0598 | 2.1019 | 1.9567
12.5333 | 82.4988 | 83.1992 | 80.7331 | 2.0603 | 2.1027 | 1.9571
12.5375 | 82.492 | 83.1701 | 80.7105 | 2.0608 | 2.1035 | 1.9576
12.5417 | 82.4724 | 83.1391 | 80.6914 | 2.0613 | 2.1043 | 1.958
12.5458 | 82.4698 | 83.147 | 80.6823 | 2.0618 | 2.1049 | 1.9584
12.55 | 82.4637 | 83.1547 | 80.67 | 2.0623 | 2.1054 | 1.9588
12.5542 | 82.4619 | 83.1674 | 80.6624 | 2.0628 | 2.1064 | 1.9593
12.5583 | 82.4525 | 83.1811 | 80.6541 | 2.0634 | 2.1073 | 1.9597
12.5625 | 82.479 | 83.1856 | 80.6609 | 2.0637 | 2.1078 | 1.9599
12.5667 | 82.4973 | 83.1892 | 80.6709 | 2.064 | 2.1082 | 1.9602
12.5708 | 82.4588 | 83.1752 | 80.6348 | 2.0648 | 2.1092 | 1.9609
12.575 | 82.4155 | 83.1623 | 80.595 | 2.0658 | 2.1101 | 1.9616
12.5792 | 82.3596 | 83.1241 | 80.546 | 2.0662 | 2.1109 | 1.962
12.5833 | 82.3125 | 83.0863 | 80.4976 | 2.0667 | 2.1116 | 1.9624
12.5875 | 82.3988 | 83.177 | 80.562 | 2.067 | 2.1119 | 1.9626
12.5917 | 82.499 | 83.2683 | 80.626 | 2.0674 | 2.1122 | 1.9628
12.5958 | 82.5696 | 83.3562 | 80.6691 | 2.0676 | 2.1125 | 1.9631
12.6 | 82.6278 | 83.4455 | 80.7128 | 2.0679 | 2.1128 | 1.9633
12.6042 | 82.6102 | 83.3865 | 80.6675 | 2.0684 | 2.1129 | 1.9634
12.6083 | 82.6065 | 83.3248 | 80.6287 | 2.0686 | 2.1129 | 1.9635
12.6125 | 82.4305 | 83.2598 | 80.5592 | 2.0694 | 2.113 | 1.9639
12.6167 | 82.3564 | 83.1942 | 80.4842 | 2.07 | 2.1132 | 1.9644
12.6208 | 82.3177 | 83.3249 | 80.5319 | 2.0699 | 2.1126 | 1.9643
12.625 | 82.3756 | 83.4597 | 80.5739 | 2.0693 | 2.1121 | 1.9642
12.6292 | 82.567 | 83.6786 | 80.694 | 2.0698 | 2.1109 | 1.964
12.6333 | 82.7981 | 83.8991 | 80.8165 | 2.0692 | 2.1098 | 1.964
12.6375 | 83.0041 | 84.0609 | 80.9004 | 2.0685 | 2.1069 | 1.9629
12.6417 | 83.1574 | 84.2221 | 80.9876 | 2.0669 | 2.1039 | 1.9618
12.6458 | 83.3495 | 84.2522 | 81.0368 | 2.0653 | 2.1008 | 1.9607
12.65 | 83.4136 | 84.2799 | 81.0992 | 2.0631 | 2.0976 | 1.9595
12.6542 | 83.4006 | 84.0818 | 81.0336 | 2.0612 | 2.095 | 1.9588
12.6583 | 83.3346 | 83.8795 | 80.9779 | 2.0592 | 2.0924 | 1.9581
12.6625 | 83.2639 | 83.6651 | 80.9209 | 2.057 | 2.0908 | 1.9574
12.6667 | 83.175 | 83.4487 | 80.8624 | 2.0554 | 2.0892 | 1.9567
12.6708 | 83.0784 | 83.2305 | 80.7956 | 2.0546 | 2.09 | 1.9572
12.675 | 82.9218 | 83.0106 | 80.7269 | 2.0546 | 2.0909 | 1.9577
12.6792 | 82.8105 | 82.8903 | 80.6773 | 2.0541 | 2.092 | 1.9579
12.6833 | 82.6824 | 82.7727 | 80.6176 | 2.0538 | 2.0931 | 1.958
12.6875 | 82.6231 | 82.845 | 80.6621 | 2.0539 | 2.0951 | 1.9585
12.6917 | 82.6015 | 82.9218 | 80.6964 | 2.0542 | 2.0971 | 1.959
12.6958 | 82.5294 | 82.9547 | 80.6761 | 2.0548 | 2.0989 | 1.9596
12.7 | 82.4168 | 82.9888 | 80.6554 | 2.0557 | 2.1007 | 1.9602
12.7042 | 82.4398 | 83.1237 | 80.696 | 2.0561 | 2.101 | 1.9599
12.7083 | 82.4534 | 83.2621 | 80.7335 | 2.0564 | 2.1013 | 1.9596
12.7125 | 82.4733 | 83.3561 | 80.7627 | 2.0572 | 2.1021 | 1.96
12.7167 | 82.5485 | 83.449 | 80.7949 | 2.0583 | 2.1028 | 1.9604
12.7208 | 82.5568 | 83.4153 | 80.7508 | 2.0584 | 2.1023 | 1.9602
12.725 | 82.5247 | 83.3778 | 80.7128 | 2.0587 | 2.1017 | 1.96
12.7292 | 82.5702 | 83.4398 | 80.7588 | 2.0589 | 2.1012 | 1.9598
12.7333 | 82.6266 | 83.5018 | 80.8034 | 2.0589 | 2.1007 | 1.9596
12.7375 | 82.5855 | 83.4348 | 80.7697 | 2.0594 | 2.101 | 1.96
12.7417 | 82.5924 | 83.364 | 80.7399 | 2.0598 | 2.1013 | 1.9603
12.7458 | 82.6127 | 83.3213 | 80.7244 | 2.0595 | 2.1006 | 1.9599
12.75 | 82.6329 | 83.2791 | 80.7089 | 2.059 | 2.1 | 1.9595
12.7542 | 82.6541 | 83.3126 | 80.7404 | 2.0593 | 2.1005 | 1.9599
12.7583 | 82.7187 | 83.3484 | 80.7686 | 2.0595 | 2.1011 | 1.9602
12.7625 | 82.6716 | 83.2842 | 80.7282 | 2.0598 | 2.1014 | 1.9602
12.7667 | 82.6695 | 83.2171 | 80.69 | 2.0601 | 2.1016 | 1.9603
12.7708 | 82.6712 | 83.2674 | 80.727 | 2.0595 | 2.1015 | 1.9601
12.775 | 82.7407 | 83.3204 | 80.7613 | 2.0591 | 2.1013 | 1.9598
12.7792 | 82.773 | 83.306 | 80.738 | 2.0594 | 2.1022 | 1.9604
12.7833 | 82.7898 | 83.2924 | 80.7157 | 2.0598 | 2.1031 | 1.9609
12.7875 | 82.7286 | 83.2586 | 80.6864 | 2.0602 | 2.1028 | 1.9606
12.7917 | 82.7204 | 83.2231 | 80.6581 | 2.06 | 2.1025 | 1.9603
12.7958 | 82.6955 | 83.3148 | 80.7242 | 2.0593 | 2.1028 | 1.9604
12.8 | 82.7455 | 83.4082 | 80.7864 | 2.059 | 2.103 | 1.9605
12.8042 | 82.7882 | 83.3688 | 80.7574 | 2.0592 | 2.1033 | 1.9607
12.8083 | 82.7934 | 83.3276 | 80.7318 | 2.0598 | 2.1037 | 1.9609
12.8125 | 82.7044 | 83.288 | 80.7032 | 2.0601 | 2.1035 | 1.9607
12.8167 | 82.6209 | 83.2493 | 80.676 | 2.0602 | 2.1032 | 1.9606
12.8208 | 82.5933 | 83.2548 | 80.6731 | 2.0596 | 2.1039 | 1.961
12.825 | 82.5618 | 83.2626 | 80.6685 | 2.0595 | 2.1045 | 1.9613
12.8292 | 82.5708 | 83.259 | 80.6667 | 2.0598 | 2.1046 | 1.9613
12.8334 | 82.5994 | 83.2538 | 80.6646 | 2.0602 | 2.1048 | 1.9613
12.8375 | 82.5568 | 83.278 | 80.686 | 2.0604 | 2.1051 | 1.9615
12.8417 | 82.5309 | 83.3021 | 80.7069 | 2.0605 | 2.1055 | 1.9617
12.8458 | 82.5345 | 83.2619 | 80.6822 | 2.0608 | 2.106 | 1.9619
12.85 | 82.5387 | 83.2209 | 80.6582 | 2.0609 | 2.1065 | 1.962
12.8542 | 82.4913 | 83.1884 | 80.6449 | 2.0617 | 2.1069 | 1.9621
12.8583 | 82.4592 | 83.1561 | 80.6326 | 2.0624 | 2.1074 | 1.9622
12.8625 | 82.4059 | 83.0925 | 80.5926 | 2.0629 | 2.1087 | 1.9628
12.8667 | 82.3454 | 83.0315 | 80.5558 | 2.0635 | 2.1101 | 1.9634
12.8708 | 82.3524 | 82.995 | 80.528 | 2.0645 | 2.111 | 1.9637
12.875 | 82.344 | 82.9618 | 80.4975 | 2.0653 | 2.112 | 1.9639
12.8792 | 82.3342 | 83.0145 | 80.5227 | 2.0663 | 2.1134 | 1.9644
12.8833 | 82.3303 | 83.0689 | 80.5447 | 2.0672 | 2.1148 | 1.9649
12.8875 | 82.3615 | 83.0585 | 80.5189 | 2.0678 | 2.1162 | 1.9654
12.8917 | 82.372 | 83.0464 | 80.4949 | 2.0685 | 2.1175 | 1.9659
12.8959 | 82.3971 | 83.1162 | 80.5225 | 2.0692 | 2.1179 | 1.9659
12.9 | 82.4273 | 83.1867 | 80.5443 | 2.0698 | 2.1183 | 1.9659
12.9042 | 82.4344 | 83.2344 | 80.5605 | 2.07 | 2.1193 | 1.9663
12.9083 | 82.4519 | 83.2788 | 80.5791 | 2.0704 | 2.1203 | 1.9668
12.9125 | 82.4639 | 83.2334 | 80.5378 | 2.0707 | 2.1206 | 1.9668
12.9167 | 82.4636 | 83.1856 | 80.5007 | 2.071 | 2.1207 | 1.9668
12.9208 | 82.4426 | 83.2522 | 80.5382 | 2.0713 | 2.1208 | 1.9668
12.925 | 82.44 | 83.3211 | 80.5705 | 2.0715 | 2.1209 | 1.9667
12.9292 | 82.4463 | 83.2735 | 80.5402 | 2.0717 | 2.1219 | 1.9673
12.9333 | 82.4377 | 83.2217 | 80.5173 | 2.072 | 2.1229 | 1.9678
12.9375 | 82.4189 | 83.1837 | 80.4914 | 2.0726 | 2.1228 | 1.9676
12.9417 | 82.4 | 83.1485 | 80.4649 | 2.0729 | 2.1226 | 1.9675
12.9459 | 82.3865 | 83.2161 | 80.5053 | 2.0731 | 2.1234 | 1.9678
12.95 | 82.3936 | 83.2855 | 80.5402 | 2.0734 | 2.1242 | 1.9681
12.9542 | 82.4152 | 83.2135 | 80.4898 | 2.0739 | 2.125 | 1.9685
12.9584 | 82.413 | 83.1372 | 80.4463 | 2.0744 | 2.1257 | 1.9688
12.9625 | 82.3846 | 83.1899 | 80.4683 | 2.0748 | 2.1256 | 1.9686
12.9667 | 82.3789 | 83.2481 | 80.4831 | 2.0751 | 2.1253 | 1.9684
12.9708 | 82.3921 | 83.2746 | 80.4966 | 2.0752 | 2.1265 | 1.969
12.975 | 82.4003 | 83.2976 | 80.5118 | 2.0756 | 2.1276 | 1.9695
12.9792 | 82.4111 | 83.2067 | 80.458 | 2.0761 | 2.1278 | 1.9695
12.9833 | 82.3952 | 83.1144 | 80.4122 | 2.0765 | 2.1278 | 1.9695
12.9875 | 82.3706 | 83.1958 | 80.4543 | 2.0767 | 2.1281 | 1.9695
12.9917 | 82.3764 | 83.2842 | 80.4872 | 2.0769 | 2.1283 | 1.9696
12.9958 | 82.4043 | 83.2606 | 80.4652 | 2.0771 | 2.1294 | 1.9701
13 | 82.4103 | 83.2294 | 80.4469 | 2.0774 | 2.1304 | 1.9706
13.0042 | 82.389 | 83.2268 | 80.4319 | 2.078 | 2.13 | 1.9703
13.0084 | 82.3702 | 83.2268 | 80.4158 | 2.0782 | 2.1296 | 1.9702
13.0125 | 82.3559 | 83.3076 | 80.4542 | 2.0783 | 2.1302 | 1.9705
13.0167 | 82.3569 | 83.3906 | 80.4883 | 2.0786 | 2.1308 | 1.9707
13.0209 | 82.3769 | 83.2862 | 80.4358 | 2.0791 | 2.1313 | 1.971
13.025 | 82.3709 | 83.1736 | 80.3945 | 2.0795 | 2.1317 | 1.9713
13.0292 | 82.3333 | 83.2035 | 80.4099 | 2.0799 | 2.1314 | 1.9711
13.0333 | 82.3378 | 83.2417 | 80.4188 | 2.0801 | 2.131 | 1.9709
13.0375 | 82.3594 | 83.2666 | 80.4323 | 2.0802 | 2.1322 | 1.9715
13.0417 | 82.3734 | 83.2882 | 80.4441 | 2.0805 | 2.1334 | 1.9719
13.0458 | 82.3906 | 83.2038 | 80.3991 | 2.0811 | 2.1335 | 1.9719
13.05 | 82.3763 | 83.1162 | 80.361 | 2.0813 | 2.1335 | 1.9719
13.0542 | 82.3451 | 83.2028 | 80.4003 | 2.0815 | 2.1337 | 1.9719
13.0583 | 82.3469 | 83.2987 | 80.4307 | 2.0816 | 2.1339 | 1.9719
13.0625 | 82.3692 | 83.2647 | 80.4069 | 2.0818 | 2.135 | 1.9724
13.0667 | 82.3623 | 83.2225 | 80.388 | 2.0822 | 2.1361 | 1.9729
13.0709 | 82.346 | 83.209 | 80.3711 | 2.0826 | 2.1357 | 1.9727
13.075 | 82.3318 | 83.1993 | 80.3542 | 2.0828 | 2.1353 | 1.9725
13.0792 | 82.3217 | 83.2846 | 80.3908 | 2.0829 | 2.1359 | 1.9728
13.0834 | 82.336 | 83.3734 | 80.4216 | 2.0832 | 2.1366 | 1.9731
13.0875 | 82.3589 | 83.2811 | 80.3711 | 2.0836 | 2.1371 | 1.9734
13.0917 | 82.345 | 83.1787 | 80.3307 | 2.084 | 2.1375 | 1.9737
13.0958 | 82.319 | 83.2338 | 80.3514 | 2.0843 | 2.137 | 1.9735
13.1 | 82.3171 | 83.2971 | 80.3641 | 2.0844 | 2.1365 | 1.9733
13.1042 | 82.3314 | 83.3273 | 80.3728 | 2.0844 | 2.1375 | 1.9738
13.1083 | 82.3442 | 83.3545 | 80.3809 | 2.0848 | 2.1385 | 1.9743
13.1125 | 82.3464 | 83.2662 | 80.3352 | 2.0853 | 2.1383 | 1.9742
13.1167 | 82.3233 | 83.1732 | 80.2977 | 2.0856 | 2.138 | 1.9743
13.1209 | 82.2933 | 83.2626 | 80.3388 | 2.0857 | 2.138 | 1.9743
13.125 | 82.2832 | 83.3614 | 80.3696 | 2.086 | 2.138 | 1.9744
13.1292 | 82.3027 | 83.3131 | 80.3413 | 2.0863 | 2.1389 | 1.9749
13.1334 | 82.2883 | 83.2574 | 80.3196 | 2.0868 | 2.1398 | 1.9753
13.1375 | 82.2742 | 83.2279 | 80.3079 | 2.0873 | 2.1393 | 1.9751
13.1417 | 82.2647 | 83.2009 | 80.2968 | 2.0877 | 2.1388 | 1.9749
13.1459 | 82.252 | 83.2632 | 80.3266 | 2.0878 | 2.1395 | 1.9753
13.15 | 82.2556 | 83.3305 | 80.3509 | 2.0884 | 2.1404 | 1.9756
13.1542 | 82.2691 | 83.2339 | 80.3028 | 2.0888 | 2.1409 | 1.9758
13.1583 | 82.2607 | 83.1284 | 80.2645 | 2.0893 | 2.1414 | 1.976
13.1625 | 82.2409 | 83.1778 | 80.289 | 2.0897 | 2.1413 | 1.9759
13.1667 | 82.2645 | 83.2344 | 80.3053 | 2.0899 | 2.1411 | 1.9758
13.1708 | 82.2771 | 83.2401 | 80.3025 | 2.0901 | 2.1423 | 1.9763
13.175 | 82.2771 | 83.2442 | 80.3015 | 2.0905 | 2.1437 | 1.9768
13.1792 | 82.2908 | 83.173 | 80.2656 | 2.0909 | 2.1437 | 1.9767
13.1834 | 82.2842 | 83.0967 | 80.2354 | 2.091 | 2.1437 | 1.9767
13.1875 | 82.267 | 83.2005 | 80.2743 | 2.0912 | 2.144 | 1.9769
13.1917 | 82.2923 | 83.3135 | 80.3022 | 2.0914 | 2.1444 | 1.977
13.1959 | 82.3016 | 83.269 | 80.2695 | 2.0916 | 2.1454 | 1.9774
13.2 | 82.2724 | 83.2183 | 80.2445 | 2.0919 | 2.1464 | 1.9778
13.2042 | 82.2699 | 83.2118 | 80.2377 | 2.0922 | 2.1459 | 1.9776
13.2084 | 82.2642 | 83.2057 | 80.2294 | 2.0922 | 2.1454 | 1.9775
13.2125 | 82.2543 | 83.2953 | 80.254 | 2.0924 | 2.146 | 1.9779
13.2167 | 82.2632 | 83.3903 | 80.273 | 2.0928 | 2.1467 | 1.9782
13.2208 | 82.265 | 83.3238 | 80.2346 | 2.0931 | 2.1468 | 1.9784
13.225 | 82.2282 | 83.249 | 80.2048 | 2.0934 | 2.147 | 1.9786
13.2292 | 82.2113 | 83.294 | 80.2218 | 2.0938 | 2.1465 | 1.9785
13.2334 | 82.2285 | 83.3441 | 80.2318 | 2.094 | 2.1459 | 1.9785
13.2375 | 82.2213 | 83.3597 | 80.2231 | 2.0942 | 2.1465 | 1.979
13.2417 | 82.2133 | 83.3744 | 80.2172 | 2.0949 | 2.1471 | 1.9793
13.2459 | 82.2176 | 83.3222 | 80.1915 | 2.0953 | 2.1467 | 1.9793
13.25 | 82.1965 | 83.2644 | 80.1699 | 2.0954 | 2.1462 | 1.9793
13.2542 | 82.1955 | 83.3338 | 80.195 | 2.0958 | 2.1461 | 1.9795
13.2584 | 82.2305 | 83.4116 | 80.212 | 2.0961 | 2.146 | 1.9796
13.2625 | 82.2336 | 83.3655 | 80.183 | 2.0964 | 2.1463 | 1.9799
13.2667 | 82.2069 | 83.3148 | 80.1629 | 2.0969 | 2.1467 | 1.9802
13.2709 | 82.2014 | 83.3081 | 80.16 | 2.0972 | 2.1461 | 1.9801
13.275 | 82.1949 | 83.3006 | 80.1534 | 2.0973 | 2.1454 | 1.98
13.2792 | 82.1879 | 83.3467 | 80.1651 | 2.0976 | 2.1458 | 1.9804
13.2833 | 82.2064 | 83.3976 | 80.1724 | 2.0981 | 2.1462 | 1.9806
13.2875 | 82.2085 | 83.3188 | 80.1371 | 2.0984 | 2.1463 | 1.9807
13.2917 | 82.1739 | 83.2338 | 80.1121 | 2.0988 | 2.1463 | 1.9809
13.2959 | 82.1682 | 83.2728 | 80.1257 | 2.0991 | 2.146 | 1.9809
13.3 | 82.1895 | 83.3159 | 80.1296 | 2.0993 | 2.1456 | 1.981
13.3042 | 82.187 | 83.3173 | 80.122 | 2.0995 | 2.1463 | 1.9813
13.3084 | 82.1844 | 83.3176 | 80.1168 | 2.1001 | 2.1471 | 1.9816
13.3125 | 82.1901 | 83.2488 | 80.0907 | 2.1004 | 2.147 | 1.9816
13.3167 | 82.1656 | 83.1753 | 80.0714 | 2.1005 | 2.1469 | 1.9817
13.3209 | 82.1617 | 83.2342 | 80.0886 | 2.1008 | 2.1471 | 1.9819
13.325 | 82.1944 | 83.2995 | 80.0944 | 2.1011 | 2.1473 | 1.982
13.3292 | 82.1903 | 83.2575 | 80.072 | 2.1014 | 2.1481 | 1.9823
13.3334 | 82.1716 | 83.2104 | 80.0567 | 2.1018 | 2.149 | 1.9826
13.3375 | 82.167 | 83.1794 | 80.0455 | 2.1021 | 2.149 | 1.9826
13.3417 | 82.1666 | 83.1477 | 80.0348 | 2.1021 | 2.1489 | 1.9827
13.3458 | 82.1574 | 83.1983 | 80.0432 | 2.1024 | 2.1496 | 1.983
13.35 | 82.1717 | 83.2537 | 80.044 | 2.1028 | 2.1504 | 1.9832
13.3542 | 82.1683 | 83.1972 | 80.0176 | 2.1031 | 2.1511 | 1.9834
13.3584 | 82.1345 | 83.1352 | 79.9993 | 2.1034 | 2.1518 | 1.9836
13.3625 | 82.1291 | 83.1486 | 80.0009 | 2.1037 | 2.152 | 1.9837
13.3667 | 82.1452 | 83.1663 | 79.998 | 2.1039 | 2.1522 | 1.9838
13.3709 | 82.1376 | 83.1864 | 79.9922 | 2.1042 | 2.1532 | 1.9842
13.375 | 82.1291 | 83.208 | 79.9854 | 2.1048 | 2.1542 | 1.9844
13.3792 | 82.1274 | 83.1625 | 79.9637 | 2.1052 | 2.1547 | 1.9846
13.3834 | 82.1059 | 83.1132 | 79.9476 | 2.1054 | 2.1551 | 1.9847
13.3875 | 82.0997 | 83.1506 | 79.9534 | 2.1057 | 2.1556 | 1.9849
13.3917 | 82.1298 | 83.1932 | 79.9523 | 2.1061 | 2.1561 | 1.9851
13.3959 | 82.1171 | 83.1777 | 79.9337 | 2.1065 | 2.1571 | 1.9854
13.4 | 82.0954 | 83.1598 | 79.9188 | 2.107 | 2.158 | 1.9857
13.4042 | 82.0939 | 83.1455 | 79.9093 | 2.1073 | 2.1583 | 1.9858
13.4084 | 82.0928 | 83.1307 | 79.9002 | 2.1074 | 2.1586 | 1.9859
13.4125 | 82.1001 | 83.1726 | 79.9105 | 2.1078 | 2.1593 | 1.9861
13.4167 | 82.1228 | 83.2181 | 79.9167 | 2.1082 | 2.1601 | 1.9863
13.4209 | 82.0885 | 83.1542 | 79.8695 | 2.1089 | 2.161 | 1.9867
13.425 | 82.0276 | 83.0852 | 79.8286 | 2.1094 | 2.162 | 1.9872
13.4292 | 82.0281 | 83.1082 | 79.831 | 2.1096 | 2.1621 | 1.9871
13.4334 | 82.0464 | 83.1334 | 79.8271 | 2.1097 | 2.1623 | 1.9871
13.4375 | 82.0975 | 83.198 | 79.8619 | 2.1101 | 2.1632 | 1.9874
13.4417 | 82.1456 | 83.264 | 79.896 | 2.1107 | 2.1642 | 1.9877
13.4459 | 82.1274 | 83.2086 | 79.8591 | 2.111 | 2.1646 | 1.9878
13.45 | 82.0803 | 83.1494 | 79.8315 | 2.1113 | 2.1651 | 1.988
13.4542 | 82.006 | 83.1236 | 79.7889 | 2.1118 | 2.1657 | 1.9884
13.4584 | 81.9636 | 83.1012 | 79.7391 | 2.1123 | 2.1663 | 1.9887
13.4625 | 81.9313 | 83.1079 | 79.7258 | 2.113 | 2.1671 | 1.9891
13.4667 | 81.9091 | 83.1145 | 79.7084 | 2.1137 | 2.168 | 1.9894
13.4709 | 82.0089 | 83.2404 | 79.7831 | 2.1139 | 2.1677 | 1.9891
13.475 | 82.097 | 83.3675 | 79.8574 | 2.1139 | 2.1675 | 1.989
13.4792 | 82.1856 | 83.4245 | 79.8697 | 2.1141 | 2.1678 | 1.9892
13.4834 | 82.2451 | 83.4832 | 79.8868 | 2.1144 | 2.1681 | 1.9895
13.4875 | 82.2776 | 83.385 | 79.8254 | 2.1147 | 2.1676 | 1.9893
13.4917 | 82.2501 | 83.2816 | 79.775 | 2.1147 | 2.1672 | 1.9891
13.4959 | 82.1272 | 83.3004 | 79.7696 | 2.1157 | 2.1669 | 1.9893
13.5 | 82.0763 | 83.3218 | 79.7552 | 2.1159 | 2.1666 | 1.9896
13.5042 | 81.9805 | 83.4175 | 79.7669 | 2.1156 | 2.1661 | 1.9897
13.5084 | 82.0061 | 83.5169 | 79.7703 | 2.1151 | 2.1657 | 1.9897
13.5125 | 82.1569 | 83.6824 | 79.8484 | 2.1152 | 2.1639 | 1.9892
13.5167 | 82.326 | 83.8466 | 79.926 | 2.1146 | 2.1621 | 1.9888
13.5209 | 82.4608 | 83.9849 | 79.9761 | 2.1146 | 2.1597 | 1.9885
13.525 | 82.5614 | 84.1249 | 80.0304 | 2.114 | 2.1574 | 1.9882
13.5292 | 82.7083 | 84.1004 | 80.0436 | 2.1125 | 2.1545 | 1.9874
13.5334 | 82.7957 | 84.0727 | 80.0777 | 2.1107 | 2.1515 | 1.9865
13.5375 | 82.8255 | 83.9146 | 80.0663 | 2.1095 | 2.1494 | 1.9863
13.5417 | 82.8331 | 83.7508 | 80.0685 | 2.1083 | 2.1473 | 1.9861
13.5459 | 82.7515 | 83.515 | 80.0028 | 2.1065 | 2.1465 | 1.986
13.55 | 82.6411 | 83.2777 | 79.9405 | 2.1052 | 2.1457 | 1.9857
13.5542 | 82.6166 | 83.0917 | 79.9234 | 2.1042 | 2.1464 | 1.9859
13.5584 | 82.5893 | 82.9042 | 79.9018 | 2.1033 | 2.1472 | 1.9858
13.5625 | 82.4712 | 82.815 | 79.8786 | 2.1033 | 2.1491 | 1.9864
13.5667 | 82.3988 | 82.7284 | 79.8369 | 2.1036 | 2.151 | 1.9869
13.5709 | 82.3137 | 82.7668 | 79.8392 | 2.1033 | 2.1528 | 1.987
13.575 | 82.2052 | 82.8102 | 79.8275 | 2.1033 | 2.1547 | 1.9869
13.5792 | 82.1289 | 82.9167 | 79.8562 | 2.1036 | 2.1564 | 1.9873
13.5834 | 82.1085 | 83.0255 | 79.877 | 2.1042 | 2.1581 | 1.9876
13.5875 | 82.0364 | 83.1404 | 79.8752 | 2.1042 | 2.1587 | 1.9876
13.5917 | 82.0423 | 83.2582 | 79.8695 | 2.1049 | 2.1593 | 1.9876
13.5959 | 82.0935 | 83.3526 | 79.8905 | 2.1053 | 2.1594 | 1.9875
13.6 | 82.1341 | 83.4463 | 79.9184 | 2.1057 | 2.1594 | 1.9874
13.6042 | 82.1142 | 83.453 | 79.9054 | 2.1063 | 2.159 | 1.9875
13.6084 | 82.1191 | 83.4561 | 79.8992 | 2.1069 | 2.1586 | 1.9877
13.6125 | 82.1285 | 83.4657 | 79.9035 | 2.1068 | 2.1578 | 1.9874
13.6167 | 82.1407 | 83.4737 | 79.9106 | 2.1067 | 2.157 | 1.9871
13.6209 | 82.1901 | 83.4232 | 79.9086 | 2.107 | 2.157 | 1.9873
13.625 | 82.2035 | 83.3699 | 79.9135 | 2.1074 | 2.157 | 1.9875
13.6292 | 82.2002 | 83.3042 | 79.8816 | 2.1075 | 2.1567 | 1.9875
13.6334 | 82.1424 | 83.2392 | 79.849 | 2.1077 | 2.1564 | 1.9874
13.6375 | 82.1639 | 83.2642 | 79.8801 | 2.1075 | 2.1565 | 1.9874
13.6417 | 82.1898 | 83.2903 | 79.9057 | 2.1075 | 2.1568 | 1.9873
13.6459 | 82.2045 | 83.2558 | 79.8984 | 2.1078 | 2.1573 | 1.9875
13.65 | 82.1989 | 83.2196 | 79.8944 | 2.1081 | 2.1578 | 1.9877
13.6542 | 82.2095 | 83.2278 | 79.8858 | 2.108 | 2.1577 | 1.9875
13.6584 | 82.1819 | 83.2395 | 79.8739 | 2.1079 | 2.1576 | 1.9873
13.6625 | 82.221 | 83.2426 | 79.8683 | 2.1078 | 2.1583 | 1.9877
13.6667 | 82.2243 | 83.2458 | 79.8623 | 2.1079 | 2.1591 | 1.9879
13.6709 | 82.243 | 83.2366 | 79.8517 | 2.1082 | 2.159 | 1.9878
13.675 | 82.2145 | 83.2259 | 79.8417 | 2.1083 | 2.1589 | 1.9878
13.6792 | 82.2381 | 83.3157 | 79.8934 | 2.108 | 2.1589 | 1.9876
13.6834 | 82.2796 | 83.4075 | 79.9389 | 2.1075 | 2.1589 | 1.9875
13.6875 | 82.3482 | 83.3362 | 79.8972 | 2.1075 | 2.1595 | 1.9878
13.6917 | 82.3902 | 83.2621 | 79.8661 | 2.1079 | 2.1601 | 1.9882
13.6959 | 82.3585 | 83.2283 | 79.8438 | 2.1082 | 2.1596 | 1.9879
13.7 | 82.2997 | 83.1963 | 79.8201 | 2.1086 | 2.1591 | 1.9876
13.7042 | 82.2737 | 83.2486 | 79.8507 | 2.1082 | 2.1598 | 1.988
13.7084 | 82.2486 | 83.3033 | 79.8748 | 2.1076 | 2.1606 | 1.9882
13.7125 | 82.252 | 83.2257 | 79.8303 | 2.1078 | 2.161 | 1.9884
13.7167 | 82.2669 | 83.1446 | 79.7946 | 2.1081 | 2.1614 | 1.9886
13.7209 | 82.2192 | 83.2 | 79.8301 | 2.1083 | 2.1613 | 1.9883
13.725 | 82.171 | 83.2579 | 79.8553 | 2.1085 | 2.1611 | 1.9881
13.7292 | 82.1375 | 83.2466 | 79.8522 | 2.1084 | 2.1622 | 1.9886
13.7334 | 82.1579 | 83.2334 | 79.853 | 2.1084 | 2.1634 | 1.989
13.7375 | 82.0925 | 83.1244 | 79.7983 | 2.1088 | 2.1637 | 1.9889
13.7417 | 82.0562 | 83.0138 | 79.7533 | 2.1096 | 2.1639 | 1.9888
13.7459 | 82.0153 | 83.05 | 79.7776 | 2.1101 | 2.1649 | 1.989
13.75 | 81.9513 | 83.0925 | 79.79 | 2.1103 | 2.1658 | 1.9892
13.7542 | 81.9576 | 83.0333 | 79.7519 | 2.1111 | 2.1675 | 1.9897
13.7584 | 81.9878 | 82.9727 | 79.7203 | 2.1118 | 2.1691 | 1.9901
13.7625 | 81.9788 | 82.977 | 79.7132 | 2.1127 | 2.1697 | 1.9901
13.7667 | 81.941 | 82.9834 | 79.7017 | 2.1136 | 2.1702 | 1.9901
13.7709 | 81.9749 | 83.0766 | 79.733 | 2.114 | 2.1716 | 1.9904
13.775 | 81.9955 | 83.1718 | 79.7534 | 2.1142 | 2.1729 | 1.9907
13.7792 | 82.0319 | 83.153 | 79.7254 | 2.1147 | 2.1736 | 1.9908
13.7834 | 82.0829 | 83.1287 | 79.707 | 2.1154 | 2.1743 | 1.991
13.7875 | 82.0684 | 83.1908 | 79.7264 | 2.1156 | 2.1744 | 1.9909
13.7917 | 82.0383 | 83.2543 | 79.7405 | 2.1158 | 2.1744 | 1.9908
13.7959 | 82.0654 | 83.274 | 79.7389 | 2.1158 | 2.1751 | 1.9911
13.8 | 82.1014 | 83.2914 | 79.739 | 2.1158 | 2.1758 | 1.9913
13.8042 | 82.0903 | 83.2518 | 79.7182 | 2.1161 | 2.1757 | 1.9912
13.8084 | 82.0795 | 83.2094 | 79.7058 | 2.1166 | 2.1755 | 1.9911
13.8125 | 82.0543 | 83.2326 | 79.7178 | 2.1166 | 2.1759 | 1.9913
13.8167 | 82.0157 | 83.2588 | 79.7251 | 2.1166 | 2.1762 | 1.9914
13.8209 | 82.0318 | 83.2127 | 79.7018 | 2.1169 | 2.1768 | 1.9916
13.825 | 82.054 | 83.1647 | 79.6835 | 2.1172 | 2.1774 | 1.9917
13.8292 | 82.0319 | 83.1636 | 79.6864 | 2.1176 | 2.1776 | 1.9917
13.8334 | 82.0058 | 83.164 | 79.6879 | 2.118 | 2.1777 | 1.9916
13.8375 | 82.0111 | 83.1864 | 79.6881 | 2.1181 | 2.1785 | 1.9919
13.8417 | 82.0121 | 83.2105 | 79.6836 | 2.1182 | 2.1792 | 1.9922
13.8459 | 82.0189 | 83.2035 | 79.6753 | 2.1186 | 2.1795 | 1.9921
13.85 | 82.0361 | 83.1939 | 79.6686 | 2.1191 | 2.1797 | 1.9921
13.8542 | 82.0201 | 83.2156 | 79.6786 | 2.1192 | 2.1801 | 1.9922
13.8584 | 81.9943 | 83.2387 | 79.6879 | 2.1195 | 2.1805 | 1.9923
13.8625 | 82.0138 | 83.2061 | 79.6651 | 2.1197 | 2.181 | 1.9925
13.8667 | 82.0241 | 83.1737 | 79.6462 | 2.1198 | 2.1815 | 1.9926
13.8709 | 82.0149 | 83.1861 | 79.6539 | 2.1202 | 2.1817 | 1.9926
13.875 | 82.0218 | 83.1982 | 79.6588 | 2.1205 | 2.1818 | 1.9925
13.8792 | 82.0183 | 83.2229 | 79.6588 | 2.1206 | 2.1823 | 1.9928
13.8834 | 82.0062 | 83.2479 | 79.6572 | 2.1207 | 2.1829 | 1.993
13.8875 | 82.0146 | 83.2415 | 79.6437 | 2.121 | 2.183 | 1.9929
13.8917 | 82.0185 | 83.234 | 79.6316 | 2.1213 | 2.1831 | 1.9929
13.8959 | 81.998 | 83.2598 | 79.6466 | 2.1215 | 2.1832 | 1.993
13.9 | 81.9856 | 83.2855 | 79.6599 | 2.1218 | 2.1834 | 1.9931
13.9042 | 81.9881 | 83.2459 | 79.6372 | 2.122 | 2.1839 | 1.9933
13.9084 | 81.9859 | 83.2055 | 79.6204 | 2.1222 | 2.1843 | 1.9934
13.9125 | 81.9794 | 83.2062 | 79.6223 | 2.1226 | 2.1843 | 1.9933
13.9167 | 81.9899 | 83.2081 | 79.6202 | 2.1228 | 2.1842 | 1.9933
13.9209 | 81.9949 | 83.2225 | 79.6297 | 2.1229 | 2.1849 | 1.9935
13.925 | 81.9926 | 83.2364 | 79.6383 | 2.1231 | 2.1855 | 1.9937
13.9292 | 82.0063 | 83.1876 | 79.6115 | 2.1234 | 2.1859 | 1.9937
13.9334 | 82.007 | 83.1385 | 79.5908 | 2.1235 | 2.1862 | 1.9938
13.9375 | 81.9885 | 83.1825 | 79.6083 | 2.1237 | 2.1864 | 1.9938
13.9417 | 81.9828 | 83.2291 | 79.6175 | 2.1239 | 2.1865 | 1.9937
13.9459 | 81.9948 | 83.2294 | 79.6104 | 2.124 | 2.1873 | 1.994
13.95 | 81.9854 | 83.2276 | 79.6066 | 2.1242 | 2.188 | 1.9942
13.9542 | 81.9812 | 83.2124 | 79.5899 | 2.1246 | 2.1879 | 1.9941
13.9584 | 81.9808 | 83.199 | 79.5753 | 2.1248 | 2.1878 | 1.9941
13.9625 | 81.969 | 83.2492 | 79.5958 | 2.1249 | 2.1881 | 1.9942
13.9667 | 81.9628 | 83.2994 | 79.6103 | 2.1251 | 2.1885 | 1.9943
13.9709 | 81.9833 | 83.2547 | 79.5843 | 2.1253 | 2.1889 | 1.9945
13.975 | 81.9729 | 83.206 | 79.5667 | 2.1256 | 2.1893 | 1.9947
13.9792 | 81.9574 | 83.2339 | 79.5721 | 2.1259 | 2.1889 | 1.9946
13.9834 | 81.966 | 83.2661 | 79.5711 | 2.1261 | 2.1886 | 1.9945
13.9875 | 81.9716 | 83.2853 | 79.5809 | 2.1261 | 2.1892 | 1.9947
13.9917 | 81.9732 | 83.3014 | 79.5898 | 2.1263 | 2.1899 | 1.9949
13.9959 | 81.9761 | 83.2368 | 79.5568 | 2.1267 | 2.1899 | 1.995
14 | 81.9554 | 83.1713 | 79.5326 | 2.1269 | 2.1898 | 1.9951
14.0042 | 81.9293 | 83.236 | 79.5577 | 2.1271 | 2.1897 | 1.995
14.0084 | 81.9289 | 83.3059 | 79.5708 | 2.1273 | 2.1897 | 1.9949
14.0125 | 81.9478 | 83.273 | 79.5582 | 2.1275 | 2.1904 | 1.9953
14.0167 | 81.9401 | 83.2347 | 79.5527 | 2.1279 | 2.1912 | 1.9955
14.0209 | 81.9282 | 83.1952 | 79.5339 | 2.1283 | 2.1909 | 1.9954
14.025 | 81.9095 | 83.1593 | 79.518 | 2.1287 | 2.1906 | 1.9953
14.0292 | 81.8987 | 83.2195 | 79.5449 | 2.1287 | 2.1912 | 1.9955
14.0334 | 81.9106 | 83.2812 | 79.5619 | 2.1291 | 2.1917 | 1.9956
14.0375 | 81.9237 | 83.2085 | 79.5294 | 2.1294 | 2.1924 | 1.9958
14.0417 | 81.9278 | 83.1301 | 79.5091 | 2.1298 | 2.193 | 1.996
14.0459 | 81.9046 | 83.1534 | 79.5172 | 2.1301 | 2.1928 | 1.9958
14.05 | 81.9072 | 83.1829 | 79.518 | 2.1303 | 2.1927 | 1.9957
14.0542 | 81.9251 | 83.2028 | 79.5249 | 2.1303 | 2.1937 | 1.9961
14.0584 | 81.941 | 83.2188 | 79.5304 | 2.1306 | 2.1948 | 1.9963
14.0625 | 81.9443 | 83.1637 | 79.4994 | 2.1309 | 2.1949 | 1.9963
14.0667 | 81.9457 | 83.1072 | 79.4776 | 2.1311 | 2.195 | 1.9963
14.0709 | 81.9212 | 83.1921 | 79.5063 | 2.1311 | 2.1952 | 1.9963
14.075 | 81.9244 | 83.2837 | 79.5211 | 2.1312 | 2.1954 | 1.9963
14.0792 | 81.9464 | 83.245 | 79.498 | 2.1313 | 2.1963 | 1.9966
14.0834 | 81.9403 | 83.1992 | 79.4846 | 2.1316 | 2.1972 | 1.9969
14.0875 | 81.9254 | 83.1996 | 79.4747 | 2.1319 | 2.1967 | 1.9967
14.0917 | 81.9126 | 83.2035 | 79.4647 | 2.132 | 2.1961 | 1.9966
14.0959 | 81.9037 | 83.292 | 79.4935 | 2.132 | 2.1965 | 1.9968
14.1 | 81.9024 | 83.383 | 79.5115 | 2.1322 | 2.1971 | 1.997
14.1042 | 81.9164 | 83.3018 | 79.4755 | 2.1325 | 2.1972 | 1.9971
14.1084 | 81.9032 | 83.2134 | 79.4542 | 2.1328 | 2.1973 | 1.9973
14.1125 | 81.8728 | 83.2642 | 79.4694 | 2.1331 | 2.1967 | 1.9971
14.1167 | 81.8686 | 83.3212 | 79.4747 | 2.1333 | 2.196 | 1.997
14.1209 | 81.8736 | 83.3443 | 79.4783 | 2.1335 | 2.1966 | 1.9973
14.125 | 81.8724 | 83.3636 | 79.4822 | 2.1339 | 2.1973 | 1.9975
14.1292 | 81.8806 | 83.2887 | 79.4538 | 2.1343 | 2.1968 | 1.9975
14.1334 | 81.8779 | 83.2111 | 79.4353 | 2.1345 | 2.1963 | 1.9975
14.1375 | 81.8615 | 83.2911 | 79.4629 | 2.1347 | 2.1961 | 1.9975
14.1417 | 81.8737 | 83.3794 | 79.4773 | 2.1349 | 2.1959 | 1.9975
14.1459 | 81.8896 | 83.3352 | 79.4568 | 2.1351 | 2.1964 | 1.9977
14.15 | 81.8781 | 83.2834 | 79.4466 | 2.1355 | 2.1969 | 1.9979
14.1542 | 81.8669 | 83.2623 | 79.4415 | 2.1358 | 2.1962 | 1.9978
14.1584 | 81.8666 | 83.2432 | 79.4348 | 2.136 | 2.1954 | 1.9977
14.1625 | 81.8558 | 83.2985 | 79.452 | 2.136 | 2.1959 | 1.9979
14.1667 | 81.8648 | 83.3579 | 79.4622 | 2.1364 | 2.1963 | 1.998
14.1709 | 81.8743 | 83.2771 | 79.4322 | 2.1367 | 2.1965 | 1.9981
14.175 | 81.8585 | 83.1885 | 79.4147 | 2.1369 | 2.1966 | 1.9982
14.1792 | 81.8398 | 83.2291 | 79.4311 | 2.1372 | 2.1962 | 1.9981
14.1834 | 81.852 | 83.2753 | 79.4358 | 2.1373 | 2.1958 | 1.9981
14.1875 | 81.858 | 83.2702 | 79.4308 | 2.1375 | 2.1967 | 1.9984
14.1917 | 81.8534 | 83.2629 | 79.4306 | 2.1379 | 2.1976 | 1.9985
14.1959 | 81.8617 | 83.1995 | 79.4104 | 2.1382 | 2.1974 | 1.9985
14.2 | 81.8469 | 83.1321 | 79.3959 | 2.1383 | 2.1971 | 1.9985
14.2042 | 81.8339 | 83.2027 | 79.4192 | 2.1385 | 2.1974 | 1.9986
14.2084 | 81.8576 | 83.2799 | 79.4282 | 2.1387 | 2.1978 | 1.9986
14.2125 | 81.8658 | 83.2141 | 79.4046 | 2.1388 | 2.1986 | 1.9988
14.2167 | 81.85 | 83.1416 | 79.3948 | 2.1392 | 2.1995 | 1.999
14.2209 | 81.8422 | 83.1335 | 79.3931 | 2.1394 | 2.1993 | 1.9989
14.225 | 81.839 | 83.1271 | 79.3863 | 2.1395 | 2.1991 | 1.9988
14.2292 | 81.8294 | 83.1838 | 79.3999 | 2.1396 | 2.2 | 1.9991
14.2334 | 81.8421 | 83.2445 | 79.4057 | 2.1399 | 2.201 | 1.9992
14.2375 | 81.847 | 83.1575 | 79.3777 | 2.1402 | 2.2016 | 1.9993
14.2417 | 81.8199 | 83.0638 | 79.3644 | 2.1404 | 2.2021 | 1.9994
14.2459 | 81.8043 | 83.1144 | 79.3774 | 2.1407 | 2.2022 | 1.9993
14.25 | 81.8136 | 83.1721 | 79.3775 | 2.1409 | 2.2022 | 1.9994
14.2542 | 81.8173 | 83.1823 | 79.3749 | 2.141 | 2.2034 | 1.9996
14.2584 | 81.8103 | 83.1916 | 79.3756 | 2.1415 | 2.2046 | 1.9998
14.2625 | 81.8177 | 83.1276 | 79.358 | 2.1418 | 2.2048 | 1.9997
14.2667 | 81.8026 | 83.0596 | 79.3489 | 2.1419 | 2.2049 | 1.9998
14.2709 | 81.7723 | 83.1226 | 79.3535 | 2.1423 | 2.2054 | 1.9999
14.275 | 81.7842 | 83.1929 | 79.3441 | 2.1427 | 2.206 | 2.0001
14.2792 | 81.7984 | 83.1662 | 79.3391 | 2.1428 | 2.2069 | 2.0002
14.2834 | 81.7946 | 83.1345 | 79.3438 | 2.1431 | 2.2078 | 2.0002
14.2875 | 81.8094 | 83.1333 | 79.352 | 2.1435 | 2.2078 | 2.0002
14.2917 | 81.8241 | 83.1334 | 79.3594 | 2.1436 | 2.2078 | 2.0003
14.2959 | 81.7852 | 83.1575 | 79.3437 | 2.1438 | 2.2087 | 2.0005
14.3 | 81.7618 | 83.1852 | 79.3236 | 2.1443 | 2.2097 | 2.0006
14.3042 | 81.7408 | 83.1005 | 79.2882 | 2.1447 | 2.2104 | 2.0008
14.3084 | 81.6935 | 83.0087 | 79.2611 | 2.1451 | 2.2112 | 2.001
14.3125 | 81.7256 | 83.0956 | 79.2999 | 2.1453 | 2.2111 | 2.0009
14.3167 | 81.784 | 83.1882 | 79.323 | 2.1454 | 2.2111 | 2.0008
14.3209 | 81.8385 | 83.2489 | 79.3536 | 2.1455 | 2.212 | 2.0009
14.325 | 81.8706 | 83.309 | 79.3917 | 2.1459 | 2.213 | 2.001
14.3292 | 81.8466 | 83.172 | 79.3213 | 2.1465 | 2.2134 | 2.0011
14.3334 | 81.783 | 83.0297 | 79.2669 | 2.1469 | 2.2137 | 2.0014
14.3375 | 81.6794 | 83.0597 | 79.2584 | 2.1471 | 2.2139 | 2.0014
14.3417 | 81.6732 | 83.0964 | 79.2306 | 2.1475 | 2.2141 | 2.0013
14.3459 | 81.6231 | 83.1551 | 79.256 | 2.148 | 2.2151 | 2.0017
14.35 | 81.6178 | 83.2119 | 79.2765 | 2.1488 | 2.2162 | 2.002
14.3542 | 81.6736 | 83.2813 | 79.3007 | 2.1493 | 2.2155 | 2.0017
14.3584 | 81.749 | 83.3518 | 79.3259 | 2.1491 | 2.2148 | 2.0015
14.3625 | 81.8272 | 83.4256 | 79.3463 | 2.1492 | 2.2148 | 2.0015
14.3667 | 81.9102 | 83.5017 | 79.3702 | 2.1494 | 2.2147 | 2.0016
14.3709 | 81.9709 | 83.3963 | 79.3162 | 2.1494 | 2.2144 | 2.0016
14.375 | 81.9568 | 83.2847 | 79.2795 | 2.1498 | 2.214 | 2.0017
14.3792 | 81.8857 | 83.3286 | 79.2888 | 2.1504 | 2.213 | 2.0015
14.3834 | 81.8532 | 83.3779 | 79.286 | 2.1502 | 2.2119 | 2.0013
14.3875 | 81.7443 | 83.4677 | 79.2965 | 2.1501 | 2.2117 | 2.0017
14.3917 | 81.7429 | 83.5582 | 79.2938 | 2.1501 | 2.2116 | 2.002
14.3959 | 81.8171 | 83.6399 | 79.31 | 2.1495 | 2.2095 | 2.0015
14.4 | 81.9105 | 83.7192 | 79.3249 | 2.1493 | 2.2074 | 2.0013
14.4042 | 82.0292 | 83.8746 | 79.3786 | 2.1495 | 2.2052 | 2.0011
14.4084 | 82.1548 | 84.0355 | 79.4296 | 2.1491 | 2.203 | 2.001
14.4125 | 82.2352 | 83.955 | 79.4071 | 2.1483 | 2.201 | 2.0008
14.4167 | 82.3138 | 83.8678 | 79.4103 | 2.1475 | 2.199 | 2.0006
14.4209 | 82.3653 | 83.7124 | 79.4035 | 2.1464 | 2.1969 | 2.0002
14.425 | 82.3481 | 83.5528 | 79.4178 | 2.1453 | 2.1947 | 1.9998
14.4292 | 82.3131 | 83.3736 | 79.3921 | 2.1443 | 2.1948 | 2.0001
14.4334 | 82.2759 | 83.1954 | 79.3726 | 2.1433 | 2.195 | 2.0002
14.4375 | 82.2636 | 82.9778 | 79.3426 | 2.1421 | 2.1959 | 2.0002
14.4417 | 82.2495 | 82.7553 | 79.3157 | 2.1414 | 2.1969 | 2
14.4459 | 82.2331 | 82.7232 | 79.3282 | 2.1409 | 2.1987 | 2.0003
14.45 | 82.1454 | 82.696 | 79.3201 | 2.1411 | 2.2006 | 2.0005
14.4542 | 82.064 | 82.7382 | 79.3128 | 2.1407 | 2.2029 | 2.0007
14.4584 | 81.9556 | 82.7845 | 79.2869 | 2.1407 | 2.2052 | 2.0008
14.4625 | 81.9124 | 82.8947 | 79.3165 | 2.1407 | 2.2064 | 2.0007
14.4667 | 81.8516 | 83.0052 | 79.3349 | 2.1405 | 2.2075 | 2.0007
14.4709 | 81.8305 | 83.1504 | 79.3365 | 2.1409 | 2.2083 | 2.0009
14.475 | 81.7768 | 83.3011 | 79.3298 | 2.1411 | 2.209 | 2.0012
14.4792 | 81.7753 | 83.3667 | 79.3255 | 2.1414 | 2.2088 | 2.0009
14.4834 | 81.7782 | 83.4298 | 79.3277 | 2.1417 | 2.2085 | 2.0008
14.4875 | 81.774 | 83.4723 | 79.3487 | 2.1421 | 2.2077 | 2.0008
14.4917 | 81.7989 | 83.5109 | 79.3757 | 2.1425 | 2.2069 | 2.0009
14.4959 | 81.8015 | 83.4848 | 79.3518 | 2.1427 | 2.2063 | 2.0008
14.5 | 81.8112 | 83.4587 | 79.3365 | 2.1428 | 2.2057 | 2.0008
14.5042 | 81.8465 | 83.3856 | 79.3335 | 2.143 | 2.2052 | 2.0007
14.5084 | 81.8547 | 83.309 | 79.3393 | 2.1431 | 2.2047 | 2.0006
14.5125 | 81.8408 | 83.2666 | 79.3302 | 2.1434 | 2.2047 | 2.0008
14.5167 | 81.8343 | 83.2248 | 79.3181 | 2.1435 | 2.2047 | 2.001
14.5209 | 81.8264 | 83.2227 | 79.331 | 2.1434 | 2.2048 | 2.0008
14.525 | 81.8426 | 83.2214 | 79.3409 | 2.1432 | 2.2049 | 2.0006
14.5292 | 81.8665 | 83.2069 | 79.355 | 2.1434 | 2.2054 | 2.0007
14.5334 | 81.8984 | 83.1915 | 79.3713 | 2.1435 | 2.2058 | 2.0009
14.5375 | 81.8687 | 83.164 | 79.3289 | 2.1438 | 2.2062 | 2.0009
14.5417 | 81.8616 | 83.1398 | 79.2856 | 2.144 | 2.2065 | 2.001
14.5459 | 81.8268 | 83.1752 | 79.3072 | 2.1438 | 2.2068 | 2.0009
14.55 | 81.8198 | 83.2106 | 79.323 | 2.1439 | 2.2071 | 2.0007
14.5542 | 81.818 | 83.2421 | 79.3363 | 2.144 | 2.2074 | 2.001
14.5584 | 81.8202 | 83.2725 | 79.3477 | 2.1442 | 2.2077 | 2.0012
14.5625 | 81.8183 | 83.2795 | 79.3345 | 2.1443 | 2.2076 | 2.001
14.5667 | 81.8405 | 83.2875 | 79.3237 | 2.1442 | 2.2075 | 2.0008
14.5709 | 81.8667 | 83.2724 | 79.3339 | 2.1441 | 2.2077 | 2.0009
14.575 | 81.912 | 83.2556 | 79.3481 | 2.144 | 2.2078 | 2.0009
14.5792 | 81.9319 | 83.2253 | 79.3245 | 2.1442 | 2.2079 | 2.0011
14.5834 | 81.9439 | 83.196 | 79.3023 | 2.1446 | 2.208 | 2.0012
14.5875 | 81.9337 | 83.1934 | 79.304 | 2.1446 | 2.2084 | 2.0011
14.5917 | 81.9051 | 83.1923 | 79.3044 | 2.1445 | 2.2087 | 2.001
14.5959 | 81.9419 | 83.1745 | 79.308 | 2.1442 | 2.2092 | 2.0012
14.6 | 81.9387 | 83.1554 | 79.311 | 2.144 | 2.2097 | 2.0014
14.6042 | 81.9688 | 83.1726 | 79.3105 | 2.1444 | 2.2098 | 2.0013
14.6084 | 81.9607 | 83.1905 | 79.3057 | 2.1446 | 2.21 | 2.0012
14.6125 | 81.9081 | 83.1687 | 79.3095 | 2.1449 | 2.2108 | 2.0014
14.6167 | 81.8792 | 83.1456 | 79.3193 | 2.1449 | 2.2117 | 2.0014
14.6209 | 81.8212 | 83.085 | 79.2971 | 2.1447 | 2.2122 | 2.0015
14.625 | 81.7919 | 83.0245 | 79.2789 | 2.1449 | 2.2127 | 2.0016
14.6292 | 81.7537 | 83.0378 | 79.2853 | 2.1453 | 2.2136 | 2.0016
14.6334 | 81.7125 | 83.0546 | 79.2859 | 2.1457 | 2.2144 | 2.0016
14.6375 | 81.6746 | 83.0089 | 79.2711 | 2.1462 | 2.2158 | 2.0019
14.6417 | 81.668 | 82.9628 | 79.2625 | 2.1467 | 2.2172 | 2.0021
14.6459 | 81.681 | 82.9846 | 79.2584 | 2.1472 | 2.2178 | 2.002
14.65 | 81.6714 | 83.0083 | 79.2447 | 2.1478 | 2.2183 | 2.002
14.6542 | 81.6971 | 83.0882 | 79.2688 | 2.1484 | 2.2194 | 2.0022
14.6584 | 81.7163 | 83.1685 | 79.2852 | 2.1487 | 2.2205 | 2.0022
14.6625 | 81.7273 | 83.1433 | 79.2613 | 2.1489 | 2.2211 | 2.0024
14.6667 | 81.7607 | 83.1138 | 79.2471 | 2.1493 | 2.2216 | 2.0025
14.6709 | 81.7783 | 83.1873 | 79.2639 | 2.1494 | 2.2214 | 2.0023
14.675 | 81.7687 | 83.2621 | 79.2694 | 2.1496 | 2.2213 | 2.0022
14.6792 | 81.7746 | 83.277 | 79.2744 | 2.1497 | 2.2219 | 2.0024
14.6834 | 81.8047 | 83.2891 | 79.2863 | 2.1496 | 2.2226 | 2.0026
14.6875 | 81.7899 | 83.2269 | 79.2565 | 2.1497 | 2.2223 | 2.0025
14.6917 | 81.7859 | 83.1625 | 79.237 | 2.1501 | 2.2221 | 2.0025
14.6959 | 81.7641 | 83.2144 | 79.2639 | 2.1501 | 2.2222 | 2.0025
14.7 | 81.7417 | 83.2697 | 79.2799 | 2.1501 | 2.2223 | 2.0024
14.7042 | 81.7346 | 83.1974 | 79.2563 | 2.1502 | 2.2232 | 2.0027
14.7084 | 81.7601 | 83.1228 | 79.247 | 2.1504 | 2.224 | 2.0029
14.7125 | 81.7457 | 83.109 | 79.2389 | 2.1507 | 2.2238 | 2.0027
14.7167 | 81.7172 | 83.0978 | 79.2261 | 2.1511 | 2.2236 | 2.0026
14.7209 | 81.7163 | 83.1716 | 79.2553 | 2.1513 | 2.2244 | 2.0028
14.725 | 81.7228 | 83.2468 | 79.2723 | 2.1512 | 2.2252 | 2.0028
14.7292 | 81.7332 | 83.1843 | 79.2417 | 2.1515 | 2.2257 | 2.0029
14.7334 | 81.7455 | 83.1178 | 79.2248 | 2.1519 | 2.2261 | 2.003
14.7375 | 81.7364 | 83.1594 | 79.2403 | 2.1521 | 2.2259 | 2.0029
14.7417 | 81.6984 | 83.2052 | 79.246 | 2.1523 | 2.2258 | 2.0027
14.7459 | 81.7128 | 83.2043 | 79.2457 | 2.1524 | 2.2267 | 2.003
14.75 | 81.7437 | 83.202 | 79.2482 | 2.1524 | 2.2277 | 2.0032
14.7542 | 81.7402 | 83.1566 | 79.2266 | 2.1527 | 2.2276 | 2.0031
14.7584 | 81.7379 | 83.1094 | 79.2116 | 2.1532 | 2.2274 | 2.0031
14.7625 | 81.7279 | 83.1931 | 79.2385 | 2.1532 | 2.2277 | 2.0031
14.7667 | 81.7106 | 83.2805 | 79.2513 | 2.1531 | 2.2279 | 2.0031
14.7709 | 81.7243 | 83.2434 | 79.2336 | 2.1533 | 2.2285 | 2.0033
14.775 | 81.7516 | 83.2017 | 79.2264 | 2.1535 | 2.2291 | 2.0034
14.7792 | 81.7242 | 83.1913 | 79.2232 | 2.1538 | 2.2287 | 2.0032
14.7834 | 81.696 | 83.182 | 79.2198 | 2.1541 | 2.2283 | 2.0032
14.7875 | 81.6912 | 83.2205 | 79.2325 | 2.1541 | 2.2289 | 2.0033
14.7917 | 81.6965 | 83.2608 | 79.2388 | 2.154 | 2.2294 | 2.0034
14.7959 | 81.7112 | 83.1993 | 79.2192 | 2.1544 | 2.2297 | 2.0034
14.8 | 81.7309 | 83.1339 | 79.2092 | 2.1547 | 2.2299 | 2.0035
14.8042 | 81.7159 | 83.1571 | 79.22 | 2.1549 | 2.2299 | 2.0034
14.8084 | 81.6928 | 83.1842 | 79.2248 | 2.155 | 2.23 | 2.0034
14.8125 | 81.7089 | 83.1801 | 79.2208 | 2.1551 | 2.2307 | 2.0036
14.8167 | 81.7256 | 83.1746 | 79.2182 | 2.1551 | 2.2315 | 2.0037
14.8209 | 81.7219 | 83.1543 | 79.21 | 2.1554 | 2.2315 | 2.0036
14.825 | 81.7139 | 83.1331 | 79.2037 | 2.1557 | 2.2315 | 2.0036
14.8292 | 81.7012 | 83.1867 | 79.2168 | 2.1557 | 2.2319 | 2.0036
14.8334 | 81.6922 | 83.2443 | 79.2235 | 2.1557 | 2.2322 | 2.0037
14.8375 | 81.7037 | 83.2153 | 79.2088 | 2.1559 | 2.2326 | 2.0038
14.8417 | 81.7181 | 83.1825 | 79.2007 | 2.1561 | 2.2331 | 2.0038
14.8459 | 81.7005 | 83.1942 | 79.2036 | 2.1563 | 2.2329 | 2.0038
14.85 | 81.6721 | 83.2069 | 79.2038 | 2.1566 | 2.2327 | 2.0037
14.8542 | 81.6809 | 83.2353 | 79.2083 | 2.1566 | 2.2331 | 2.0039
14.8584 | 81.6892 | 83.2645 | 79.2111 | 2.1566 | 2.2335 | 2.004
14.8625 | 81.6979 | 83.2289 | 79.1984 | 2.1569 | 2.2335 | 2.0039
14.8667 | 81.7075 | 83.1902 | 79.1899 | 2.1572 | 2.2335 | 2.004
14.8709 | 81.6919 | 83.212 | 79.1991 | 2.1573 | 2.2335 | 2.004
14.875 | 81.6667 | 83.2358 | 79.2044 | 2.1574 | 2.2335 | 2.004
14.8792 | 81.6764 | 83.2245 | 79.1962 | 2.1576 | 2.2339 | 2.0041
14.8834 | 81.6874 | 83.2125 | 79.1909 | 2.1577 | 2.2343 | 2.0042
14.8875 | 81.6752 | 83.2039 | 79.1901 | 2.158 | 2.2342 | 2.0041
14.8917 | 81.6665 | 83.1952 | 79.1872 | 2.1583 | 2.2341 | 2.0041
14.8959 | 81.6647 | 83.2041 | 79.1927 | 2.1584 | 2.2345 | 2.0042
14.9 | 81.6443 | 83.2145 | 79.1982 | 2.1585 | 2.2349 | 2.0043
14.9042 | 81.6547 | 83.1803 | 79.1834 | 2.1588 | 2.2351 | 2.0043
14.9084 | 81.6617 | 83.1453 | 79.1728 | 2.1591 | 2.2354 | 2.0044
14.9125 | 81.645 | 83.1686 | 79.1847 | 2.1593 | 2.2355 | 2.0043
14.9167 | 81.641 | 83.1927 | 79.1906 | 2.1596 | 2.2356 | 2.0043
14.9209 | 81.6475 | 83.1734 | 79.1833 | 2.1597 | 2.2363 | 2.0044
14.925 | 81.6504 | 83.1537 | 79.1816 | 2.1599 | 2.237 | 2.0046
14.9292 | 81.6518 | 83.1342 | 79.1723 | 2.1602 | 2.2371 | 2.0045
14.9334 | 81.6619 | 83.1142 | 79.1626 | 2.1604 | 2.2372 | 2.0045
14.9375 | 81.6599 | 83.154 | 79.1774 | 2.1604 | 2.2377 | 2.0045
14.9417 | 81.664 | 83.1936 | 79.1875 | 2.1606 | 2.2382 | 2.0046
14.9459 | 81.6699 | 83.1684 | 79.1717 | 2.1607 | 2.2387 | 2.0047
14.95 | 81.6779 | 83.1431 | 79.1628 | 2.1608 | 2.2391 | 2.0048
14.9542 | 81.6643 | 83.1655 | 79.1678 | 2.1609 | 2.2391 | 2.0047
14.9584 | 81.6649 | 83.1888 | 79.166 | 2.1611 | 2.2391 | 2.0046
14.9625 | 81.6695 | 83.2063 | 79.1671 | 2.1611 | 2.2396 | 2.0048
14.9667 | 81.6619 | 83.2222 | 79.1707 | 2.1612 | 2.2401 | 2.0049
14.9709 | 81.6592 | 83.2138 | 79.1581 | 2.1614 | 2.24 | 2.0049
14.975 | 81.6498 | 83.2066 | 79.1479 | 2.1616 | 2.2398 | 2.0049
14.9792 | 81.6426 | 83.2521 | 79.165 | 2.1616 | 2.2398 | 2.0049
14.9834 | 81.6385 | 83.2981 | 79.1732 | 2.1618 | 2.2399 | 2.0049
14.9875 | 81.6438 | 83.269 | 79.1581 | 2.162 | 2.24 | 2.005
14.9917 | 81.6359 | 83.238 | 79.1532 | 2.1622 | 2.2402 | 2.0051
14.9959 | 81.6172 | 83.2547 | 79.1545 | 2.1625 | 2.2397 | 2.005
15 | 81.6076 | 83.2729 | 79.1501 | 2.1627 | 2.2392 | 2.0049
15.0042 | 81.613 | 83.2911 | 79.1606 | 2.1628 | 2.2394 | 2.0051
15.0084 | 81.6193 | 83.3071 | 79.1686 | 2.163 | 2.2397 | 2.0052
15.0125 | 81.6258 | 83.2544 | 79.1466 | 2.1634 | 2.2395 | 2.0052
15.0167 | 81.6253 | 83.2024 | 79.1357 | 2.1636 | 2.2393 | 2.0052
15.0209 | 81.6137 | 83.2539 | 79.1529 | 2.1638 | 2.239 | 2.0051
15.025 | 81.6094 | 83.3079 | 79.1575 | 2.1639 | 2.2387 | 2.0051
15.0292 | 81.6268 | 83.2814 | 79.1514 | 2.164 | 2.2391 | 2.0053
15.0334 | 81.6283 | 83.2508 | 79.1524 | 2.1642 | 2.2396 | 2.0054
15.0375 | 81.6202 | 83.2191 | 79.1396 | 2.1645 | 2.2391 | 2.0053
15.0417 | 81.6133 | 83.1904 | 79.1305 | 2.1647 | 2.2386 | 2.0053
15.0459 | 81.605 | 83.2445 | 79.1504 | 2.1647 | 2.2389 | 2.0053
15.05 | 81.6059 | 83.2993 | 79.1585 | 2.1649 | 2.2391 | 2.0053
15.0542 | 81.6163 | 83.2346 | 79.1385 | 2.1651 | 2.2394 | 2.0055
15.0584 | 81.6163 | 83.1656 | 79.1314 | 2.1653 | 2.2397 | 2.0056
15.0625 | 81.5988 | 83.1793 | 79.1359 | 2.1656 | 2.2394 | 2.0054
15.0667 | 81.5931 | 83.197 | 79.1341 | 2.1657 | 2.2391 | 2.0054
15.0709 | 81.6014 | 83.2151 | 79.1415 | 2.1658 | 2.2398 | 2.0056
15.075 | 81.602 | 83.2303 | 79.1461 | 2.166 | 2.2405 | 2.0056
15.0792 | 81.6082 | 83.168 | 79.1268 | 2.1662 | 2.2405 | 2.0056
15.0834 | 81.6086 | 83.1041 | 79.1171 | 2.1664 | 2.2406 | 2.0056
15.0875 | 81.5929 | 83.1518 | 79.1336 | 2.1665 | 2.2407 | 2.0056
15.0917 | 81.5956 | 83.2035 | 79.1382 | 2.1667 | 2.2409 | 2.0056
15.0959 | 81.6081 | 83.1682 | 79.1275 | 2.1668 | 2.2418 | 2.0058
15.1 | 81.6055 | 83.128 | 79.1248 | 2.1669 | 2.2426 | 2.0059
15.1042 | 81.597 | 83.1111 | 79.1198 | 2.1672 | 2.2426 | 2.0058
15.1084 | 81.5967 | 83.0967 | 79.1142 | 2.1673 | 2.2424 | 2.0057
15.1125 | 81.5865 | 83.1416 | 79.1283 | 2.1674 | 2.2432 | 2.0059
15.1167 | 81.5861 | 83.1881 | 79.1338 | 2.1675 | 2.244 | 2.0059
15.1209 | 81.5898 | 83.1193 | 79.1088 | 2.1678 | 2.2446 | 2.006
15.125 | 81.573 | 83.0467 | 79.0962 | 2.168 | 2.2452 | 2.0061
15.1292 | 81.5675 | 83.0989 | 79.1159 | 2.1682 | 2.2451 | 2.0059
15.1334 | 81.5762 | 83.1574 | 79.1249 | 2.1683 | 2.2451 | 2.0058
15.1375 | 81.5844 | 83.1589 | 79.1242 | 2.1685 | 2.2462 | 2.0061
15.1417 | 81.5766 | 83.1582 | 79.1269 | 2.1688 | 2.2474 | 2.0063
15.1459 | 81.5607 | 83.0866 | 79.0956 | 2.1691 | 2.2475 | 2.0062
15.15 | 81.5351 | 83.0134 | 79.0738 | 2.1693 | 2.2476 | 2.0062
15.1542 | 81.5173 | 83.0926 | 79.0953 | 2.1695 | 2.248 | 2.0063
15.1584 | 81.5382 | 83.1773 | 79.099 | 2.1698 | 2.2485 | 2.0063
15.1625 | 81.5816 | 83.1637 | 79.1088 | 2.1698 | 2.2493 | 2.0063
15.1667 | 81.6075 | 83.1452 | 79.1286 | 2.1699 | 2.2501 | 2.0063
15.1709 | 81.6014 | 83.1253 | 79.1196 | 2.1704 | 2.2501 | 2.0063
15.175 | 81.5889 | 83.1074 | 79.1166 | 2.1706 | 2.25 | 2.0063
15.1792 | 81.5184 | 83.097 | 79.0851 | 2.1708 | 2.251 | 2.0066
15.1834 | 81.4693 | 83.0877 | 79.0461 | 2.1711 | 2.252 | 2.0067
15.1875 | 81.4778 | 83.0574 | 79.0533 | 2.1714 | 2.2524 | 2.0066
15.1917 | 81.4835 | 83.022 | 79.0612 | 2.1716 | 2.2527 | 2.0066
15.1959 | 81.5095 | 83.1382 | 79.1034 | 2.1721 | 2.2528 | 2.0066
15.2 | 81.5424 | 83.2605 | 79.1326 | 2.1725 | 2.2529 | 2.0067
15.2042 | 81.5972 | 83.2423 | 79.1196 | 2.1721 | 2.2537 | 2.0067
15.2084 | 81.5947 | 83.221 | 79.1228 | 2.1723 | 2.2545 | 2.0066
15.2125 | 81.6315 | 83.1032 | 79.0812 | 2.1728 | 2.2546 | 2.0067
15.2167 | 81.5781 | 82.9823 | 79.0518 | 2.1731 | 2.2547 | 2.0069
15.2209 | 81.4898 | 83.06 | 79.0575 | 2.1736 | 2.255 | 2.0069
15.225 | 81.4264 | 83.145 | 79.0379 | 2.1737 | 2.2552 | 2.0068
15.2292 | 81.4003 | 83.1935 | 79.0639 | 2.1741 | 2.2559 | 2.007
15.2334 | 81.3944 | 83.2384 | 79.0893 | 2.1745 | 2.2566 | 2.0071
15.2375 | 81.4464 | 83.2854 | 79.0912 | 2.1753 | 2.2558 | 2.007
15.2417 | 81.4624 | 83.3337 | 79.0917 | 2.1756 | 2.255 | 2.0071
15.2459 | 81.533 | 83.4147 | 79.1078 | 2.1756 | 2.2546 | 2.0069
15.25 | 81.602 | 83.4983 | 79.1257 | 2.1754 | 2.2543 | 2.0066
15.2542 | 81.6898 | 83.4054 | 79.0981 | 2.1753 | 2.2539 | 2.0068
15.2584 | 81.7192 | 83.3069 | 79.092 | 2.1758 | 2.2535 | 2.007
15.2625 | 81.7219 | 83.3402 | 79.0837 | 2.1763 | 2.2522 | 2.0068
15.2667 | 81.6586 | 83.3782 | 79.0623 | 2.1766 | 2.2509 | 2.0067
15.2709 | 81.5787 | 83.4668 | 79.0845 | 2.1767 | 2.2506 | 2.0068
15.275 | 81.5265 | 83.5546 | 79.0958 | 2.1764 | 2.2503 | 2.0069
15.2792 | 81.5597 | 83.5824 | 79.0889 | 2.1759 | 2.2485 | 2.0068
15.2834 | 81.5943 | 83.6088 | 79.0811 | 2.1755 | 2.2466 | 2.0069
15.2875 | 81.6961 | 83.7456 | 79.1191 | 2.1755 | 2.2445 | 2.0066
15.2917 | 81.8048 | 83.8878 | 79.1472 | 2.1753 | 2.2424 | 2.0064
15.2959 | 81.8756 | 83.7923 | 79.1318 | 2.1751 | 2.2412 | 2.0065
15.3 | 81.8899 | 83.6893 | 79.1435 | 2.1748 | 2.24 | 2.0066
15.3042 | 81.9649 | 83.5246 | 79.1227 | 2.1743 | 2.2381 | 2.0063
15.3084 | 81.9686 | 83.3588 | 79.1219 | 2.1733 | 2.2362 | 2.006
15.3125 | 81.9625 | 83.2382 | 79.1296 | 2.1727 | 2.2368 | 2.0062
15.3167 | 82.0043 | 83.1182 | 79.1426 | 2.1721 | 2.2374 | 2.0062
15.3209 | 82.0123 | 82.8795 | 79.0982 | 2.171 | 2.2388 | 2.0064
15.325 | 81.9778 | 82.6346 | 79.0668 | 2.1703 | 2.2403 | 2.0064
15.3292 | 81.9546 | 82.6492 | 79.0904 | 2.1701 | 2.2417 | 2.0063
15.3334 | 81.9629 | 82.6703 | 79.0897 | 2.1692 | 2.2431 | 2.0061
15.3375 | 81.8638 | 82.7455 | 79.1012 | 2.169 | 2.2459 | 2.0065
15.3417 | 81.833 | 82.8216 | 79.0942 | 2.1689 | 2.2486 | 2.0068
15.3459 | 81.8057 | 82.8845 | 79.0859 | 2.1686 | 2.2494 | 2.0066
15.35 | 81.7471 | 82.9476 | 79.071 | 2.1687 | 2.2501 | 2.0065
15.3542 | 81.7165 | 83.1536 | 79.0999 | 2.169 | 2.2505 | 2.0065
15.3584 | 81.6598 | 83.367 | 79.1101 | 2.1689 | 2.2509 | 2.0067
15.3625 | 81.5974 | 83.4051 | 79.0958 | 2.1689 | 2.2508 | 2.0067
15.3667 | 81.5678 | 83.4372 | 79.0898 | 2.1688 | 2.2508 | 2.0067
15.3709 | 81.5566 | 83.4688 | 79.1072 | 2.1687 | 2.2492 | 2.0064
15.375 | 81.5978 | 83.4993 | 79.1321 | 2.1691 | 2.2476 | 2.0063
15.3792 | 81.593 | 83.4861 | 79.1173 | 2.1693 | 2.2474 | 2.0065
15.3834 | 81.5745 | 83.4744 | 79.1105 | 2.1695 | 2.2471 | 2.0068
15.3875 | 81.5621 | 83.3354 | 79.0801 | 2.1696 | 2.2465 | 2.0066
15.3917 | 81.57 | 83.1901 | 79.0637 | 2.1696 | 2.2459 | 2.0064
15.3959 | 81.5743 | 83.2115 | 79.0985 | 2.1697 | 2.2456 | 2.0065
15.4 | 81.5751 | 83.2361 | 79.1238 | 2.1701 | 2.2452 | 2.0065
15.4042 | 81.591 | 83.2037 | 79.1136 | 2.1701 | 2.246 | 2.0066
15.4084 | 81.5716 | 83.1708 | 79.1065 | 2.1702 | 2.2468 | 2.0066
15.4125 | 81.6052 | 83.109 | 79.0983 | 2.17 | 2.2468 | 2.0065
15.4167 | 81.6406 | 83.0454 | 79.0963 | 2.1701 | 2.2468 | 2.0064
15.4209 | 81.6648 | 83.0979 | 79.0977 | 2.1703 | 2.2474 | 2.0066
15.425 | 81.6562 | 83.156 | 79.0886 | 2.1706 | 2.248 | 2.0067
15.4292 | 81.6363 | 83.1599 | 79.0869 | 2.1708 | 2.2485 | 2.0066
15.4334 | 81.5958 | 83.1613 | 79.083 | 2.1707 | 2.249 | 2.0065
15.4375 | 81.5855 | 83.1916 | 79.0987 | 2.1705 | 2.2489 | 2.0066
15.4417 | 81.5869 | 83.2218 | 79.1133 | 2.1706 | 2.2488 | 2.0066
15.4459 | 81.5923 | 83.2474 | 79.1025 | 2.1707 | 2.249 | 2.0067
15.45 | 81.5779 | 83.275 | 79.0909 | 2.1709 | 2.2492 | 2.0067
15.4542 | 81.5625 | 83.2401 | 79.0971 | 2.1711 | 2.2492 | 2.0066
15.4584 | 81.5765 | 83.2015 | 79.1088 | 2.1709 | 2.2491 | 2.0064
15.4625 | 81.5729 | 83.1824 | 79.0962 | 2.171 | 2.2493 | 2.0066
15.4667 | 81.6016 | 83.1663 | 79.0876 | 2.1711 | 2.2495 | 2.0068
15.4709 | 81.5889 | 83.1512 | 79.08 | 2.1714 | 2.2498 | 2.0067
15.475 | 81.5809 | 83.137 | 79.069 | 2.1716 | 2.2502 | 2.0066
15.4792 | 81.584 | 83.1329 | 79.0889 | 2.1713 | 2.2505 | 2.0067
15.4834 | 81.6203 | 83.1265 | 79.1063 | 2.1712 | 2.2509 | 2.0068
15.4875 | 81.6804 | 83.1219 | 79.0876 | 2.1711 | 2.2514 | 2.0068
15.4917 | 81.6968 | 83.1191 | 79.0716 | 2.1713 | 2.2519 | 2.0069
15.4959 | 81.7086 | 83.1031 | 79.0819 | 2.1718 | 2.2524 | 2.0068
15.5 | 81.6877 | 83.0856 | 79.0904 | 2.1719 | 2.2529 | 2.0066
15.5042 | 81.6436 | 83.0607 | 79.0896 | 2.1719 | 2.2537 | 2.0069
15.5084 | 81.6233 | 83.036 | 79.0931 | 2.1718 | 2.2544 | 2.007
15.5125 | 81.5899 | 83.0102 | 79.0713 | 2.1718 | 2.2552 | 2.007
15.5167 | 81.5456 | 82.9872 | 79.0525 | 2.1721 | 2.2561 | 2.0069
15.5209 | 81.4899 | 82.9878 | 79.0704 | 2.1723 | 2.257 | 2.007
15.525 | 81.475 | 82.9882 | 79.0819 | 2.1727 | 2.2579 | 2.007
15.5292 | 81.4673 | 83.0116 | 79.0726 | 2.1727 | 2.2587 | 2.0071
15.5334 | 81.4754 | 83.036 | 79.0617 | 2.1732 | 2.2596 | 2.0073
15.5375 | 81.4887 | 83.0706 | 79.0624 | 2.1738 | 2.2602 | 2.0072
15.5417 | 81.4931 | 83.1049 | 79.0587 | 2.1741 | 2.2608 | 2.0071
15.5459 | 81.4871 | 83.1368 | 79.0723 | 2.1743 | 2.2612 | 2.0072
15.55 | 81.5149 | 83.1662 | 79.0824 | 2.1745 | 2.2615 | 2.0073
15.5542 | 81.555 | 83.1969 | 79.0692 | 2.1745 | 2.2616 | 2.0073
15.5584 | 81.5579 | 83.2275 | 79.0576 | 2.1748 | 2.2617 | 2.0073
15.5625 | 81.5712 | 83.2339 | 79.067 | 2.175 | 2.2617 | 2.0072
15.5667 | 81.5578 | 83.2385 | 79.0776 | 2.1749 | 2.2618 | 2.0072
15.5709 | 81.5555 | 83.2207 | 79.0726 | 2.1748 | 2.2618 | 2.0073
15.575 | 81.5584 | 83.2017 | 79.0718 | 2.1748 | 2.2618 | 2.0074
15.5792 | 81.5603 | 83.1907 | 79.0649 | 2.175 | 2.2619 | 2.0073
15.5834 | 81.5433 | 83.1818 | 79.0605 | 2.1751 | 2.262 | 2.0072
15.5875 | 81.5191 | 83.1377 | 79.063 | 2.1753 | 2.2624 | 2.0073
15.5917 | 81.516 | 83.0936 | 79.0699 | 2.1753 | 2.2629 | 2.0074
15.5959 | 81.5129 | 83.0955 | 79.061 | 2.1754 | 2.2631 | 2.0074
15.6 | 81.5145 | 83.0985 | 79.0485 | 2.1756 | 2.2633 | 2.0074
15.6042 | 81.5115 | 83.1348 | 79.0616 | 2.1759 | 2.2638 | 2.0074
15.6084 | 81.5056 | 83.1717 | 79.0689 | 2.176 | 2.2643 | 2.0073
15.6125 | 81.502 | 83.1431 | 79.061 | 2.1761 | 2.2647 | 2.0075
15.6167 | 81.5028 | 83.113 | 79.0592 | 2.1763 | 2.2651 | 2.0076
15.6209 | 81.514 | 83.1391 | 79.0585 | 2.1765 | 2.2651 | 2.0075
15.625 | 81.5031 | 83.1666 | 79.0525 | 2.1767 | 2.2651 | 2.0074
15.6292 | 81.502 | 83.1639 | 79.0592 | 2.1768 | 2.2657 | 2.0075
15.6334 | 81.5092 | 83.1605 | 79.0676 | 2.1769 | 2.2664 | 2.0076
15.6375 | 81.5154 | 83.1394 | 79.0531 | 2.1769 | 2.2664 | 2.0075
15.6417 | 81.5156 | 83.1175 | 79.0424 | 2.1772 | 2.2663 | 2.0076
15.6459 | 81.5219 | 83.1779 | 79.0584 | 2.1773 | 2.2665 | 2.0075
15.65 | 81.5121 | 83.2397 | 79.0639 | 2.1773 | 2.2666 | 2.0075
15.6542 | 81.5053 | 83.1977 | 79.0549 | 2.1774 | 2.2671 | 2.0076
15.6584 | 81.5146 | 83.1532 | 79.0565 | 2.1775 | 2.2676 | 2.0077
15.6625 | 81.5061 | 83.1543 | 79.0497 | 2.1777 | 2.2673 | 2.0076
15.6667 | 81.4876 | 83.1561 | 79.0406 | 2.1779 | 2.2669 | 2.0076
15.6709 | 81.4866 | 83.1949 | 79.0576 | 2.1781 | 2.2674 | 2.0076
15.675 | 81.4911 | 83.2346 | 79.0672 | 2.178 | 2.2679 | 2.0076
15.6792 | 81.4948 | 83.1604 | 79.0474 | 2.1782 | 2.2682 | 2.0077
15.6834 | 81.5085 | 83.0841 | 79.0416 | 2.1784 | 2.2684 | 2.0078
15.6875 | 81.505 | 83.1175 | 79.0491 | 2.1786 | 2.2683 | 2.0077
15.6917 | 81.4829 | 83.1532 | 79.0468 | 2.1787 | 2.2682 | 2.0076
15.6959 | 81.4909 | 83.1569 | 79.0521 | 2.1787 | 2.269 | 2.0078
15.7 | 81.5049 | 83.1597 | 79.058 | 2.1787 | 2.2699 | 2.0078
15.7042 | 81.5053 | 83.124 | 79.0427 | 2.1789 | 2.2698 | 2.0078
15.7084 | 81.505 | 83.0877 | 79.0343 | 2.1791 | 2.2697 | 2.0078
15.7125 | 81.4946 | 83.1564 | 79.0507 | 2.1792 | 2.2699 | 2.0078
15.7167 | 81.4826 | 83.2278 | 79.0545 | 2.1792 | 2.2702 | 2.0077
15.7209 | 81.487 | 83.189 | 79.0441 | 2.1793 | 2.2707 | 2.0079
15.725 | 81.4995 | 83.1469 | 79.0441 | 2.1794 | 2.2712 | 2.0079
15.7292 | 81.4872 | 83.157 | 79.0404 | 2.1797 | 2.2708 | 2.0078
15.7334 | 81.4702 | 83.1686 | 79.0342 | 2.1799 | 2.2704 | 2.0078
15.7375 | 81.4727 | 83.2165 | 79.0488 | 2.1799 | 2.2708 | 2.0079
15.7417 | 81.4806 | 83.2649 | 79.0556 | 2.1799 | 2.2713 | 2.0079
15.7459 | 81.4894 | 83.1918 | 79.037 | 2.18 | 2.2714 | 2.0079
15.75 | 81.4958 | 83.115 | 79.0317 | 2.1804 | 2.2715 | 2.008
15.7542 | 81.4764 | 83.1594 | 79.0401 | 2.1805 | 2.2712 | 2.0079
15.7584 | 81.458 | 83.2076 | 79.0386 | 2.1805 | 2.2708 | 2.0078
15.7625 | 81.465 | 83.2099 | 79.0432 | 2.1806 | 2.2715 | 2.008
15.7667 | 81.4851 | 83.2104 | 79.0484 | 2.1806 | 2.2722 | 2.008
15.7709 | 81.4789 | 83.1507 | 79.0323 | 2.1809 | 2.272 | 2.008
15.775 | 81.4617 | 83.0904 | 79.0245 | 2.1813 | 2.2718 | 2.008
15.7792 | 81.4527 | 83.1467 | 79.0391 | 2.1813 | 2.272 | 2.008
15.7834 | 81.4378 | 83.2067 | 79.0426 | 2.1813 | 2.2722 | 2.008
15.7875 | 81.4526 | 83.1675 | 79.0353 | 2.1815 | 2.2728 | 2.0081
15.7917 | 81.4724 | 83.1247 | 79.036 | 2.1818 | 2.2735 | 2.0082
15.7959 | 81.4545 | 83.1131 | 79.0318 | 2.182 | 2.2733 | 2.008
15.8 | 81.4333 | 83.1037 | 79.0269 | 2.1823 | 2.2731 | 2.008
15.8042 | 81.4394 | 83.1364 | 79.0363 | 2.1822 | 2.2737 | 2.0081
15.8084 | 81.4507 | 83.1693 | 79.0406 | 2.1823 | 2.2744 | 2.0081
15.8125 | 81.4635 | 83.1189 | 79.0262 | 2.1825 | 2.2747 | 2.0082
15.8167 | 81.475 | 83.0647 | 79.021 | 2.1828 | 2.275 | 2.0082
15.8209 | 81.4608 | 83.1126 | 79.0317 | 2.1828 | 2.275 | 2.0081
15.825 | 81.4468 | 83.1642 | 79.034 | 2.1829 | 2.2751 | 2.0081
15.8292 | 81.4585 | 83.1622 | 79.0322 | 2.1829 | 2.2758 | 2.0082
15.8334 | 81.4873 | 83.1585 | 79.0333 | 2.1829 | 2.2765 | 2.0083
15.8375 | 81.4767 | 83.1345 | 79.0221 | 2.1831 | 2.2764 | 2.0082
15.8417 | 81.4744 | 83.1095 | 79.015 | 2.1834 | 2.2761 | 2.0082
15.8459 | 81.4562 | 83.1786 | 79.03 | 2.1833 | 2.2763 | 2.0082
15.85 | 81.4479 | 83.2505 | 79.0358 | 2.1833 | 2.2765 | 2.0082
15.8542 | 81.4569 | 83.2167 | 79.0239 | 2.1833 | 2.2768 | 2.0083
15.8584 | 81.471 | 83.1804 | 79.0197 | 2.1835 | 2.2771 | 2.0084
15.8625 | 81.4557 | 83.1958 | 79.0219 | 2.1837 | 2.2766 | 2.0083
15.8667 | 81.434 | 83.2129 | 79.0205 | 2.1839 | 2.276 | 2.0082
15.8709 | 81.428 | 83.2493 | 79.0281 | 2.1839 | 2.2763 | 2.0084
15.875 | 81.4245 | 83.2854 | 79.0327 | 2.184 | 2.2766 | 2.0084
15.8792 | 81.4286 | 83.2356 | 79.019 | 2.1842 | 2.2764 | 2.0084
15.8834 | 81.4315 | 83.183 | 79.0123 | 2.1845 | 2.2761 | 2.0084
15.8875 | 81.422 | 83.2152 | 79.023 | 2.1847 | 2.2758 | 2.0084
15.8917 | 81.412 | 83.2505 | 79.0273 | 2.1848 | 2.2755 | 2.0083
15.8959 | 81.422 | 83.2398 | 79.0217 | 2.1849 | 2.2758 | 2.0084
15.9 | 81.4327 | 83.2283 | 79.0205 | 2.1851 | 2.2761 | 2.0085
15.9042 | 81.4329 | 83.2062 | 79.0171 | 2.1853 | 2.2757 | 2.0084
15.9084 | 81.4268 | 83.183 | 79.0136 | 2.1855 | 2.2753 | 2.0084
15.9125 | 81.4288 | 83.2078 | 79.0218 | 2.1855 | 2.2755 | 2.0085
15.9167 | 81.4227 | 83.2345 | 79.0274 | 2.1856 | 2.2756 | 2.0085
15.9209 | 81.4304 | 83.2004 | 79.0153 | 2.1858 | 2.2757 | 2.0085
15.925 | 81.4343 | 83.1651 | 79.0091 | 2.1859 | 2.2758 | 2.0085
15.9292 | 81.4229 | 83.1792 | 79.0181 | 2.186 | 2.2756 | 2.0085
15.9334 | 81.417 | 83.193 | 79.0201 | 2.1862 | 2.2755 | 2.0084
15.9375 | 81.4177 | 83.1822 | 79.0166 | 2.1862 | 2.2759 | 2.0086
15.9417 | 81.4207 | 83.1714 | 79.0181 | 2.1864 | 2.2764 | 2.0086
15.9459 | 81.4171 | 83.1481 | 79.0109 | 2.1865 | 2.2763 | 2.0085
15.95 | 81.413 | 83.1238 | 79.0048 | 2.1867 | 2.2762 | 2.0085
15.9542 | 81.4101 | 83.152 | 79.0176 | 2.1868 | 2.2765 | 2.0086
15.9584 | 81.4113 | 83.1799 | 79.0232 | 2.1869 | 2.2768 | 2.0086
15.9625 | 81.4147 | 83.1376 | 79.0096 | 2.187 | 2.2773 | 2.0086
15.9667 | 81.4218 | 83.0951 | 79.0052 | 2.1872 | 2.2777 | 2.0087
15.9709 | 81.4108 | 83.1036 | 79.0084 | 2.1873 | 2.2777 | 2.0086
15.975 | 81.4032 | 83.1121 | 79.0052 | 2.1875 | 2.2777 | 2.0086
15.9792 | 81.4132 | 83.127 | 79.0148 | 2.1875 | 2.2784 | 2.0087
15.9834 | 81.4263 | 83.1415 | 79.0237 | 2.1875 | 2.2791 | 2.0087
15.9875 | 81.4155 | 83.0954 | 79.0064 | 2.1878 | 2.2794 | 2.0087
15.9917 | 81.4127 | 83.0495 | 78.9966 | 2.188 | 2.2797 | 2.0088
15.9959 | 81.3925 | 83.0791 | 79.0038 | 2.1881 | 2.28 | 2.0087
16 | 81.3789 | 83.1091 | 79.0012 | 2.1881 | 2.2803 | 2.0087
16.0042 | 81.3943 | 83.1005 | 79.0015 | 2.1883 | 2.281 | 2.0088
16.0084 | 81.4063 | 83.0922 | 79.0062 | 2.1884 | 2.2818 | 2.0089
16.0125 | 81.4154 | 83.0967 | 79.0125 | 2.1886 | 2.2818 | 2.0087
16.0167 | 81.4115 | 83.1031 | 79.0196 | 2.1887 | 2.2818 | 2.0086
16.0209 | 81.398 | 83.1041 | 79.0117 | 2.1889 | 2.2826 | 2.0088
16.025 | 81.3635 | 83.1042 | 79.0038 | 2.1891 | 2.2834 | 2.009
16.0292 | 81.3442 | 83.0497 | 78.9766 | 2.1894 | 2.2838 | 2.009
16.0334 | 81.3312 | 82.9953 | 78.9538 | 2.1896 | 2.2842 | 2.009
16.0375 | 81.3534 | 83.0812 | 78.9974 | 2.1897 | 2.2842 | 2.0089
16.0417 | 81.3937 | 83.1691 | 79.025 | 2.1898 | 2.2843 | 2.0087
16.0459 | 81.4239 | 83.1681 | 79.0239 | 2.1899 | 2.2851 | 2.0089
16.05 | 81.4288 | 83.1654 | 79.0342 | 2.1902 | 2.286 | 2.0091
16.0542 | 81.4241 | 83.0833 | 78.9977 | 2.1903 | 2.286 | 2.0089
16.0584 | 81.395 | 83.0017 | 78.9752 | 2.1904 | 2.286 | 2.0088
16.0625 | 81.3378 | 83.0239 | 78.9777 | 2.1907 | 2.2867 | 2.009
16.0667 | 81.312 | 83.0458 | 78.9612 | 2.1911 | 2.2874 | 2.0092
16.0709 | 81.2924 | 83.0764 | 78.9781 | 2.1912 | 2.2878 | 2.0091
16.075 | 81.3088 | 83.1061 | 78.9913 | 2.1913 | 2.2882 | 2.009
16.0792 | 81.3282 | 83.1607 | 79.011 | 2.1919 | 2.2883 | 2.009
16.0834 | 81.3774 | 83.2175 | 79.0323 | 2.192 | 2.2883 | 2.0091
16.0875 | 81.3933 | 83.1793 | 79.009 | 2.1921 | 2.2888 | 2.0091
16.0917 | 81.4219 | 83.1383 | 78.9954 | 2.1922 | 2.2893 | 2.0091
16.0959 | 81.4236 | 83.0799 | 78.9822 | 2.1923 | 2.2894 | 2.009
16.1 | 81.4269 | 83.0218 | 78.9778 | 2.1924 | 2.2894 | 2.009
16.1042 | 81.3549 | 83.0829 | 78.9833 | 2.193 | 2.2897 | 2.0092
16.1084 | 81.3004 | 83.1473 | 78.9697 | 2.1933 | 2.29 | 2.0093
16.1125 | 81.2546 | 83.1907 | 78.9807 | 2.1936 | 2.2902 | 2.0092
16.1167 | 81.2333 | 83.2315 | 78.9863 | 2.1938 | 2.2904 | 2.0092
16.1209 | 81.2352 | 83.2907 | 78.9968 | 2.1944 | 2.2897 | 2.0091
16.125 | 81.2543 | 83.3523 | 79.0076 | 2.1949 | 2.289 | 2.0093
16.1292 | 81.2946 | 83.4001 | 79.0064 | 2.1952 | 2.2884 | 2.0092
16.1334 | 81.3502 | 83.4489 | 79.0064 | 2.195 | 2.2879 | 2.0091
16.1375 | 81.4208 | 83.3901 | 78.9987 | 2.195 | 2.2872 | 2.0091
16.1417 | 81.5054 | 83.3279 | 79.009 | 2.195 | 2.2865 | 2.0091
16.1459 | 81.5235 | 83.3447 | 78.9951 | 2.1954 | 2.2854 | 2.0091
16.15 | 81.5056 | 83.3643 | 78.9751 | 2.196 | 2.2843 | 2.0092
16.1542 | 81.4476 | 83.4272 | 78.9907 | 2.1962 | 2.2836 | 2.0091
16.1584 | 81.4001 | 83.4894 | 78.9957 | 2.1959 | 2.283 | 2.009
16.1625 | 81.3598 | 83.5129 | 78.9978 | 2.1956 | 2.2816 | 2.0091
16.1667 | 81.408 | 83.5361 | 78.9992 | 2.1951 | 2.2802 | 2.0093
16.1709 | 81.4391 | 83.6105 | 79.005 | 2.1949 | 2.2784 | 2.009
16.175 | 81.5097 | 83.6877 | 79.002 | 2.1952 | 2.2766 | 2.0089
16.1792 | 81.552 | 83.6148 | 79.0105 | 2.1953 | 2.2756 | 2.0089
16.1834 | 81.5919 | 83.5376 | 79.0374 | 2.1952 | 2.2747 | 2.0089
16.1875 | 81.6389 | 83.3772 | 79.0119 | 2.195 | 2.2736 | 2.0089
16.1917 | 81.6903 | 83.2165 | 79.0063 | 2.1946 | 2.2726 | 2.0089
16.1959 | 81.7353 | 83.0985 | 79.0067 | 2.1941 | 2.2732 | 2.0089
16.2 | 81.7545 | 82.98 | 79.0137 | 2.1936 | 2.2739 | 2.0086
16.2042 | 81.7646 | 82.7981 | 78.9959 | 2.193 | 2.2756 | 2.0089
16.2084 | 81.7411 | 82.612 | 78.99 | 2.1924 | 2.2774 | 2.009
16.2125 | 81.7251 | 82.629 | 78.9959 | 2.1918 | 2.2788 | 2.0089
16.2167 | 81.7329 | 82.6495 | 78.982 | 2.1913 | 2.2802 | 2.0088
16.2209 | 81.704 | 82.7457 | 79.006 | 2.1909 | 2.2826 | 2.009
16.225 | 81.7102 | 82.8418 | 79.0136 | 2.1905 | 2.285 | 2.009
16.2292 | 81.7078 | 82.8966 | 78.9906 | 2.1902 | 2.2858 | 2.0091
16.2334 | 81.6594 | 82.9528 | 78.962 | 2.19 | 2.2866 | 2.0092
16.2375 | 81.6478 | 83.1665 | 78.993 | 2.19 | 2.2864 | 2.009
16.2417 | 81.6031 | 83.3847 | 78.9989 | 2.19 | 2.2863 | 2.0089
16.2459 | 81.5711 | 83.4376 | 79.0071 | 2.1899 | 2.2862 | 2.009
16.25 | 81.5359 | 83.486 | 79.0231 | 2.1898 | 2.2861 | 2.0092
16.2542 | 81.5311 | 83.4657 | 79.0035 | 2.1897 | 2.2844 | 2.009
16.2584 | 81.5195 | 83.447 | 78.9967 | 2.1896 | 2.2826 | 2.0089
16.2625 | 81.513 | 83.4418 | 79.0006 | 2.1897 | 2.2822 | 2.009
16.2667 | 81.4991 | 83.4371 | 79.0074 | 2.1899 | 2.2817 | 2.009
16.2709 | 81.4644 | 83.2965 | 78.9855 | 2.1899 | 2.2814 | 2.0091
16.275 | 81.4399 | 83.1507 | 78.9784 | 2.1899 | 2.281 | 2.0091
16.2792 | 81.412 | 83.1662 | 79.0018 | 2.1898 | 2.2804 | 2.0089
16.2834 | 81.3959 | 83.1852 | 79.0174 | 2.1899 | 2.2799 | 2.0088
16.2875 | 81.3924 | 83.1408 | 79.01 | 2.19 | 2.281 | 2.0091
16.2917 | 81.3821 | 83.0944 | 79.0093 | 2.19 | 2.2822 | 2.0092
16.2959 | 81.3871 | 83.0206 | 78.9899 | 2.1901 | 2.2821 | 2.009
16.3 | 81.4154 | 82.9461 | 78.9762 | 2.19 | 2.282 | 2.0089
16.3042 | 81.4352 | 83.0552 | 79.0038 | 2.19 | 2.2826 | 2.009
16.3084 | 81.4479 | 83.1693 | 79.014 | 2.1902 | 2.2832 | 2.009
16.3125 | 81.4482 | 83.1315 | 78.9922 | 2.1904 | 2.2841 | 2.0091
16.3167 | 81.4338 | 83.0901 | 78.9773 | 2.1905 | 2.2849 | 2.0092
16.3209 | 81.4217 | 83.1316 | 78.9926 | 2.1904 | 2.2843 | 2.009
16.325 | 81.4151 | 83.1748 | 79.0004 | 2.1903 | 2.2836 | 2.0088
16.3292 | 81.4277 | 83.2393 | 79.0107 | 2.1902 | 2.2842 | 2.0091
16.3334 | 81.4225 | 83.305 | 79.0168 | 2.1903 | 2.2848 | 2.0092
16.3375 | 81.4312 | 83.198 | 78.9894 | 2.1905 | 2.2847 | 2.0091
16.3417 | 81.4032 | 83.087 | 78.979 | 2.1906 | 2.2846 | 2.009
16.3459 | 81.3885 | 83.1249 | 78.9972 | 2.1907 | 2.2844 | 2.009
16.35 | 81.3698 | 83.1679 | 79.0072 | 2.1907 | 2.2841 | 2.009
16.3542 | 81.3527 | 83.1442 | 78.9956 | 2.1909 | 2.2851 | 2.0092
16.3584 | 81.3542 | 83.1194 | 78.986 | 2.1911 | 2.2861 | 2.0092
16.3625 | 81.3437 | 83.0637 | 78.9839 | 2.1914 | 2.286 | 2.0091
16.3667 | 81.3526 | 83.006 | 78.9858 | 2.1915 | 2.2858 | 2.009
16.3709 | 81.3956 | 83.07 | 78.9993 | 2.1914 | 2.2865 | 2.0091
16.375 | 81.4242 | 83.1378 | 79.0029 | 2.1913 | 2.2871 | 2.0092
16.3792 | 81.472 | 83.0794 | 78.9901 | 2.1914 | 2.2879 | 2.0092
16.3834 | 81.4873 | 83.0169 | 78.9844 | 2.1916 | 2.2888 | 2.0091
16.3875 | 81.5034 | 82.9989 | 78.9895 | 2.1918 | 2.289 | 2.0091
16.3917 | 81.4761 | 82.9826 | 78.9971 | 2.1919 | 2.2892 | 2.0091
16.3959 | 81.4699 | 83.0039 | 78.9915 | 2.1919 | 2.2903 | 2.0092
16.4 | 81.432 | 83.0283 | 78.9826 | 2.1919 | 2.2914 | 2.0093
16.4042 | 81.4104 | 82.9887 | 78.9822 | 2.192 | 2.2921 | 2.0092
16.4084 | 81.3703 | 82.9464 | 78.9832 | 2.1921 | 2.2928 | 2.0091
16.4125 | 81.3612 | 82.9984 | 78.9882 | 2.1922 | 2.2933 | 2.0092
16.4167 | 81.3404 | 83.0532 | 78.9892 | 2.1923 | 2.2937 | 2.0093
16.4209 | 81.3233 | 83.0831 | 78.984 | 2.1925 | 2.2945 | 2.0093
16.425 | 81.3318 | 83.1114 | 78.974 | 2.1928 | 2.2952 | 2.0093
16.4292 | 81.3279 | 83.1226 | 78.985 | 2.193 | 2.2952 | 2.0093
16.4334 | 81.3463 | 83.1311 | 78.9948 | 2.1931 | 2.2952 | 2.0093
16.4375 | 81.3629 | 83.1772 | 78.9868 | 2.1932 | 2.2953 | 2.0093
16.4417 | 81.3788 | 83.2248 | 78.9798 | 2.1933 | 2.2954 | 2.0095
16.4459 | 81.3834 | 83.2165 | 78.983 | 2.1934 | 2.2954 | 2.0093
16.45 | 81.3844 | 83.2049 | 78.9843 | 2.1935 | 2.2954 | 2.0092
16.4542 | 81.3848 | 83.1926 | 78.9894 | 2.1934 | 2.2952 | 2.0093
16.4584 | 81.3868 | 83.1805 | 79 | 2.1934 | 2.295 | 2.0094
16.4625 | 81.3887 | 83.1518 | 78.9811 | 2.1935 | 2.2953 | 2.0094
16.4667 | 81.3824 | 83.1258 | 78.9695 | 2.1936 | 2.2956 | 2.0094
16.4709 | 81.3644 | 83.0936 | 78.9817 | 2.1937 | 2.2958 | 2.0093
16.475 | 81.3519 | 83.0601 | 78.9904 | 2.1937 | 2.296 | 2.0092
16.4792 | 81.353 | 83.0725 | 78.9847 | 2.1938 | 2.2964 | 2.0094
16.4834 | 81.3537 | 83.0866 | 78.9811 | 2.1938 | 2.2968 | 2.0095
16.4875 | 81.353 | 83.0954 | 78.9784 | 2.1941 | 2.2972 | 2.0094
16.4917 | 81.3448 | 83.1043 | 78.9725 | 2.1943 | 2.2976 | 2.0093
16.4959 | 81.3348 | 83.1069 | 78.9858 | 2.1943 | 2.2978 | 2.0094
16.5 | 81.3324 | 83.108 | 78.9959 | 2.1944 | 2.298 | 2.0094
16.5042 | 81.3421 | 83.1137 | 78.9798 | 2.1945 | 2.2983 | 2.0094
16.5084 | 81.3506 | 83.1208 | 78.9688 | 2.1947 | 2.2986 | 2.0095
16.5125 | 81.3419 | 83.1234 | 78.9785 | 2.1949 | 2.2988 | 2.0094
16.5167 | 81.3396 | 83.1251 | 78.9827 | 2.195 | 2.299 | 2.0093
16.5209 | 81.3448 | 83.1336 | 78.9838 | 2.195 | 2.2991 | 2.0094
16.525 | 81.3574 | 83.1416 | 78.9858 | 2.195 | 2.2993 | 2.0095
16.5292 | 81.3609 | 83.1473 | 78.9764 | 2.1951 | 2.2994 | 2.0095
16.5334 | 81.3618 | 83.1537 | 78.9697 | 2.1953 | 2.2996 | 2.0094
16.5375 | 81.3418 | 83.145 | 78.9801 | 2.1954 | 2.2997 | 2.0094
16.5417 | 81.3304 | 83.1349 | 78.9876 | 2.1954 | 2.2999 | 2.0094
16.5459 | 81.3403 | 83.1431 | 78.9796 | 2.1954 | 2.2999 | 2.0095
16.55 | 81.3436 | 83.1516 | 78.9739 | 2.1955 | 2.2999 | 2.0095
16.5542 | 81.3375 | 83.1489 | 78.9768 | 2.1957 | 2.3001 | 2.0095
16.5584 | 81.3357 | 83.1469 | 78.9785 | 2.1959 | 2.3004 | 2.0094
16.5625 | 81.3302 | 83.1165 | 78.9788 | 2.1959 | 2.3006 | 2.0095
16.5667 | 81.3285 | 83.0851 | 78.9818 | 2.1959 | 2.3008 | 2.0096
16.5709 | 81.3424 | 83.0993 | 78.9755 | 2.1961 | 2.3009 | 2.0095
16.575 | 81.3431 | 83.1142 | 78.969 | 2.1962 | 2.3011 | 2.0095
16.5792 | 81.3331 | 83.1139 | 78.9775 | 2.1963 | 2.3015 | 2.0095
16.5834 | 81.3337 | 83.1142 | 78.9831 | 2.1964 | 2.302 | 2.0095
16.5875 | 81.3418 | 83.1044 | 78.9764 | 2.1963 | 2.3021 | 2.0095
16.5917 | 81.3403 | 83.094 | 78.9736 | 2.1964 | 2.3021 | 2.0096
16.5959 | 81.3426 | 83.126 | 78.975 | 2.1966 | 2.3023 | 2.0095
16.6 | 81.3334 | 83.1588 | 78.9724 | 2.1967 | 2.3025 | 2.0095
16.6042 | 81.3193 | 83.1474 | 78.9755 | 2.1967 | 2.3028 | 2.0096
16.6084 | 81.3202 | 83.1356 | 78.9803 | 2.1968 | 2.303 | 2.0096
16.6125 | 81.3314 | 83.1476 | 78.9741 | 2.1968 | 2.3029 | 2.0096
16.6167 | 81.3261 | 83.1591 | 78.9689 | 2.197 | 2.3027 | 2.0096
16.6209 | 81.3264 | 83.1716 | 78.9751 | 2.1972 | 2.3029 | 2.0096
16.625 | 81.3205 | 83.1845 | 78.9771 | 2.1972 | 2.3032 | 2.0095
16.6292 | 81.318 | 83.1478 | 78.9718 | 2.1972 | 2.3032 | 2.0096
16.6334 | 81.3227 | 83.11 | 78.973 | 2.1974 | 2.3032 | 2.0097
16.6375 | 81.3273 | 83.1426 | 78.9738 | 2.1975 | 2.3031 | 2.0096
16.6417 | 81.3211 | 83.1759 | 78.9695 | 2.1976 | 2.303 | 2.0096
16.6459 | 81.3154 | 83.1575 | 78.9741 | 2.1977 | 2.3035 | 2.0096
16.65 | 81.3147 | 83.1391 | 78.9787 | 2.1978 | 2.304 | 2.0096
16.6542 | 81.3178 | 83.1039 | 78.9682 | 2.1979 | 2.3039 | 2.0096
16.6584 | 81.3086 | 83.0682 | 78.9644 | 2.1981 | 2.3038 | 2.0097
16.6625 | 81.3104 | 83.1175 | 78.9732 | 2.1982 | 2.304 | 2.0096
16.6667 | 81.3004 | 83.1684 | 78.9726 | 2.1983 | 2.3042 | 2.0096
16.6709 | 81.2968 | 83.1255 | 78.9718 | 2.1983 | 2.3047 | 2.0097
16.675 | 81.3068 | 83.0818 | 78.977 | 2.1985 | 2.3053 | 2.0097
16.6792 | 81.3025 | 83.0739 | 78.9678 | 2.1986 | 2.3051 | 2.0097
16.6834 | 81.2986 | 83.0663 | 78.9608 | 2.1989 | 2.305 | 2.0097
16.6875 | 81.2964 | 83.105 | 78.9715 | 2.1989 | 2.3055 | 2.0097
16.6917 | 81.3026 | 83.1434 | 78.9745 | 2.199 | 2.3061 | 2.0096
16.6959 | 81.3076 | 83.0968 | 78.967 | 2.199 | 2.3064 | 2.0097
16.7 | 81.3123 | 83.0485 | 78.9687 | 2.1993 | 2.3067 | 2.0098
16.7042 | 81.3106 | 83.0873 | 78.9691 | 2.1993 | 2.3067 | 2.0097
16.7084 | 81.3007 | 83.1281 | 78.9638 | 2.1994 | 2.3066 | 2.0097
16.7125 | 81.3092 | 83.1363 | 78.9701 | 2.1994 | 2.3072 | 2.0097
16.7167 | 81.3216 | 83.1432 | 78.9753 | 2.1994 | 2.3078 | 2.0097
16.7209 | 81.3238 | 83.1179 | 78.9641 | 2.1995 | 2.3077 | 2.0097
16.725 | 81.3168 | 83.0919 | 78.96 | 2.1997 | 2.3075 | 2.0098
16.7292 | 81.306 | 83.1557 | 78.9697 | 2.1997 | 2.3075 | 2.0097
16.7334 | 81.3018 | 83.2218 | 78.9689 | 2.1996 | 2.3075 | 2.0097
16.7375 | 81.3099 | 83.1886 | 78.9658 | 2.1997 | 2.3078 | 2.0098
16.7417 | 81.3194 | 83.1538 | 78.9693 | 2.1998 | 2.3081 | 2.0098
16.7459 | 81.3071 | 83.1661 | 78.9639 | 2.2 | 2.3075 | 2.0097
16.75 | 81.2866 | 83.1796 | 78.9583 | 2.2001 | 2.3069 | 2.0098
16.7542 | 81.2744 | 83.2198 | 78.9703 | 2.2001 | 2.3071 | 2.0098
16.7584 | 81.2811 | 83.2595 | 78.9744 | 2.2002 | 2.3074 | 2.0098
16.7625 | 81.2863 | 83.1916 | 78.9616 | 2.2003 | 2.3072 | 2.0098
16.7667 | 81.2922 | 83.1222 | 78.9606 | 2.2006 | 2.3071 | 2.0099
16.7709 | 81.2768 | 83.1689 | 78.9657 | 2.2008 | 2.3066 | 2.0098
16.775 | 81.2652 | 83.2183 | 78.9628 | 2.2008 | 2.3062 | 2.0097
16.7792 | 81.2712 | 83.2101 | 78.9677 | 2.2009 | 2.3066 | 2.0098
16.7834 | 81.2908 | 83.1996 | 78.9725 | 2.2009 | 2.3072 | 2.0099
16.7875 | 81.2966 | 83.1456 | 78.9589 | 2.2012 | 2.3067 | 2.0098
16.7917 | 81.2874 | 83.092 | 78.9546 | 2.2014 | 2.3063 | 2.0099
16.7959 | 81.2798 | 83.1571 | 78.9676 | 2.2014 | 2.3063 | 2.0098
16.8 | 81.2726 | 83.2246 | 78.9691 | 2.2014 | 2.3064 | 2.0098
16.8042 | 81.286 | 83.1733 | 78.9632 | 2.2014 | 2.3068 | 2.0099
16.8084 | 81.3014 | 83.1188 | 78.9646 | 2.2016 | 2.3073 | 2.0099
16.8125 | 81.295 | 83.1091 | 78.9596 | 2.2018 | 2.3068 | 2.0098
16.8167 | 81.2747 | 83.101 | 78.9555 | 2.2019 | 2.3064 | 2.0098
16.8209 | 81.27 | 83.1427 | 78.9661 | 2.2019 | 2.3069 | 2.0099
16.825 | 81.2706 | 83.1843 | 78.9695 | 2.2019 | 2.3075 | 2.0099
16.8292 | 81.2843 | 83.1211 | 78.9599 | 2.202 | 2.3076 | 2.0099
16.8334 | 81.2896 | 83.0553 | 78.9594 | 2.2022 | 2.3078 | 2.0099
16.8375 | 81.2765 | 83.0849 | 78.9622 | 2.2024 | 2.3077 | 2.0099
16.8417 | 81.2555 | 83.1166 | 78.9585 | 2.2025 | 2.3077 | 2.0099
16.8459 | 81.2603 | 83.11 | 78.9591 | 2.2025 | 2.3084 | 2.0099
16.85 | 81.27 | 83.102 | 78.9606 | 2.2025 | 2.3091 | 2.0099
16.8542 | 81.2836 | 83.071 | 78.9579 | 2.2027 | 2.3091 | 2.0099
16.8584 | 81.283 | 83.0396 | 78.9582 | 2.2029 | 2.309 | 2.0099
16.8625 | 81.2784 | 83.0856 | 78.9694 | 2.2029 | 2.3094 | 2.0099
16.8667 | 81.2731 | 83.1333 | 78.9749 | 2.2028 | 2.3098 | 2.0098
16.8709 | 81.2594 | 83.0695 | 78.9533 | 2.203 | 2.3105 | 2.01
16.875 | 81.2543 | 83.0037 | 78.9405 | 2.2032 | 2.3113 | 2.0101
16.8792 | 81.2448 | 83.0245 | 78.9468 | 2.2033 | 2.3111 | 2.01
16.8834 | 81.2446 | 83.0469 | 78.9438 | 2.2033 | 2.311 | 2.0099
16.8875 | 81.2687 | 83.1039 | 78.9704 | 2.2034 | 2.3117 | 2.0099
16.8917 | 81.2987 | 83.1625 | 78.9937 | 2.2034 | 2.3125 | 2.0099
16.8959 | 81.2932 | 83.0854 | 78.9653 | 2.2036 | 2.3128 | 2.01
16.9 | 81.2789 | 83.0072 | 78.9532 | 2.204 | 2.3131 | 2.01
16.9042 | 81.2442 | 83.0187 | 78.947 | 2.2041 | 2.3133 | 2.01
16.9084 | 81.2107 | 83.0316 | 78.9334 | 2.2042 | 2.3134 | 2.0099
16.9125 | 81.2002 | 83.0464 | 78.942 | 2.2044 | 2.3142 | 2.0101
16.9167 | 81.2168 | 83.061 | 78.9424 | 2.2045 | 2.315 | 2.0102
16.9209 | 81.2382 | 83.0949 | 78.9633 | 2.2047 | 2.3148 | 2.01
16.925 | 81.2692 | 83.129 | 78.9844 | 2.2048 | 2.3146 | 2.0098
16.9292 | 81.2887 | 83.1289 | 78.975 | 2.2049 | 2.3153 | 2.01
16.9334 | 81.2873 | 83.1295 | 78.9756 | 2.2051 | 2.316 | 2.0101
16.9375 | 81.2889 | 83.0313 | 78.9415 | 2.2051 | 2.3163 | 2.0101
16.9417 | 81.2628 | 82.9314 | 78.9166 | 2.2052 | 2.3166 | 2.01
16.9459 | 81.2212 | 82.9941 | 78.9426 | 2.2055 | 2.3168 | 2.01
16.95 | 81.1901 | 83.0576 | 78.9488 | 2.2057 | 2.3169 | 2.0101
16.9542 | 81.1702 | 83.1057 | 78.9546 | 2.2058 | 2.3176 | 2.0102
16.9584 | 81.1566 | 83.1541 | 78.9562 | 2.2061 | 2.3184 | 2.0103
16.9625 | 81.2054 | 83.1359 | 78.9571 | 2.2063 | 2.3181 | 2.0101
16.9667 | 81.2303 | 83.1163 | 78.9676 | 2.2065 | 2.3179 | 2.01
16.9709 | 81.2313 | 83.1275 | 78.9637 | 2.2067 | 2.3181 | 2.0101
16.975 | 81.2551 | 83.1394 | 78.9612 | 2.2069 | 2.3184 | 2.0102
16.9792 | 81.2623 | 83.0936 | 78.9455 | 2.2067 | 2.3187 | 2.0101
16.9834 | 81.271 | 83.0483 | 78.9382 | 2.2067 | 2.319 | 2.01
16.9875 | 81.2544 | 83.0783 | 78.9478 | 2.2071 | 2.3189 | 2.0101
16.9917 | 81.2257 | 83.1078 | 78.9463 | 2.2075 | 2.3188 | 2.0102
16.9959 | 81.1409 | 83.1855 | 78.95 | 2.2077 | 2.3188 | 2.0102
17 | 81.0937 | 83.2638 | 78.9414 | 2.208 | 2.3188 | 2.0102
17.0042 | 81.094 | 83.2991 | 78.9524 | 2.2083 | 2.3182 | 2.0101
17.0084 | 81.1101 | 83.3356 | 78.9673 | 2.2087 | 2.3175 | 2.0101
17.0125 | 81.1384 | 83.3638 | 78.9639 | 2.2093 | 2.3167 | 2.0101
17.0167 | 81.1748 | 83.3919 | 78.9613 | 2.2097 | 2.3159 | 2.0102
17.0209 | 81.221 | 83.369 | 78.9527 | 2.2095 | 2.3152 | 2.0101
17.025 | 81.2636 | 83.3457 | 78.9558 | 2.2094 | 2.3144 | 2.01
17.0292 | 81.3293 | 83.3338 | 78.9548 | 2.2094 | 2.3135 | 2.01
17.0334 | 81.3432 | 83.3223 | 78.9564 | 2.2098 | 2.3126 | 2.0102
17.0375 | 81.3504 | 83.3651 | 78.9553 | 2.2102 | 2.3117 | 2.0101
17.0417 | 81.2902 | 83.4075 | 78.9433 | 2.2104 | 2.3108 | 2.0101
17.0459 | 81.2555 | 83.4318 | 78.9518 | 2.2103 | 2.3098 | 2.0101
17.05 | 81.23 | 83.4566 | 78.9596 | 2.21 | 2.3088 | 2.0101
17.0542 | 81.234 | 83.4753 | 78.9591 | 2.2098 | 2.3074 | 2.0101
17.0584 | 81.2483 | 83.4946 | 78.9531 | 2.2098 | 2.3061 | 2.0102
17.0625 | 81.27 | 83.4492 | 78.9612 | 2.2099 | 2.3053 | 2.01
17.0667 | 81.2948 | 83.4026 | 78.9769 | 2.2098 | 2.3045 | 2.0099
17.0709 | 81.3301 | 83.2502 | 78.9615 | 2.2096 | 2.3042 | 2.01
17.075 | 81.3918 | 83.0976 | 78.9686 | 2.2094 | 2.304 | 2.0101
17.0792 | 81.4726 | 82.9692 | 78.9525 | 2.2093 | 2.3046 | 2.01
17.0834 | 81.5074 | 82.8397 | 78.9422 | 2.2095 | 2.3052 | 2.0099
17.0875 | 81.5011 | 82.7487 | 78.9535 | 2.2093 | 2.307 | 2.01
17.0917 | 81.5189 | 82.6549 | 78.9687 | 2.2091 | 2.3087 | 2.0099
17.0959 | 81.5064 | 82.6468 | 78.9616 | 2.2084 | 2.3104 | 2.0101
17.1 | 81.5529 | 82.6387 | 78.9489 | 2.208 | 2.3121 | 2.0101
17.1042 | 81.5646 | 82.7335 | 78.9567 | 2.2078 | 2.3138 | 2.0101
17.1084 | 81.5649 | 82.8287 | 78.9481 | 2.2075 | 2.3155 | 2.0099
17.1125 | 81.5293 | 82.9305 | 78.9496 | 2.2073 | 2.3164 | 2.0101
17.1167 | 81.5098 | 83.0332 | 78.9403 | 2.2068 | 2.3173 | 2.0103
17.1209 | 81.5082 | 83.2011 | 78.9552 | 2.2065 | 2.3168 | 2.0101
17.125 | 81.5097 | 83.3708 | 78.9499 | 2.2063 | 2.3163 | 2.01
17.1292 | 81.5053 | 83.4425 | 78.9664 | 2.2064 | 2.3158 | 2.01
17.1334 | 81.4744 | 83.5142 | 78.9861 | 2.2063 | 2.3153 | 2.0101
17.1375 | 81.4717 | 83.454 | 78.9543 | 2.2061 | 2.3139 | 2.0101
17.1417 | 81.4801 | 83.3953 | 78.9396 | 2.2058 | 2.3125 | 2.0102
17.1459 | 81.5111 | 83.3805 | 78.9493 | 2.2057 | 2.3116 | 2.01
17.15 | 81.5258 | 83.3658 | 78.9563 | 2.2058 | 2.3106 | 2.0099
17.1542 | 81.4934 | 83.2681 | 78.9552 | 2.2059 | 2.3106 | 2.0101
17.1584 | 81.4631 | 83.1687 | 78.9665 | 2.2059 | 2.3105 | 2.0102
17.1625 | 81.4375 | 83.1096 | 78.9529 | 2.2057 | 2.3102 | 2.0101
17.1667 | 81.4189 | 83.0511 | 78.944 | 2.2056 | 2.3098 | 2.01
17.1709 | 81.4107 | 83.0445 | 78.9606 | 2.2056 | 2.3106 | 2.01
17.175 | 81.3954 | 83.0364 | 78.9744 | 2.2057 | 2.3114 | 2.01
17.1792 | 81.3813 | 82.983 | 78.955 | 2.2057 | 2.312 | 2.0101
17.1834 | 81.3736 | 82.9296 | 78.9439 | 2.2056 | 2.3126 | 2.0102
17.1875 | 81.3735 | 82.9978 | 78.953 | 2.2055 | 2.3128 | 2.01
17.1917 | 81.3814 | 83.0681 | 78.9501 | 2.2055 | 2.3131 | 2.0099
17.1959 | 81.3797 | 83.0864 | 78.9561 | 2.2056 | 2.314 | 2.0101
17.2 | 81.377 | 83.1032 | 78.9593 | 2.2056 | 2.3148 | 2.0102
17.2042 | 81.352 | 83.1223 | 78.9525 | 2.2057 | 2.3144 | 2.0101
17.2084 | 81.3576 | 83.142 | 78.9444 | 2.2056 | 2.3139 | 2.01
17.2125 | 81.3526 | 83.1948 | 78.9604 | 2.2054 | 2.3142 | 2.0101
17.2167 | 81.3674 | 83.2478 | 78.971 | 2.2054 | 2.3144 | 2.01
17.2209 | 81.3874 | 83.1645 | 78.9519 | 2.2054 | 2.3145 | 2.0101
17.225 | 81.3766 | 83.0801 | 78.9459 | 2.2056 | 2.3146 | 2.0102
17.2292 | 81.3546 | 83.0995 | 78.9533 | 2.2059 | 2.3143 | 2.01
17.2334 | 81.3275 | 83.1217 | 78.9555 | 2.2059 | 2.3139 | 2.0099
17.2375 | 81.2813 | 83.0993 | 78.9553 | 2.2058 | 2.3149 | 2.0101
17.2417 | 81.2622 | 83.076 | 78.9578 | 2.2058 | 2.3159 | 2.0102
17.2459 | 81.2306 | 83.0169 | 78.9453 | 2.2058 | 2.3158 | 2.0101
17.25 | 81.2191 | 82.9574 | 78.9371 | 2.2059 | 2.3158 | 2.0101
17.2542 | 81.2144 | 83.0326 | 78.9589 | 2.2062 | 2.3163 | 2.0101
17.2584 | 81.2287 | 83.1092 | 78.968 | 2.2061 | 2.3168 | 2.0101
17.2625 | 81.2408 | 83.0378 | 78.9507 | 2.2062 | 2.3178 | 2.0102
17.2667 | 81.2748 | 82.9635 | 78.9457 | 2.2061 | 2.3189 | 2.0103
17.2709 | 81.2906 | 82.9587 | 78.948 | 2.2063 | 2.3188 | 2.0101
17.275 | 81.3201 | 82.956 | 78.9478 | 2.2064 | 2.3187 | 2.01
17.2792 | 81.3175 | 83.0047 | 78.9581 | 2.2064 | 2.3199 | 2.0102
17.2834 | 81.3207 | 83.0545 | 78.9627 | 2.2065 | 2.3211 | 2.0102
17.2875 | 81.3243 | 82.9802 | 78.9428 | 2.2065 | 2.3217 | 2.0102
17.2917 | 81.3033 | 82.9038 | 78.9337 | 2.2066 | 2.3222 | 2.0102
17.2959 | 81.2934 | 82.9924 | 78.9529 | 2.2068 | 2.3223 | 2.0101
17.3 | 81.2673 | 83.0832 | 78.958 | 2.2067 | 2.3223 | 2.0101
17.3042 | 81.242 | 83.101 | 78.9532 | 2.2067 | 2.3233 | 2.0102
17.3084 | 81.2306 | 83.1164 | 78.9496 | 2.2067 | 2.3243 | 2.0103
17.3125 | 81.2313 | 83.0888 | 78.9421 | 2.2067 | 2.3239 | 2.0102
17.3167 | 81.2329 | 83.0599 | 78.9384 | 2.2068 | 2.3234 | 2.0101
17.3209 | 81.2346 | 83.1618 | 78.9565 | 2.207 | 2.3235 | 2.0102
17.325 | 81.2345 | 83.2645 | 78.9621 | 2.207 | 2.3235 | 2.0102
17.3292 | 81.2313 | 83.2087 | 78.9475 | 2.207 | 2.3238 | 2.0102
17.3334 | 81.2429 | 83.1495 | 78.9426 | 2.207 | 2.324 | 2.0103
17.3375 | 81.2508 | 83.1321 | 78.9474 | 2.2071 | 2.3234 | 2.0101
17.3417 | 81.2534 | 83.1171 | 78.9549 | 2.2072 | 2.3227 | 2.0101
17.3459 | 81.2463 | 83.1269 | 78.9533 | 2.2073 | 2.3233 | 2.0102
17.35 | 81.2486 | 83.1383 | 78.9518 | 2.2073 | 2.324 | 2.0103
17.3542 | 81.238 | 83.0571 | 78.9423 | 2.2073 | 2.3241 | 2.0102
17.3584 | 81.2356 | 82.9744 | 78.94 | 2.2074 | 2.3242 | 2.0101
17.3625 | 81.2356 | 83.0272 | 78.9514 | 2.2074 | 2.3243 | 2.0102
17.3667 | 81.2277 | 83.083 | 78.9565 | 2.2074 | 2.3244 | 2.0102
17.3709 | 81.226 | 83.0838 | 78.949 | 2.2075 | 2.3252 | 2.0103
17.375 | 81.2224 | 83.0832 | 78.9415 | 2.2077 | 2.326 | 2.0103
17.3792 | 81.218 | 83.0561 | 78.9457 | 2.2078 | 2.3259 | 2.0102
17.3834 | 81.2097 | 83.0281 | 78.9508 | 2.2079 | 2.3258 | 2.0101
17.3875 | 81.2178 | 83.0838 | 78.951 | 2.208 | 2.3261 | 2.0102
17.3917 | 81.2158 | 83.1415 | 78.948 | 2.208 | 2.3264 | 2.0103
17.3959 | 81.2205 | 83.117 | 78.9454 | 2.2082 | 2.3267 | 2.0102
17.4 | 81.2258 | 83.0899 | 78.9423 | 2.2083 | 2.327 | 2.0102
17.4042 | 81.2243 | 83.0957 | 78.9488 | 2.2083 | 2.3269 | 2.0102
17.4084 | 81.2308 | 83.1025 | 78.956 | 2.2083 | 2.3267 | 2.0103
17.4125 | 81.2306 | 83.1213 | 78.9464 | 2.2084 | 2.327 | 2.0103
17.4167 | 81.2299 | 83.1403 | 78.9386 | 2.2084 | 2.3274 | 2.0103
17.4209 | 81.2224 | 83.1156 | 78.946 | 2.2085 | 2.3273 | 2.0102
17.425 | 81.2172 | 83.0886 | 78.9502 | 2.2086 | 2.3273 | 2.0102
17.4292 | 81.2189 | 83.1092 | 78.9491 | 2.2086 | 2.3273 | 2.0103
17.4334 | 81.2243 | 83.132 | 78.9506 | 2.2086 | 2.3273 | 2.0103
17.4375 | 81.2223 | 83.1138 | 78.944 | 2.2088 | 2.3277 | 2.0103
17.4417 | 81.216 | 83.0948 | 78.9388 | 2.2089 | 2.328 | 2.0102
17.4459 | 81.2098 | 83.0756 | 78.9475 | 2.209 | 2.328 | 2.0103
17.45 | 81.2088 | 83.0557 | 78.9538 | 2.209 | 2.328 | 2.0103
17.4542 | 81.2138 | 83.0769 | 78.9457 | 2.209 | 2.3283 | 2.0103
17.4584 | 81.2258 | 83.1 | 78.9414 | 2.2091 | 2.3286 | 2.0103
17.4625 | 81.2207 | 83.084 | 78.9453 | 2.2092 | 2.3289 | 2.0103
17.4667 | 81.2159 | 83.0669 | 78.9455 | 2.2093 | 2.3292 | 2.0102
17.4709 | 81.218 | 83.0726 | 78.9475 | 2.2093 | 2.3292 | 2.0103
17.475 | 81.2186 | 83.0786 | 78.9503 | 2.2093 | 2.3293 | 2.0103
17.4792 | 81.2187 | 83.1009 | 78.9431 | 2.2094 | 2.3295 | 2.0103
17.4834 | 81.2189 | 83.124 | 78.9378 | 2.2095 | 2.3298 | 2.0103
17.4875 | 81.2061 | 83.1195 | 78.9472 | 2.2096 | 2.3298 | 2.0103
17.4917 | 81.2002 | 83.114 | 78.9512 | 2.2096 | 2.3299 | 2.0103
17.4959 | 81.2096 | 83.1216 | 78.9451 | 2.2096 | 2.3299 | 2.0103
17.5 | 81.2107 | 83.1294 | 78.9438 | 2.2097 | 2.3298 | 2.0104
17.5042 | 81.2085 | 83.1275 | 78.9423 | 2.2099 | 2.3299 | 2.0103
17.5084 | 81.2024 | 83.1257 | 78.9397 | 2.21 | 2.3301 | 2.0103
17.5125 | 81.1958 | 83.1202 | 78.9472 | 2.21 | 2.33 | 2.0103
17.5167 | 81.2013 | 83.1142 | 78.9519 | 2.21 | 2.33 | 2.0103
17.5209 | 81.2082 | 83.1157 | 78.9435 | 2.2101 | 2.3301 | 2.0103
17.525 | 81.214 | 83.1177 | 78.94 | 2.2102 | 2.3302 | 2.0104
17.5292 | 81.2021 | 83.0966 | 78.9431 | 2.2104 | 2.3304 | 2.0103
17.5334 | 81.1914 | 83.0758 | 78.9431 | 2.2104 | 2.3306 | 2.0103
17.5375 | 81.1995 | 83.0785 | 78.9444 | 2.2104 | 2.3307 | 2.0103
17.5417 | 81.1971 | 83.0807 | 78.9466 | 2.2105 | 2.3307 | 2.0104
17.5459 | 81.2038 | 83.0881 | 78.943 | 2.2106 | 2.331 | 2.0103
17.55 | 81.194 | 83.0968 | 78.9401 | 2.2108 | 2.3313 | 2.0103
17.5542 | 81.1869 | 83.0708 | 78.9445 | 2.2109 | 2.3315 | 2.0103
17.5584 | 81.1813 | 83.0451 | 78.9472 | 2.2109 | 2.3318 | 2.0103
17.5625 | 81.1953 | 83.0565 | 78.942 | 2.211 | 2.3319 | 2.0104
17.5667 | 81.2007 | 83.0663 | 78.9403 | 2.2111 | 2.3321 | 2.0104
17.5709 | 81.1954 | 83.0755 | 78.9426 | 2.2113 | 2.3324 | 2.0103
17.575 | 81.1885 | 83.0852 | 78.9415 | 2.2114 | 2.3328 | 2.0103
17.5792 | 81.1892 | 83.0672 | 78.9434 | 2.2113 | 2.333 | 2.0104
17.5834 | 81.1928 | 83.0489 | 78.9469 | 2.2113 | 2.3332 | 2.0104
17.5875 | 81.2038 | 83.0752 | 78.9413 | 2.2115 | 2.3333 | 2.0104
17.5917 | 81.2052 | 83.101 | 78.9371 | 2.2116 | 2.3334 | 2.0104
17.5959 | 81.1986 | 83.1059 | 78.9434 | 2.2116 | 2.3336 | 2.0104
17.6 | 81.192 | 83.1111 | 78.9454 | 2.2116 | 2.3339 | 2.0103
17.6042 | 81.1979 | 83.1052 | 78.9417 | 2.2116 | 2.3339 | 2.0104
17.6084 | 81.2033 | 83.0983 | 78.9423 | 2.2116 | 2.3338 | 2.0104
17.6125 | 81.2052 | 83.13 | 78.9409 | 2.2117 | 2.3338 | 2.0104
17.6167 | 81.1994 | 83.1632 | 78.9369 | 2.2118 | 2.3337 | 2.0104
17.6209 | 81.1957 | 83.1542 | 78.9428 | 2.2118 | 2.3338 | 2.0104
17.625 | 81.1875 | 83.1455 | 78.9472 | 2.2118 | 2.3338 | 2.0104
17.6292 | 81.1886 | 83.1514 | 78.9405 | 2.2119 | 2.3335 | 2.0104
17.6334 | 81.1862 | 83.156 | 78.9375 | 2.212 | 2.3332 | 2.0104
17.6375 | 81.1782 | 83.1686 | 78.9417 | 2.2121 | 2.3332 | 2.0104
17.6417 | 81.1719 | 83.1823 | 78.9415 | 2.2122 | 2.3332 | 2.0103
17.6459 | 81.172 | 83.1531 | 78.9411 | 2.2123 | 2.3331 | 2.0104
17.65 | 81.1721 | 83.1235 | 78.9445 | 2.2124 | 2.333 | 2.0104
17.6542 | 81.1713 | 83.1429 | 78.9405 | 2.2126 | 2.3327 | 2.0104
17.6584 | 81.1739 | 83.1618 | 78.9358 | 2.2127 | 2.3325 | 2.0104
17.6625 | 81.1734 | 83.1461 | 78.9416 | 2.2127 | 2.3327 | 2.0104
17.6667 | 81.1729 | 83.1311 | 78.9452 | 2.2128 | 2.333 | 2.0104
17.6709 | 81.1825 | 83.1085 | 78.9385 | 2.2129 | 2.3327 | 2.0104
17.675 | 81.1786 | 83.0858 | 78.9381 | 2.213 | 2.3325 | 2.0105
17.6792 | 81.1747 | 83.1221 | 78.9426 | 2.2131 | 2.3326 | 2.0104
17.6834 | 81.177 | 83.1584 | 78.9404 | 2.2131 | 2.3327 | 2.0104
17.6875 | 81.1794 | 83.1128 | 78.9397 | 2.2131 | 2.333 | 2.0105
17.6917 | 81.178 | 83.0669 | 78.9424 | 2.2132 | 2.3334 | 2.0105
17.6959 | 81.1824 | 83.0727 | 78.9364 | 2.2133 | 2.3331 | 2.0104
17.7 | 81.1738 | 83.0784 | 78.9334 | 2.2134 | 2.3328 | 2.0104
17.7042 | 81.1705 | 83.1088 | 78.9448 | 2.2134 | 2.3333 | 2.0104
17.7084 | 81.1781 | 83.1386 | 78.9476 | 2.2135 | 2.3337 | 2.0104
17.7125 | 81.1826 | 83.0758 | 78.9393 | 2.2135 | 2.3339 | 2.0105
17.7167 | 81.1798 | 83.0121 | 78.941 | 2.2136 | 2.3341 | 2.0105
17.7209 | 81.162 | 83.041 | 78.9341 | 2.2138 | 2.3341 | 2.0104
17.725 | 81.1474 | 83.0701 | 78.9231 | 2.2139 | 2.3341 | 2.0105
17.7292 | 81.1573 | 83.0799 | 78.9395 | 2.2138 | 2.3347 | 2.0105
17.7334 | 81.1794 | 83.0892 | 78.9486 | 2.2137 | 2.3353 | 2.0104
17.7375 | 81.2 | 83.053 | 78.9446 | 2.2139 | 2.3354 | 2.0104
17.7417 | 81.2057 | 83.0171 | 78.9518 | 2.2142 | 2.3354 | 2.0105
17.7459 | 81.1854 | 83.0409 | 78.9406 | 2.2143 | 2.3357 | 2.0105
17.75 | 81.1578 | 83.0648 | 78.9261 | 2.2144 | 2.3361 | 2.0104
17.7542 | 81.145 | 83.0235 | 78.9268 | 2.2144 | 2.3367 | 2.0105
17.7584 | 81.151 | 82.9815 | 78.9256 | 2.2145 | 2.3374 | 2.0105
17.7625 | 81.1563 | 83.019 | 78.936 | 2.2145 | 2.3372 | 2.0105
17.7667 | 81.1617 | 83.0582 | 78.9415 | 2.2147 | 2.337 | 2.0105
17.7709 | 81.181 | 83.1023 | 78.9553 | 2.2147 | 2.3377 | 2.0104
17.775 | 81.1908 | 83.1472 | 78.9698 | 2.2146 | 2.3383 | 2.0103
17.7792 | 81.1884 | 83.0315 | 78.9343 | 2.2149 | 2.3388 | 2.0105
17.7834 | 81.1711 | 82.9152 | 78.9173 | 2.2152 | 2.3392 | 2.0107
17.7875 | 81.136 | 82.9638 | 78.9218 | 2.2152 | 2.3391 | 2.0105
17.7917 | 81.1106 | 83.0134 | 78.9104 | 2.2153 | 2.3389 | 2.0104
17.7959 | 81.0957 | 83.0734 | 78.9409 | 2.2154 | 2.3398 | 2.0105
17.8 | 81.1228 | 83.1331 | 78.9594 | 2.2156 | 2.3407 | 2.0106
17.8042 | 81.145 | 83.087 | 78.9425 | 2.2157 | 2.3405 | 2.0105
17.8084 | 81.161 | 83.0411 | 78.9424 | 2.2158 | 2.3404 | 2.0105
17.8125 | 81.1727 | 83.0599 | 78.9424 | 2.2159 | 2.3406 | 2.0104
17.8167 | 81.1868 | 83.0789 | 78.9438 | 2.2158 | 2.3409 | 2.0104
17.8209 | 81.1768 | 83.014 | 78.9298 | 2.216 | 2.3416 | 2.0106
17.825 | 81.1736 | 82.9481 | 78.9178 | 2.2162 | 2.3423 | 2.0107
17.8292 | 81.1412 | 82.9897 | 78.9279 | 2.2163 | 2.3421 | 2.0105
17.8334 | 81.1123 | 83.032 | 78.9292 | 2.2164 | 2.3418 | 2.0104
17.8375 | 81.0929 | 83.0988 | 78.9424 | 2.2165 | 2.3425 | 2.0106
17.8417 | 81.0867 | 83.1646 | 78.9457 | 2.2168 | 2.3432 | 2.0107
17.8459 | 81.1042 | 83.1133 | 78.9342 | 2.2169 | 2.3431 | 2.0106
17.85 | 81.1195 | 83.0617 | 78.9344 | 2.2171 | 2.3429 | 2.0105
17.8542 | 81.1224 | 83.0987 | 78.9415 | 2.2173 | 2.3427 | 2.0105
17.8584 | 81.1428 | 83.1375 | 78.9503 | 2.2174 | 2.3426 | 2.0105
17.8625 | 81.1639 | 83.0993 | 78.9348 | 2.2172 | 2.3431 | 2.0106
17.8667 | 81.1667 | 83.06 | 78.9229 | 2.2173 | 2.3437 | 2.0106
17.8709 | 81.1713 | 83.0686 | 78.9278 | 2.2176 | 2.3432 | 2.0105
17.875 | 81.1461 | 83.0771 | 78.9293 | 2.2178 | 2.3426 | 2.0105
17.8792 | 81.0751 | 83.1868 | 78.9408 | 2.2181 | 2.3426 | 2.0106
17.8834 | 81.0295 | 83.2979 | 78.9369 | 2.2184 | 2.3426 | 2.0107
17.8875 | 81.026 | 83.2915 | 78.9339 | 2.2185 | 2.3421 | 2.0106
17.8917 | 81.0272 | 83.285 | 78.9346 | 2.2188 | 2.3415 | 2.0105
17.8959 | 81.0337 | 83.3169 | 78.9397 | 2.2195 | 2.3403 | 2.0105
17.9 | 81.0636 | 83.3496 | 78.9475 | 2.2199 | 2.3392 | 2.0106
17.9042 | 81.0547 | 83.35 | 78.9382 | 2.2201 | 2.3387 | 2.0106
17.9084 | 81.0832 | 83.3507 | 78.9337 | 2.22 | 2.3382 | 2.0105
17.9125 | 81.1605 | 83.2991 | 78.9344 | 2.22 | 2.3372 | 2.0105
17.9167 | 81.2182 | 83.2467 | 78.9438 | 2.2199 | 2.3362 | 2.0104
17.9209 | 81.245 | 83.2923 | 78.9397 | 2.2203 | 2.3354 | 2.0105
17.925 | 81.2592 | 83.3384 | 78.928 | 2.2207 | 2.3346 | 2.0106
17.9292 | 81.2395 | 83.3461 | 78.9311 | 2.2207 | 2.334 | 2.0105
17.9334 | 81.198 | 83.3539 | 78.9295 | 2.2207 | 2.3334 | 2.0104
17.9375 | 81.1855 | 83.3463 | 78.9413 | 2.2207 | 2.3322 | 2.0105
17.9417 | 81.1693 | 83.3384 | 78.9511 | 2.2205 | 2.3311 | 2.0106
17.9459 | 81.1497 | 83.3077 | 78.9432 | 2.2206 | 2.3307 | 2.0105
17.95 | 81.1332 | 83.2782 | 78.9394 | 2.2208 | 2.3303 | 2.0105
17.9542 | 81.1523 | 83.1254 | 78.9318 | 2.2204 | 2.3305 | 2.0105
17.9584 | 81.1347 | 82.973 | 78.9423 | 2.2204 | 2.3307 | 2.0104
17.9625 | 81.1968 | 82.8755 | 78.9346 | 2.2204 | 2.3314 | 2.0105
17.9667 | 81.2054 | 82.776 | 78.931 | 2.2203 | 2.332 | 2.0105
17.9709 | 81.2343 | 82.7373 | 78.939 | 2.2205 | 2.3338 | 2.0105
17.975 | 81.2667 | 82.6963 | 78.9484 | 2.2205 | 2.3355 | 2.0103
17.9792 | 81.2913 | 82.662 | 78.9416 | 2.2202 | 2.3372 | 2.0105
17.9834 | 81.3297 | 82.626 | 78.9398 | 2.2202 | 2.3389 | 2.0106
17.9875 | 81.3799 | 82.7348 | 78.9337 | 2.2202 | 2.34 | 2.0106
17.9917 | 81.3949 | 82.8424 | 78.9101 | 2.22 | 2.3412 | 2.0105
17.9959 | 81.3727 | 82.9863 | 78.9354 | 2.2201 | 2.342 | 2.0105
18 | 81.3803 | 83.1301 | 78.9427 | 2.2198 | 2.3427 | 2.0105
18.0042 | 81.373 | 83.2368 | 78.9437 | 2.2195 | 2.3421 | 2.0105
18.0084 | 81.3574 | 83.345 | 78.9367 | 2.2194 | 2.3415 | 2.0107
18.0125 | 81.3703 | 83.4175 | 78.9395 | 2.2195 | 2.3405 | 2.0105
18.0167 | 81.3549 | 83.4926 | 78.9405 | 2.2194 | 2.3395 | 2.0104
18.0209 | 81.3441 | 83.4361 | 78.9355 | 2.2192 | 2.3385 | 2.0105
18.025 | 81.3578 | 83.3817 | 78.9417 | 2.219 | 2.3375 | 2.0106
18.0292 | 81.3908 | 83.3305 | 78.9336 | 2.2188 | 2.3363 | 2.0105
18.0334 | 81.4011 | 83.2801 | 78.9282 | 2.2187 | 2.3352 | 2.0105
18.0375 | 81.3934 | 83.2128 | 78.9352 | 2.2188 | 2.3352 | 2.0105
18.0417 | 81.3807 | 83.1453 | 78.9497 | 2.2186 | 2.3352 | 2.0105
18.0459 | 81.3626 | 83.0496 | 78.9353 | 2.2184 | 2.3352 | 2.0105
18.05 | 81.3634 | 82.9528 | 78.9307 | 2.2182 | 2.3353 | 2.0106
18.0542 | 81.3757 | 82.9634 | 78.9392 | 2.2182 | 2.3358 | 2.0105
18.0584 | 81.3732 | 82.9724 | 78.943 | 2.2182 | 2.3362 | 2.0103
18.0625 | 81.3562 | 82.9452 | 78.9376 | 2.2182 | 2.3373 | 2.0105
18.0667 | 81.3436 | 82.9177 | 78.9397 | 2.2182 | 2.3383 | 2.0106
18.0709 | 81.3536 | 82.9453 | 78.9333 | 2.218 | 2.3385 | 2.0105
18.075 | 81.3472 | 82.9729 | 78.9202 | 2.2179 | 2.3386 | 2.0104
18.0792 | 81.3578 | 83.0552 | 78.941 | 2.2181 | 2.3392 | 2.0105
18.0834 | 81.3426 | 83.1374 | 78.9502 | 2.2181 | 2.3398 | 2.0105
18.0875 | 81.3175 | 83.1188 | 78.935 | 2.2182 | 2.3399 | 2.0106
18.0917 | 81.3095 | 83.1008 | 78.9267 | 2.2181 | 2.3399 | 2.0107
18.0959 | 81.3095 | 83.139 | 78.9368 | 2.2178 | 2.3395 | 2.0105
18.1 | 81.3291 | 83.1777 | 78.9383 | 2.2177 | 2.3391 | 2.0104
18.1042 | 81.3705 | 83.1547 | 78.9403 | 2.2176 | 2.3395 | 2.0105
18.1084 | 81.3888 | 83.1326 | 78.9479 | 2.2177 | 2.3399 | 2.0106
18.1125 | 81.3912 | 83.0728 | 78.9306 | 2.2177 | 2.3397 | 2.0105
18.1167 | 81.3827 | 83.0141 | 78.9216 | 2.2177 | 2.3395 | 2.0105
18.1209 | 81.3457 | 83.0345 | 78.9378 | 2.2176 | 2.3399 | 2.0105
18.125 | 81.3339 | 83.0551 | 78.9458 | 2.2176 | 2.3403 | 2.0105
18.1292 | 81.3174 | 83.0108 | 78.935 | 2.2175 | 2.3409 | 2.0106
18.1334 | 81.2927 | 82.9664 | 78.9314 | 2.2176 | 2.3415 | 2.0107
18.1375 | 81.2756 | 82.9774 | 78.9335 | 2.2177 | 2.3417 | 2.0105
18.1417 | 81.2355 | 82.9879 | 78.9314 | 2.2177 | 2.3418 | 2.0104
18.1459 | 81.2162 | 82.9931 | 78.9393 | 2.2176 | 2.3427 | 2.0106
18.15 | 81.2041 | 82.9977 | 78.9456 | 2.2174 | 2.3436 | 2.0106
18.1542 | 81.2062 | 82.963 | 78.9319 | 2.2173 | 2.344 | 2.0106
18.1584 | 81.2227 | 82.929 | 78.9248 | 2.2173 | 2.3443 | 2.0106
18.1625 | 81.2269 | 82.9683 | 78.9363 | 2.2174 | 2.3449 | 2.0105
18.1667 | 81.2379 | 83.0077 | 78.9408 | 2.2175 | 2.3454 | 2.0105
18.1709 | 81.2423 | 82.9915 | 78.9349 | 2.2174 | 2.3461 | 2.0106
18.175 | 81.2502 | 82.9748 | 78.933 | 2.2174 | 2.3468 | 2.0107
18.1792 | 81.2578 | 83.0065 | 78.9334 | 2.2174 | 2.3468 | 2.0105
18.1834 | 81.253 | 83.0385 | 78.9298 | 2.2176 | 2.3467 | 2.0105
18.1875 | 81.2424 | 83.0724 | 78.9374 | 2.2176 | 2.3473 | 2.0106
18.1917 | 81.2297 | 83.1053 | 78.9421 | 2.2176 | 2.3479 | 2.0106
18.1959 | 81.2226 | 83.0887 | 78.9305 | 2.2175 | 2.3477 | 2.0106
18.2 | 81.2182 | 83.0712 | 78.9225 | 2.2175 | 2.3476 | 2.0106
18.2042 | 81.2181 | 83.1414 | 78.9376 | 2.2175 | 2.3473 | 2.0105
18.2084 | 81.2078 | 83.211 | 78.9419 | 2.2176 | 2.347 | 2.0105
18.2125 | 81.2021 | 83.172 | 78.9347 | 2.2176 | 2.3473 | 2.0106
18.2167 | 81.1966 | 83.1326 | 78.9361 | 2.2175 | 2.3476 | 2.0107
18.2209 | 81.2002 | 83.0996 | 78.9307 | 2.2175 | 2.347 | 2.0105
18.225 | 81.2001 | 83.0681 | 78.9285 | 2.2175 | 2.3465 | 2.0105
18.2292 | 81.2002 | 83.0835 | 78.9383 | 2.2176 | 2.3469 | 2.0106
18.2334 | 81.1952 | 83.0995 | 78.9451 | 2.2176 | 2.3474 | 2.0106
18.2375 | 81.1854 | 83.0244 | 78.9286 | 2.2176 | 2.3477 | 2.0106
18.2417 | 81.1826 | 82.9498 | 78.9231 | 2.2176 | 2.348 | 2.0106
18.2459 | 81.1775 | 83.0009 | 78.9357 | 2.2176 | 2.348 | 2.0105
18.25 | 81.1754 | 83.0528 | 78.9387 | 2.2177 | 2.3479 | 2.0105
18.2542 | 81.1647 | 83.0528 | 78.9366 | 2.2177 | 2.3488 | 2.0106
18.2584 | 81.1597 | 83.0516 | 78.9367 | 2.2178 | 2.3497 | 2.0107
18.2625 | 81.1443 | 83.0175 | 78.928 | 2.2178 | 2.3495 | 2.0106
18.2667 | 81.1332 | 82.9834 | 78.9233 | 2.2178 | 2.3493 | 2.0105
18.2709 | 81.1337 | 83.0684 | 78.9399 | 2.2178 | 2.3495 | 2.0106
18.275 | 81.1328 | 83.1536 | 78.944 | 2.2178 | 2.3497 | 2.0106
18.2792 | 81.1337 | 83.1017 | 78.9312 | 2.2179 | 2.3502 | 2.0106
18.2834 | 81.1407 | 83.0489 | 78.9274 | 2.218 | 2.3506 | 2.0107
18.2875 | 81.1334 | 83.0544 | 78.9312 | 2.218 | 2.3501 | 2.0105
18.2917 | 81.1264 | 83.0607 | 78.9331 | 2.2181 | 2.3496 | 2.0105
18.2959 | 81.1331 | 83.1076 | 78.938 | 2.2181 | 2.3501 | 2.0106
18.3 | 81.136 | 83.1538 | 78.9381 | 2.2181 | 2.3506 | 2.0107
18.3042 | 81.1316 | 83.0883 | 78.9284 | 2.2182 | 2.3506 | 2.0106
18.3084 | 81.1344 | 83.0226 | 78.9266 | 2.2183 | 2.3505 | 2.0106
18.3125 | 81.1322 | 83.0652 | 78.936 | 2.2183 | 2.3503 | 2.0106
18.3167 | 81.1236 | 83.109 | 78.9397 | 2.2183 | 2.3501 | 2.0106
18.3209 | 81.1311 | 83.0915 | 78.933 | 2.2184 | 2.3507 | 2.0106
18.325 | 81.133 | 83.0727 | 78.9294 | 2.2185 | 2.3514 | 2.0107
18.3292 | 81.1244 | 83.0356 | 78.9298 | 2.2186 | 2.3511 | 2.0106
18.3334 | 81.1208 | 82.9993 | 78.9322 | 2.2186 | 2.3508 | 2.0105
18.3375 | 81.1262 | 83.0542 | 78.9371 | 2.2186 | 2.3512 | 2.0106
18.3417 | 81.1267 | 83.1099 | 78.9374 | 2.2186 | 2.3515 | 2.0107
18.3459 | 81.1326 | 83.0617 | 78.9298 | 2.2187 | 2.3519 | 2.0106
18.35 | 81.1351 | 83.012 | 78.9268 | 2.2188 | 2.3524 | 2.0106
18.3542 | 81.1291 | 83.0313 | 78.9329 | 2.2188 | 2.3521 | 2.0106
18.3584 | 81.1235 | 83.052 | 78.9364 | 2.2189 | 2.3518 | 2.0106
18.3625 | 81.1274 | 83.0946 | 78.9348 | 2.2189 | 2.3522 | 2.0106
18.3667 | 81.1329 | 83.1365 | 78.9319 | 2.2189 | 2.3527 | 2.0107
18.3709 | 81.1271 | 83.0884 | 78.9304 | 2.219 | 2.3527 | 2.0106
18.375 | 81.1219 | 83.0395 | 78.9307 | 2.2191 | 2.3526 | 2.0106
18.3792 | 81.1217 | 83.0775 | 78.9334 | 2.2191 | 2.3524 | 2.0106
18.3834 | 81.113 | 83.1169 | 78.9347 | 2.2191 | 2.3522 | 2.0106
18.3875 | 81.1207 | 83.1159 | 78.9317 | 2.2192 | 2.3526 | 2.0106
18.3917 | 81.1214 | 83.1136 | 78.9289 | 2.2193 | 2.3529 | 2.0106
18.3959 | 81.1154 | 83.0811 | 78.9328 | 2.2194 | 2.3527 | 2.0106
18.4 | 81.1134 | 83.0494 | 78.9361 | 2.2194 | 2.3525 | 2.0106
18.4042 | 81.1144 | 83.0729 | 78.9322 | 2.2194 | 2.3526 | 2.0106
18.4084 | 81.118 | 83.097 | 78.9306 | 2.2195 | 2.3528 | 2.0107
18.4125 | 81.1193 | 83.0688 | 78.9304 | 2.2196 | 2.3531 | 2.0106
18.4167 | 81.1141 | 83.0393 | 78.9287 | 2.2197 | 2.3533 | 2.0106
18.4209 | 81.1101 | 83.0427 | 78.9335 | 2.2197 | 2.3532 | 2.0106
18.425 | 81.1062 | 83.0478 | 78.9371 | 2.2197 | 2.3532 | 2.0106
18.4292 | 81.1097 | 83.0549 | 78.931 | 2.2198 | 2.3536 | 2.0106
18.4334 | 81.1106 | 83.0625 | 78.9282 | 2.2199 | 2.354 | 2.0107
18.4375 | 81.1086 | 83.036 | 78.9316 | 2.22 | 2.3542 | 2.0106
18.4417 | 81.1053 | 83.0087 | 78.9319 | 2.2201 | 2.3543 | 2.0106
18.4459 | 81.1045 | 83.035 | 78.9323 | 2.2201 | 2.3544 | 2.0106
18.45 | 81.1107 | 83.0613 | 78.9342 | 2.2201 | 2.3546 | 2.0107
18.4542 | 81.111 | 83.053 | 78.93 | 2.2202 | 2.355 | 2.0106
18.4584 | 81.1111 | 83.0443 | 78.9271 | 2.2203 | 2.3553 | 2.0106
18.4625 | 81.1098 | 83.039 | 78.9323 | 2.2204 | 2.3553 | 2.0106
18.4667 | 81.1108 | 83.0337 | 78.9346 | 2.2204 | 2.3553 | 2.0106
18.4709 | 81.1166 | 83.0662 | 78.931 | 2.2204 | 2.3555 | 2.0107
18.475 | 81.1177 | 83.098 | 78.9305 | 2.2205 | 2.3557 | 2.0107
18.4792 | 81.114 | 83.083 | 78.9309 | 2.2205 | 2.3558 | 2.0106
18.4834 | 81.1111 | 83.0677 | 78.9291 | 2.2206 | 2.356 | 2.0106
18.4875 | 81.1114 | 83.08 | 78.9319 | 2.2205 | 2.3558 | 2.0107
18.4917 | 81.1175 | 83.0927 | 78.9344 | 2.2205 | 2.3556 | 2.0107
18.4959 | 81.1237 | 83.1147 | 78.9298 | 2.2206 | 2.3557 | 2.0107
18.5 | 81.1221 | 83.1372 | 78.927 | 2.2207 | 2.3558 | 2.0107
18.5042 | 81.1149 | 83.1226 | 78.9322 | 2.2208 | 2.3556 | 2.0106
18.5084 | 81.1072 | 83.1083 | 78.9329 | 2.2208 | 2.3555 | 2.0106
18.5125 | 81.1079 | 83.1201 | 78.9303 | 2.2208 | 2.3553 | 2.0107
18.5167 | 81.1074 | 83.1317 | 78.9316 | 2.2208 | 2.3551 | 2.0107
18.5209 | 81.1035 | 83.1316 | 78.9299 | 2.2209 | 2.3551 | 2.0106
18.525 | 81.0946 | 83.1325 | 78.9272 | 2.2211 | 2.355 | 2.0106
18.5292 | 81.0869 | 83.1177 | 78.9329 | 2.2211 | 2.3548 | 2.0107
18.5334 | 81.0881 | 83.1024 | 78.936 | 2.2211 | 2.3547 | 2.0106
18.5375 | 81.0922 | 83.1034 | 78.9282 | 2.2212 | 2.3547 | 2.0107
18.5417 | 81.1 | 83.104 | 78.926 | 2.2213 | 2.3546 | 2.0107
18.5459 | 81.0961 | 83.0946 | 78.9306 | 2.2214 | 2.3546 | 2.0106
18.55 | 81.0917 | 83.0864 | 78.9311 | 2.2215 | 2.3547 | 2.0106
18.5542 | 81.0937 | 83.0831 | 78.9329 | 2.2215 | 2.3547 | 2.0107
18.5584 | 81.1031 | 83.0785 | 78.9357 | 2.2215 | 2.3546 | 2.0107
18.5625 | 81.1048 | 83.0752 | 78.9283 | 2.2216 | 2.3548 | 2.0107
18.5667 | 81.1078 | 83.0722 | 78.9244 | 2.2218 | 2.3549 | 2.0107
18.5709 | 81.0954 | 83.0579 | 78.9289 | 2.2218 | 2.355 | 2.0107
18.575 | 81.0856 | 83.0444 | 78.9283 | 2.2218 | 2.3552 | 2.0107
18.5792 | 81.0992 | 83.061 | 78.9312 | 2.2218 | 2.3552 | 2.0107
18.5834 | 81.1149 | 83.0756 | 78.9365 | 2.2217 | 2.3552 | 2.0106
18.5875 | 81.1165 | 83.0655 | 78.9343 | 2.2219 | 2.3555 | 2.0107
18.5917 | 81.1161 | 83.056 | 78.9331 | 2.2221 | 2.3558 | 2.0107
18.5959 | 81.0943 | 83.0243 | 78.9263 | 2.2222 | 2.356 | 2.0107
18.6 | 81.0719 | 82.992 | 78.9203 | 2.2222 | 2.3561 | 2.0107
18.6042 | 81.0736 | 83.022 | 78.9237 | 2.2223 | 2.3563 | 2.0107
18.6084 | 81.0836 | 83.0508 | 78.9238 | 2.2223 | 2.3565 | 2.0107
18.6125 | 81.0939 | 83.0562 | 78.9375 | 2.2224 | 2.3568 | 2.0107
18.6167 | 81.1011 | 83.0635 | 78.9463 | 2.2224 | 2.3572 | 2.0106
18.6209 | 81.1141 | 83.0306 | 78.9352 | 2.2224 | 2.3573 | 2.0107
18.625 | 81.1086 | 82.9969 | 78.9378 | 2.2225 | 2.3575 | 2.0107
18.6292 | 81.1019 | 82.9866 | 78.9198 | 2.2227 | 2.3579 | 2.0107
18.6334 | 81.077 | 82.9757 | 78.8997 | 2.2228 | 2.3583 | 2.0108
18.6375 | 81.0654 | 82.9952 | 78.9245 | 2.2229 | 2.3586 | 2.0107
18.6417 | 81.0697 | 83.0163 | 78.9342 | 2.2228 | 2.3589 | 2.0106
18.6459 | 81.0778 | 83.0501 | 78.9385 | 2.2228 | 2.359 | 2.0107
18.65 | 81.0963 | 83.0838 | 78.9495 | 2.223 | 2.3592 | 2.0108
18.6542 | 81.1181 | 83.0527 | 78.934 | 2.223 | 2.3596 | 2.0107
18.6584 | 81.1095 | 83.023 | 78.9273 | 2.223 | 2.3599 | 2.0106
18.6625 | 81.1184 | 82.9703 | 78.9225 | 2.2232 | 2.3603 | 2.0107
18.6667 | 81.0986 | 82.9177 | 78.9195 | 2.2233 | 2.3606 | 2.0108
18.6709 | 81.0683 | 82.9777 | 78.9223 | 2.2234 | 2.3607 | 2.0107
18.675 | 81.0417 | 83.0368 | 78.9137 | 2.2235 | 2.3608 | 2.0107
18.6792 | 81.0454 | 83.0692 | 78.9347 | 2.2235 | 2.3613 | 2.0107
18.6834 | 81.0563 | 83.1029 | 78.9494 | 2.2236 | 2.3618 | 2.0106
18.6875 | 81.0779 | 83.0543 | 78.9318 | 2.2238 | 2.3618 | 2.0107
18.6917 | 81.076 | 83.0053 | 78.9295 | 2.224 | 2.3618 | 2.0108
18.6959 | 81.0876 | 83.0205 | 78.9272 | 2.224 | 2.3619 | 2.0107
18.7 | 81.0885 | 83.0355 | 78.9251 | 2.2238 | 2.362 | 2.0105
18.7042 | 81.1025 | 83.0025 | 78.9289 | 2.2239 | 2.3627 | 2.0107
18.7084 | 81.102 | 82.9703 | 78.931 | 2.2241 | 2.3633 | 2.0108
18.7125 | 81.0938 | 82.9885 | 78.9223 | 2.2242 | 2.3632 | 2.0107
18.7167 | 81.0553 | 83.0045 | 78.9113 | 2.2244 | 2.363 | 2.0107
18.7209 | 81.0356 | 83.0771 | 78.9326 | 2.2244 | 2.3633 | 2.0107
18.725 | 81.0365 | 83.1496 | 78.9413 | 2.2246 | 2.3637 | 2.0107
18.7292 | 81.0266 | 83.1032 | 78.9303 | 2.2246 | 2.3637 | 2.0108
18.7334 | 81.0397 | 83.0581 | 78.9291 | 2.2249 | 2.3637 | 2.0108
18.7375 | 81.0518 | 83.0786 | 78.927 | 2.2251 | 2.3633 | 2.0107
18.7417 | 81.0649 | 83.098 | 78.9301 | 2.225 | 2.3629 | 2.0106
18.7459 | 81.071 | 83.0896 | 78.9312 | 2.2251 | 2.3634 | 2.0107
18.75 | 81.088 | 83.0813 | 78.93 | 2.2252 | 2.3639 | 2.0108
18.7542 | 81.0805 | 83.076 | 78.9222 | 2.2253 | 2.3634 | 2.0107
18.7584 | 81.0648 | 83.0708 | 78.9164 | 2.2255 | 2.3628 | 2.0107
18.7625 | 81.0328 | 83.1758 | 78.9331 | 2.2256 | 2.3625 | 2.0107
18.7667 | 81.0113 | 83.2805 | 78.9364 | 2.2258 | 2.3622 | 2.0107
18.7709 | 80.9912 | 83.2672 | 78.9288 | 2.226 | 2.3619 | 2.0108
18.775 | 80.979 | 83.2555 | 78.9212 | 2.2263 | 2.3615 | 2.0108
18.7792 | 80.9609 | 83.28 | 78.9255 | 2.2268 | 2.3602 | 2.0107
18.7834 | 80.9554 | 83.3051 | 78.9343 | 2.2272 | 2.3588 | 2.0106
18.7875 | 80.9448 | 83.3173 | 78.9362 | 2.2275 | 2.3585 | 2.0107
18.7917 | 80.9503 | 83.3295 | 78.9384 | 2.2278 | 2.3581 | 2.0108
18.7959 | 81.0107 | 83.2487 | 78.924 | 2.2279 | 2.3573 | 2.0107
18.8 | 81.0543 | 83.169 | 78.9221 | 2.2279 | 2.3564 | 2.0106
18.8042 | 81.0851 | 83.2164 | 78.9273 | 2.228 | 2.3556 | 2.0107
18.8084 | 81.1217 | 83.2629 | 78.9276 | 2.2281 | 2.3548 | 2.0107
18.8125 | 81.1389 | 83.2634 | 78.9303 | 2.2281 | 2.3546 | 2.0108
18.8167 | 81.1508 | 83.2633 | 78.9239 | 2.2282 | 2.3544 | 2.0107
18.8209 | 81.1555 | 83.2315 | 78.9309 | 2.2283 | 2.3534 | 2.0107
18.825 | 81.1725 | 83.2009 | 78.9423 | 2.2282 | 2.3525 | 2.0106
18.8292 | 81.1382 | 83.1772 | 78.9328 | 2.2284 | 2.3525 | 2.0107
18.8334 | 81.1538 | 83.1546 | 78.9257 | 2.2285 | 2.3525 | 2.0108
18.8375 | 81.1136 | 83.0186 | 78.9203 | 2.2284 | 2.353 | 2.0107
18.8417 | 81.0924 | 82.8833 | 78.9222 | 2.2286 | 2.3534 | 2.0106
18.8459 | 81.075 | 82.8291 | 78.9304 | 2.2285 | 2.3541 | 2.0107
18.85 | 81.0505 | 82.7725 | 78.9443 | 2.2284 | 2.3547 | 2.0107
18.8542 | 81.035 | 82.7378 | 78.9335 | 2.2285 | 2.3565 | 2.0108
18.8584 | 81.0518 | 82.7006 | 78.9275 | 2.2285 | 2.3583 | 2.0107
18.8625 | 81.0492 | 82.6674 | 78.9249 | 2.2283 | 2.3597 | 2.0107
18.8667 | 81.0623 | 82.6317 | 78.9268 | 2.2284 | 2.361 | 2.0106
18.8709 | 81.094 | 82.7762 | 78.9304 | 2.2283 | 2.3619 | 2.0107
18.875 | 81.1198 | 82.9171 | 78.9172 | 2.2282 | 2.3628 | 2.0108
18.8792 | 81.1245 | 83.0439 | 78.931 | 2.2284 | 2.3633 | 2.0107
18.8834 | 81.1537 | 83.1705 | 78.9281 | 2.2286 | 2.3639 | 2.0106
18.8875 | 81.1464 | 83.2463 | 78.9327 | 2.2284 | 2.363 | 2.0107
18.8917 | 81.1461 | 83.3213 | 78.9348 | 2.2285 | 2.3621 | 2.0108
18.8959 | 81.1616 | 83.3978 | 78.931 | 2.2285 | 2.361 | 2.0107
18.9 | 81.1695 | 83.4752 | 78.921 | 2.2283 | 2.3599 | 2.0107
18.9042 | 81.1787 | 83.4097 | 78.9277 | 2.2284 | 2.359 | 2.0107
18.9084 | 81.2056 | 83.3481 | 78.9405 | 2.2284 | 2.358 | 2.0107
18.9125 | 81.2202 | 83.2731 | 78.9263 | 2.2282 | 2.357 | 2.0107
18.9167 | 81.228 | 83.1981 | 78.9225 | 2.2284 | 2.3559 | 2.0108
18.9209 | 81.2482 | 83.1466 | 78.9261 | 2.2284 | 2.3559 | 2.0107
18.925 | 81.2484 | 83.0955 | 78.9303 | 2.2284 | 2.3559 | 2.0106
18.9292 | 81.2457 | 82.9952 | 78.9298 | 2.2284 | 2.3563 | 2.0107
18.9334 | 81.2563 | 82.8939 | 78.9401 | 2.2283 | 2.3566 | 2.0108
18.9375 | 81.2575 | 82.8938 | 78.9276 | 2.2282 | 2.3571 | 2.0107
18.9417 | 81.2715 | 82.8902 | 78.9184 | 2.2282 | 2.3575 | 2.0107
18.9459 | 81.2598 | 82.8992 | 78.9294 | 2.2282 | 2.3586 | 2.0107
18.95 | 81.2703 | 82.9082 | 78.9373 | 2.2281 | 2.3597 | 2.0106
18.9542 | 81.2841 | 82.9223 | 78.9296 | 2.2279 | 2.36 | 2.0107
18.9584 | 81.2865 | 82.935 | 78.9222 | 2.2279 | 2.3603 | 2.0108
18.9625 | 81.283 | 83.0241 | 78.9289 | 2.2279 | 2.3606 | 2.0107
18.9667 | 81.2706 | 83.1127 | 78.9251 | 2.2279 | 2.3609 | 2.0106
18.9709 | 81.2321 | 83.106 | 78.9305 | 2.228 | 2.3611 | 2.0107
18.975 | 81.2128 | 83.1019 | 78.9351 | 2.2279 | 2.3614 | 2.0108
18.9792 | 81.2126 | 83.1158 | 78.9288 | 2.2276 | 2.3608 | 2.0107
18.9834 | 81.2118 | 83.1296 | 78.9213 | 2.2275 | 2.3603 | 2.0107
18.9875 | 81.2474 | 83.1283 | 78.9298 | 2.2275 | 2.3606 | 2.0107
18.9917 | 81.2565 | 83.1291 | 78.938 | 2.2275 | 2.3609 | 2.0107
18.9959 | 81.2689 | 83.0467 | 78.9262 | 2.2276 | 2.3609 | 2.0107
19 | 81.2841 | 82.9662 | 78.9238 | 2.2275 | 2.3609 | 2.0108
19.0042 | 81.2892 | 82.9931 | 78.9284 | 2.2274 | 2.361 | 2.0107
19.0084 | 81.3088 | 83.0189 | 78.927 | 2.2272 | 2.361 | 2.0106
19.0125 | 81.3235 | 82.9883 | 78.929 | 2.2271 | 2.3619 | 2.0107
19.0167 | 81.3187 | 82.9582 | 78.9347 | 2.2269 | 2.3628 | 2.0108
19.0209 | 81.3086 | 82.9352 | 78.9259 | 2.2268 | 2.3629 | 2.0107
19.025 | 81.2791 | 82.9105 | 78.9187 | 2.2267 | 2.3629 | 2.0107
19.0292 | 81.265 | 82.9634 | 78.9318 | 2.2267 | 2.3636 | 2.0107
19.0334 | 81.2471 | 83.0156 | 78.9374 | 2.2267 | 2.3643 | 2.0107
19.0375 | 81.2398 | 82.9597 | 78.9258 | 2.2266 | 2.365 | 2.0108
19.0417 | 81.2281 | 82.904 | 78.9243 | 2.2266 | 2.3657 | 2.0108
19.0459 | 81.222 | 82.9429 | 78.9272 | 2.2266 | 2.3657 | 2.0107
19.05 | 81.2161 | 82.9808 | 78.923 | 2.2266 | 2.3656 | 2.0106
19.0542 | 81.2121 | 83.0163 | 78.9322 | 2.2265 | 2.3665 | 2.0107
19.0584 | 81.2162 | 83.052 | 78.9387 | 2.2264 | 2.3673 | 2.0108
19.0625 | 81.2245 | 83.0116 | 78.9236 | 2.2264 | 2.3673 | 2.0107
19.0667 | 81.2318 | 82.9699 | 78.9167 | 2.2264 | 2.3673 | 2.0108
19.0709 | 81.2346 | 83.0438 | 78.9305 | 2.2265 | 2.3673 | 2.0107
19.075 | 81.2345 | 83.1173 | 78.9325 | 2.2265 | 2.3672 | 2.0106
19.0792 | 81.2273 | 83.1124 | 78.9286 | 2.2265 | 2.3676 | 2.0108
19.0834 | 81.2319 | 83.1056 | 78.9281 | 2.2264 | 2.368 | 2.0109
19.0875 | 81.234 | 83.1074 | 78.9249 | 2.2263 | 2.3673 | 2.0107
19.0917 | 81.2374 | 83.1073 | 78.9207 | 2.2264 | 2.3667 | 2.0107
19.0959 | 81.2348 | 83.137 | 78.9324 | 2.2265 | 2.3668 | 2.0107
19.1 | 81.2302 | 83.1681 | 78.9397 | 2.2264 | 2.367 | 2.0107
19.1042 | 81.226 | 83.0897 | 78.9237 | 2.2263 | 2.367 | 2.0108
19.1084 | 81.2298 | 83.0105 | 78.92 | 2.2263 | 2.367 | 2.0108
19.1125 | 81.2377 | 83.0197 | 78.9275 | 2.2262 | 2.3668 | 2.0107
19.1167 | 81.2358 | 83.0313 | 78.9306 | 2.2263 | 2.3666 | 2.0106
19.1209 | 81.2411 | 83.0199 | 78.9296 | 2.2263 | 2.3673 | 2.0108
19.125 | 81.239 | 83.0105 | 78.9314 | 2.2263 | 2.3681 | 2.0108
19.1292 | 81.2431 | 82.9829 | 78.924 | 2.2262 | 2.368 | 2.0107
19.1334 | 81.248 | 82.9538 | 78.9202 | 2.2262 | 2.368 | 2.0107
19.1375 | 81.2511 | 82.9992 | 78.9309 | 2.2262 | 2.3684 | 2.0107
19.1417 | 81.2423 | 83.0467 | 78.935 | 2.2263 | 2.3689 | 2.0107
19.1459 | 81.2372 | 83.0326 | 78.926 | 2.2263 | 2.3692 | 2.0108
19.15 | 81.2241 | 83.0167 | 78.9209 | 2.2263 | 2.3695 | 2.0108
19.1542 | 81.2195 | 83.0459 | 78.9283 | 2.2262 | 2.3693 | 2.0107
19.1584 | 81.2188 | 83.0739 | 78.9298 | 2.2262 | 2.3691 | 2.0107
19.1625 | 81.2148 | 83.0762 | 78.9291 | 2.2262 | 2.3696 | 2.0108
19.1667 | 81.2086 | 83.08 | 78.9301 | 2.2263 | 2.37 | 2.0108
19.1709 | 81.2018 | 83.0609 | 78.924 | 2.2262 | 2.3697 | 2.0107
19.175 | 81.1903 | 83.0388 | 78.92 | 2.2262 | 2.3695 | 2.0107
19.1792 | 81.1855 | 83.0774 | 78.9312 | 2.2262 | 2.3695 | 2.0107
19.1834 | 81.1845 | 83.1173 | 78.9356 | 2.2261 | 2.3696 | 2.0107
19.1875 | 81.1795 | 83.0759 | 78.9251 | 2.2262 | 2.3699 | 2.0108
19.1917 | 81.1777 | 83.0347 | 78.9226 | 2.2262 | 2.3701 | 2.0108
19.1959 | 81.1702 | 83.0428 | 78.9268 | 2.2262 | 2.3698 | 2.0107
19.2 | 81.1603 | 83.0495 | 78.9271 | 2.2262 | 2.3695 | 2.0107
19.2042 | 81.1543 | 83.0592 | 78.9297 | 2.2262 | 2.37 | 2.0108
19.2084 | 81.1532 | 83.0713 | 78.9319 | 2.2262 | 2.3705 | 2.0108
19.2125 | 81.1452 | 83.0315 | 78.9236 | 2.2262 | 2.3705 | 2.0107
19.2167 | 81.1432 | 82.9904 | 78.9211 | 2.2263 | 2.3704 | 2.0107
19.2209 | 81.1365 | 83.0281 | 78.9304 | 2.2262 | 2.3705 | 2.0107
19.225 | 81.1289 | 83.0665 | 78.9325 | 2.2262 | 2.3706 | 2.0107
19.2292 | 81.1286 | 83.0425 | 78.9254 | 2.2262 | 2.3711 | 2.0108
19.2334 | 81.1258 | 83.0194 | 78.9242 | 2.2262 | 2.3716 | 2.0108
19.2375 | 81.1226 | 83.0307 | 78.9261 | 2.2262 | 2.3713 | 2.0107
19.2417 | 81.1205 | 83.0404 | 78.926 | 2.2263 | 2.371 | 2.0107
19.2459 | 81.1137 | 83.0775 | 78.9312 | 2.2263 | 2.3714 | 2.0108
19.25 | 81.1136 | 83.1159 | 78.932 | 2.2262 | 2.3717 | 2.0108
19.2542 | 81.1086 | 83.0677 | 78.9223 | 2.2263 | 2.3717 | 2.0108
19.2584 | 81.1067 | 83.0179 | 78.9204 | 2.2263 | 2.3718 | 2.0108
19.2625 | 81.1015 | 83.0652 | 78.9291 | 2.2263 | 2.3714 | 2.0107
19.2667 | 81.0923 | 83.1126 | 78.9303 | 2.2264 | 2.3711 | 2.0107
19.2709 | 81.0892 | 83.1045 | 78.9284 | 2.2264 | 2.3716 | 2.0108
19.275 | 81.0873 | 83.0972 | 78.9284 | 2.2263 | 2.3721 | 2.0108
19.2792 | 81.0809 | 83.0498 | 78.9235 | 2.2264 | 2.3718 | 2.0107
19.2834 | 81.0812 | 83.0013 | 78.9232 | 2.2264 | 2.3714 | 2.0107
19.2875 | 81.0736 | 83.0512 | 78.9299 | 2.2264 | 2.3715 | 2.0108
19.2917 | 81.0715 | 83.1027 | 78.9302 | 2.2264 | 2.3717 | 2.0108
19.2959 | 81.0679 | 83.0591 | 78.9249 | 2.2264 | 2.3721 | 2.0108
19.3 | 81.0656 | 83.0145 | 78.9245 | 2.2265 | 2.3725 | 2.0108
19.3042 | 81.058 | 83.0105 | 78.9264 | 2.2265 | 2.3723 | 2.0107
19.3084 | 81.0521 | 83.0079 | 78.9273 | 2.2266 | 2.372 | 2.0107
19.3125 | 81.0508 | 83.0404 | 78.9287 | 2.2265 | 2.3725 | 2.0108
19.3167 | 81.0481 | 83.0744 | 78.9281 | 2.2266 | 2.3731 | 2.0108
19.3209 | 81.049 | 83.0285 | 78.9243 | 2.2267 | 2.3732 | 2.0108
19.325 | 81.049 | 82.9797 | 78.9242 | 2.2267 | 2.3733 | 2.0108
19.3292 | 81.0397 | 83.0156 | 78.9283 | 2.2268 | 2.3733 | 2.0108
19.3334 | 81.0417 | 83.0534 | 78.9291 | 2.2268 | 2.3732 | 2.0108
19.3375 | 81.049 | 83.0525 | 78.9261 | 2.2268 | 2.3738 | 2.0108
19.3417 | 81.0533 | 83.0509 | 78.9249 | 2.2269 | 2.3743 | 2.0108
19.3459 | 81.0543 | 83.0341 | 78.9256 | 2.227 | 2.3741 | 2.0108
19.35 | 81.0523 | 83.0153 | 78.9263 | 2.227 | 2.3739 | 2.0107
19.3542 | 81.0471 | 83.0623 | 78.9284 | 2.227 | 2.3741 | 2.0108
19.3584 | 81.0479 | 83.1109 | 78.9289 | 2.227 | 2.3742 | 2.0108
19.3625 | 81.0522 | 83.0812 | 78.9246 | 2.2271 | 2.3744 | 2.0108
19.3667 | 81.0514 | 83.049 | 78.9232 | 2.2271 | 2.3746 | 2.0108
19.3709 | 81.0476 | 83.0687 | 78.9273 | 2.2272 | 2.3742 | 2.0108
19.375 | 81.049 | 83.0894 | 78.9285 | 2.2272 | 2.3738 | 2.0107
19.3792 | 81.0526 | 83.1152 | 78.9272 | 2.2272 | 2.374 | 2.0108
19.3834 | 81.0583 | 83.1416 | 78.9264 | 2.2272 | 2.3743 | 2.0108
19.3875 | 81.0584 | 83.1026 | 78.9245 | 2.2273 | 2.3741 | 2.0108
19.3917 | 81.056 | 83.0613 | 78.9233 | 2.2273 | 2.3738 | 2.0108
19.3959 | 81.0518 | 83.0984 | 78.9278 | 2.2273 | 2.3735 | 2.0108
19.4 | 81.0464 | 83.1381 | 78.9303 | 2.2273 | 2.3732 | 2.0108
19.4042 | 81.049 | 83.125 | 78.9264 | 2.2274 | 2.3734 | 2.0108
19.4084 | 81.0449 | 83.1106 | 78.9243 | 2.2275 | 2.3736 | 2.0108
19.4125 | 81.0352 | 83.0798 | 78.9254 | 2.2275 | 2.3733 | 2.0108
19.4167 | 81.0334 | 83.0482 | 78.9258 | 2.2276 | 2.3729 | 2.0107
19.4209 | 81.0325 | 83.0779 | 78.9255 | 2.2276 | 2.373 | 2.0108
19.425 | 81.0337 | 83.1104 | 78.9259 | 2.2277 | 2.3731 | 2.0108
19.4292 | 81.0396 | 83.0843 | 78.9275 | 2.2278 | 2.3732 | 2.0108
19.4334 | 81.0428 | 83.0558 | 78.929 | 2.2278 | 2.3733 | 2.0107
19.4375 | 81.0372 | 83.0463 | 78.9279 | 2.2279 | 2.3732 | 2.0108
19.4417 | 81.0343 | 83.0377 | 78.928 | 2.2279 | 2.3731 | 2.0108
19.4459 | 81.0341 | 83.0458 | 78.921 | 2.228 | 2.3734 | 2.0108
19.45 | 81.0291 | 83.0556 | 78.9162 | 2.228 | 2.3736 | 2.0108
19.4542 | 81.0285 | 83.0465 | 78.9269 | 2.2281 | 2.3737 | 2.0108
19.4584 | 81.0328 | 83.035 | 78.9307 | 2.2282 | 2.3737 | 2.0107
19.4625 | 81.0441 | 83.0497 | 78.932 | 2.2281 | 2.3738 | 2.0108
19.4667 | 81.0544 | 83.0658 | 78.9375 | 2.2281 | 2.3739 | 2.0108
19.4709 | 81.0589 | 83.0352 | 78.9237 | 2.2282 | 2.3742 | 2.0108
19.475 | 81.0552 | 83.0041 | 78.917 | 2.2284 | 2.3746 | 2.0108
19.4792 | 81.0302 | 82.9949 | 78.9197 | 2.2285 | 2.3747 | 2.0108
19.4834 | 81.0107 | 82.9841 | 78.9121 | 2.2285 | 2.3747 | 2.0108
19.4875 | 81.0208 | 83.0349 | 78.928 | 2.2285 | 2.3749 | 2.0108
19.4917 | 81.0409 | 83.088 | 78.9412 | 2.2284 | 2.3751 | 2.0107
19.4959 | 81.0465 | 83.0574 | 78.9341 | 2.2286 | 2.3755 | 2.0108
19.5 | 81.0596 | 83.0257 | 78.9347 | 2.2288 | 2.3758 | 2.0108
19.5042 | 81.0582 | 82.9888 | 78.9221 | 2.2287 | 2.3759 | 2.0108
19.5084 | 81.0439 | 82.9512 | 78.9152 | 2.2287 | 2.376 | 2.0107
19.5125 | 81.0417 | 82.9722 | 78.9179 | 2.2289 | 2.3764 | 2.0108
19.5167 | 81.031 | 82.9951 | 78.913 | 2.2289 | 2.3769 | 2.0109
19.5209 | 81.0057 | 83.0262 | 78.9295 | 2.229 | 2.377 | 2.0108
19.525 | 81.0048 | 83.0564 | 78.9342 | 2.2289 | 2.3772 | 2.0107
19.5292 | 81.0221 | 83.058 | 78.932 | 2.229 | 2.3774 | 2.0108
19.5334 | 81.0423 | 83.0603 | 78.9429 | 2.2289 | 2.3776 | 2.0108
19.5375 | 81.0556 | 83.0092 | 78.9224 | 2.2291 | 2.3779 | 2.0108
19.5417 | 81.0628 | 82.9592 | 78.9097 | 2.2293 | 2.3782 | 2.0108
19.5459 | 81.0554 | 82.9697 | 78.9227 | 2.2293 | 2.3784 | 2.0108
19.55 | 81.0425 | 82.9796 | 78.9259 | 2.2293 | 2.3785 | 2.0107
19.5542 | 81.0263 | 83.0167 | 78.9252 | 2.2294 | 2.3789 | 2.0108
19.5584 | 81.0146 | 83.0545 | 78.9228 | 2.2295 | 2.3793 | 2.0109
19.5625 | 81.0036 | 83.0546 | 78.9261 | 2.2294 | 2.3794 | 2.0108
19.5667 | 81.0091 | 83.0544 | 78.926 | 2.2295 | 2.3794 | 2.0107
19.5709 | 81.0138 | 83.0512 | 78.9292 | 2.2297 | 2.3796 | 2.0108
19.575 | 81.0135 | 83.0477 | 78.9379 | 2.2297 | 2.3797 | 2.0109
19.5792 | 81.0152 | 83.0264 | 78.9225 | 2.2298 | 2.3799 | 2.0108
19.5834 | 81.02 | 83.0059 | 78.9148 | 2.2297 | 2.3801 | 2.0108
19.5875 | 81.0409 | 82.9971 | 78.9251 | 2.2297 | 2.3803 | 2.0108
19.5917 | 81.0397 | 82.9873 | 78.9294 | 2.2298 | 2.3806 | 2.0107
19.5959 | 81.0476 | 83.0169 | 78.9244 | 2.23 | 2.3807 | 2.0108
19.6 | 81.0136 | 83.0455 | 78.9171 | 2.2302 | 2.3809 | 2.0109
19.6042 | 80.9929 | 83.0814 | 78.9251 | 2.2303 | 2.3809 | 2.0108
19.6084 | 80.9875 | 83.1185 | 78.9268 | 2.2302 | 2.3809 | 2.0107
19.6125 | 80.9907 | 83.1077 | 78.9299 | 2.2303 | 2.3809 | 2.0108
19.6167 | 80.9934 | 83.096 | 78.9353 | 2.2305 | 2.3809 | 2.0109
19.6209 | 81.0102 | 83.093 | 78.921 | 2.2306 | 2.3806 | 2.0108
19.625 | 81.0028 | 83.0893 | 78.915 | 2.2307 | 2.3804 | 2.0108
19.6292 | 81.0008 | 83.0963 | 78.9268 | 2.2308 | 2.3804 | 2.0108
19.6334 | 81.0112 | 83.104 | 78.9347 | 2.2308 | 2.3805 | 2.0107
19.6375 | 81.0173 | 83.109 | 78.9261 | 2.2308 | 2.3802 | 2.0108
19.6417 | 81.0059 | 83.1124 | 78.919 | 2.231 | 2.3799 | 2.0109
19.6459 | 80.999 | 83.1752 | 78.9231 | 2.2311 | 2.3794 | 2.0108
19.65 | 80.9907 | 83.2383 | 78.9211 | 2.2312 | 2.3789 | 2.0107
19.6542 | 80.9588 | 83.2543 | 78.9283 | 2.2314 | 2.3784 | 2.0108
19.6584 | 80.948 | 83.2704 | 78.9287 | 2.2317 | 2.378 | 2.0109
19.6625 | 80.93 | 83.2774 | 78.9238 | 2.232 | 2.3769 | 2.0108
19.6667 | 80.9061 | 83.2829 | 78.9244 | 2.2322 | 2.3758 | 2.0107
19.6709 | 80.9064 | 83.2788 | 78.9297 | 2.2326 | 2.3753 | 2.0107
19.675 | 80.917 | 83.2764 | 78.9381 | 2.2329 | 2.3747 | 2.0108
19.6792 | 80.9282 | 83.2059 | 78.9214 | 2.2332 | 2.3742 | 2.0108
19.6834 | 80.9361 | 83.1354 | 78.9131 | 2.2335 | 2.3736 | 2.0109
19.6875 | 80.9589 | 83.1646 | 78.9209 | 2.2337 | 2.3729 | 2.0108
19.6917 | 80.9548 | 83.1933 | 78.9251 | 2.2338 | 2.3721 | 2.0107
19.6959 | 80.9851 | 83.1936 | 78.9337 | 2.2338 | 2.3721 | 2.0108
19.7 | 81.0005 | 83.1954 | 78.9354 | 2.2338 | 2.3721 | 2.0109
19.7042 | 81.0424 | 83.1385 | 78.9233 | 2.2338 | 2.3716 | 2.0108
19.7084 | 81.0517 | 83.0826 | 78.9195 | 2.2338 | 2.3711 | 2.0107
19.7125 | 81.0859 | 83.0674 | 78.9242 | 2.2339 | 2.3712 | 2.0108
19.7167 | 81.1085 | 83.0551 | 78.9263 | 2.2338 | 2.3713 | 2.0108
19.7209 | 81.1204 | 82.9623 | 78.9247 | 2.2339 | 2.372 | 2.0108
19.725 | 81.128 | 82.8708 | 78.9232 | 2.2341 | 2.3727 | 2.0108
19.7292 | 81.1314 | 82.8175 | 78.9245 | 2.2341 | 2.3734 | 2.0108
19.7334 | 81.1038 | 82.7641 | 78.937 | 2.2341 | 2.374 | 2.0107
19.7375 | 81.0968 | 82.7386 | 78.9283 | 2.2342 | 2.3757 | 2.0108
19.7417 | 81.0797 | 82.7142 | 78.9243 | 2.2341 | 2.3773 | 2.0109
19.7459 | 81.0622 | 82.7128 | 78.9211 | 2.2341 | 2.3784 | 2.0108
19.75 | 81.0503 | 82.7098 | 78.9172 | 2.2342 | 2.3796 | 2.0107
19.7542 | 81.0558 | 82.8536 | 78.9285 | 2.234 | 2.3802 | 2.0108
19.7584 | 81.0372 | 82.9975 | 78.9292 | 2.234 | 2.3809 | 2.0108
19.7625 | 81.045 | 83.0979 | 78.9286 | 2.2342 | 2.3812 | 2.0108
19.7667 | 81.0432 | 83.1966 | 78.9151 | 2.2341 | 2.3815 | 2.0108
19.7709 | 81.0195 | 83.2743 | 78.926 | 2.2342 | 2.3804 | 2.0108
19.775 | 81.0066 | 83.3474 | 78.931 | 2.2344 | 2.3793 | 2.0107
19.7792 | 80.9991 | 83.4071 | 78.9303 | 2.2342 | 2.3783 | 2.0108
19.7834 | 80.981 | 83.4672 | 78.9257 | 2.2341 | 2.3773 | 2.0109
19.7875 | 80.9802 | 83.3808 | 78.9219 | 2.2343 | 2.3763 | 2.0108
19.7917 | 80.9915 | 83.2941 | 78.9225 | 2.2342 | 2.3752 | 2.0107
19.7959 | 80.986 | 83.2307 | 78.9237 | 2.2343 | 2.3743 | 2.0108
19.8 | 80.987 | 83.1677 | 78.9325 | 2.2345 | 2.3733 | 2.0109
19.8042 | 81.003 | 83.102 | 78.9253 | 2.2343 | 2.3735 | 2.0108
19.8084 | 80.9984 | 83.0399 | 78.9209 | 2.2344 | 2.3737 | 2.0108
19.8125 | 81.016 | 82.9401 | 78.9225 | 2.2345 | 2.3741 | 2.0108
19.8167 | 81.0104 | 82.8396 | 78.9338 | 2.2345 | 2.3745 | 2.0107
19.8209 | 81.0024 | 82.8513 | 78.9259 | 2.2346 | 2.3751 | 2.0108
19.825 | 81.0115 | 82.8643 | 78.9224 | 2.2345 | 2.3757 | 2.0109
19.8292 | 81.0328 | 82.8792 | 78.9258 | 2.2342 | 2.3768 | 2.0108
19.8334 | 81.048 | 82.8952 | 78.9244 | 2.2343 | 2.3779 | 2.0107
19.8375 | 81.0913 | 82.9168 | 78.9255 | 2.2344 | 2.3782 | 2.0108
19.8417 | 81.1048 | 82.9355 | 78.9289 | 2.2344 | 2.3786 | 2.0109
19.8459 | 81.1108 | 83.0233 | 78.9262 | 2.2346 | 2.3788 | 2.0108
19.85 | 81.1246 | 83.1121 | 78.9148 | 2.2345 | 2.379 | 2.0108
19.8542 | 81.1055 | 83.119 | 78.9277 | 2.2346 | 2.3791 | 2.0108
19.8584 | 81.1066 | 83.125 | 78.9337 | 2.2347 | 2.3793 | 2.0108
19.8625 | 81.0971 | 83.122 | 78.925 | 2.2346 | 2.3788 | 2.0108
19.8667 | 81.0894 | 83.1173 | 78.9221 | 2.2345 | 2.3783 | 2.0109
19.8709 | 81.0936 | 83.1173 | 78.9252 | 2.2345 | 2.3784 | 2.0108
19.875 | 81.0962 | 83.1207 | 78.9237 | 2.2345 | 2.3785 | 2.0107
19.8792 | 81.0951 | 83.0491 | 78.9257 | 2.2345 | 2.3786 | 2.0108
19.8834 | 81.1159 | 82.9774 | 78.9334 | 2.2344 | 2.3787 | 2.0108
19.8875 | 81.125 | 82.9779 | 78.9226 | 2.2343 | 2.3788 | 2.0108
19.8917 | 81.1571 | 82.9791 | 78.9157 | 2.2343 | 2.3788 | 2.0108
19.8959 | 81.1757 | 82.9721 | 78.9267 | 2.2343 | 2.3796 | 2.0108
19.9 | 81.194 | 82.9672 | 78.9316 | 2.2344 | 2.3804 | 2.0107
19.9042 | 81.2001 | 82.938 | 78.9252 | 2.2344 | 2.3807 | 2.0108
19.9084 | 81.2092 | 82.9068 | 78.9252 | 2.2343 | 2.381 | 2.0109
19.9125 | 81.2122 | 82.9476 | 78.924 | 2.2342 | 2.3814 | 2.0108
19.9167 | 81.2207 | 82.9898 | 78.9198 | 2.2342 | 2.3819 | 2.0107
19.9209 | 81.2218 | 82.9695 | 78.9267 | 2.2342 | 2.3826 | 2.0108
19.925 | 81.2094 | 82.949 | 78.9324 | 2.2341 | 2.3833 | 2.0108
19.9292 | 81.1995 | 82.9716 | 78.924 | 2.2341 | 2.3833 | 2.0108
19.9334 | 81.1967 | 82.9927 | 78.9179 | 2.234 | 2.3832 | 2.0108
19.9375 | 81.1924 | 83.0322 | 78.9265 | 2.234 | 2.3838 | 2.0108
19.9417 | 81.1882 | 83.0734 | 78.9297 | 2.234 | 2.3843 | 2.0107
19.9459 | 81.1883 | 83.0346 | 78.9247 | 2.234 | 2.3844 | 2.0108
19.95 | 81.1819 | 82.9939 | 78.9253 | 2.2339 | 2.3845 | 2.0109
19.9542 | 81.1841 | 83.0545 | 78.9244 | 2.2339 | 2.3842 | 2.0108
19.9584 | 81.1827 | 83.1151 | 78.9184 | 2.2339 | 2.3839 | 2.0107
19.9625 | 81.1819 | 83.1236 | 78.9272 | 2.2339 | 2.3843 | 2.0108
19.9667 | 81.1787 | 83.1311 | 78.9326 | 2.2339 | 2.3846 | 2.0108
19.9709 | 81.1801 | 83.1062 | 78.9231 | 2.2338 | 2.3841 | 2.0108
19.975 | 81.1815 | 83.0786 | 78.9183 | 2.2338 | 2.3835 | 2.0109
19.9792 | 81.1822 | 83.1179 | 78.9268 | 2.2338 | 2.3834 | 2.0108
19.9834 | 81.1811 | 83.1583 | 78.9294 | 2.2338 | 2.3834 | 2.0107
19.9875 | 81.1706 | 83.0806 | 78.9238 | 2.2339 | 2.3837 | 2.0108
19.9917 | 81.1672 | 83.0015 | 78.9267 | 2.2338 | 2.384 | 2.0109
19.9959 | 81.1622 | 83.0029 | 78.923 | 2.2337 | 2.3836 | 2.0108
20 | 81.1635 | 83.0063 | 78.9192 | 2.2337 | 2.3832 | 2.0107
20.0042 | 81.1644 | 83.0206 | 78.9281 | 2.2337 | 2.384 | 2.0108
20.0084 | 81.0536 | 82.9747 | 78.8025 | 2.2328 | 2.3843 | 2.0097
20.0125 | 80.9032 | 82.7845 | 78.5292 | 2.2316 | 2.3834 | 2.0076
20.0167 | 80.6939 | 82.5527 | 78.1981 | 2.2291 | 2.3819 | 2.0043
20.0209 | 80.4638 | 82.4246 | 77.8216 | 2.2263 | 2.3795 | 1.9996
20.025 | 80.224 | 82.2947 | 77.443 | 2.2238 | 2.3772 | 1.9954
20.0292 | 79.9846 | 82.0697 | 77.0721 | 2.2213 | 2.3757 | 1.9918
20.0334 | 79.6736 | 81.8048 | 76.633 | 2.2188 | 2.3742 | 1.9882
20.0375 | 79.3463 | 81.4915 | 76.1139 | 2.2164 | 2.3716 | 1.9845
20.0417 | 79.0673 | 81.198 | 75.6514 | 2.2139 | 2.3689 | 1.9808
20.0459 | 78.8008 | 81.0136 | 75.2581 | 2.2114 | 2.3669 | 1.9771
20.05 | 78.5346 | 80.8373 | 74.8658 | 2.2094 | 2.3652 | 1.974
20.0542 | 78.2761 | 80.5437 | 74.4656 | 2.2077 | 2.3637 | 1.9714
20.0584 | 77.9961 | 80.2374 | 74.0529 | 2.2056 | 2.3621 | 1.9686
20.0625 | 77.7215 | 80.0042 | 73.6295 | 2.2036 | 2.3598 | 1.9654
20.0667 | 77.4956 | 79.7992 | 73.2548 | 2.2017 | 2.3576 | 1.9624
20.0709 | 77.2843 | 79.6043 | 72.9324 | 2.1998 | 2.3564 | 1.9597
20.075 | 77.0467 | 79.3993 | 72.5862 | 2.1982 | 2.3554 | 1.9571
20.0792 | 76.8022 | 79.1225 | 72.207 | 2.1965 | 2.3536 | 1.9546
20.0834 | 76.5615 | 78.8448 | 71.8412 | 2.1947 | 2.3518 | 1.9519
20.0875 | 76.3278 | 78.6747 | 71.4983 | 2.1927 | 2.35 | 1.949
20.0917 | 76.122 | 78.5213 | 71.1759 | 2.1909 | 2.3484 | 1.9463
20.0959 | 75.9169 | 78.286 | 70.8673 | 2.1893 | 2.3474 | 1.944
20.1 | 75.6894 | 78.0345 | 70.5398 | 2.1877 | 2.3463 | 1.9416
20.1042 | 75.4505 | 77.8049 | 70.1922 | 2.186 | 2.3444 | 1.9391
20.1084 | 75.2297 | 77.5864 | 69.8691 | 2.1843 | 2.3425 | 1.9366
20.1125 | 75.0302 | 77.4321 | 69.5772 | 2.1825 | 2.3412 | 1.9341
20.1167 | 74.8298 | 77.2819 | 69.2862 | 2.1809 | 2.3401 | 1.9318
20.1209 | 74.6304 | 77.0419 | 68.9879 | 2.1795 | 2.3387 | 1.9297
20.125 | 74.4172 | 76.792 | 68.6844 | 2.1779 | 2.3372 | 1.9275
20.1292 | 74.1959 | 76.6125 | 68.3815 | 2.1763 | 2.3354 | 1.9252
20.1334 | 74.0037 | 76.4474 | 68.0996 | 2.1747 | 2.3337 | 1.9229
20.1375 | 73.8218 | 76.2669 | 67.8373 | 2.1731 | 2.3325 | 1.9208
20.1417 | 73.6341 | 76.0804 | 67.5684 | 2.1716 | 2.3314 | 1.9188
20.1459 | 73.4336 | 75.8635 | 67.2915 | 2.1702 | 2.3296 | 1.9168
20.15 | 73.2313 | 75.6465 | 67.0187 | 2.1688 | 2.3278 | 1.9147
20.1542 | 73.036 | 75.4728 | 66.7565 | 2.1672 | 2.3264 | 1.9127
20.1584 | 72.8576 | 75.3093 | 66.5079 | 2.1657 | 2.3251 | 1.9107
20.1625 | 72.6894 | 75.0961 | 66.2646 | 2.1643 | 2.3238 | 1.9088
20.1667 | 72.5092 | 74.874 | 66.0159 | 2.163 | 2.3225 | 1.907
20.1709 | 72.3129 | 74.6923 | 65.7663 | 2.1617 | 2.3209 | 1.9051
20.175 | 72.1288 | 74.518 | 65.5248 | 2.1603 | 2.3193 | 1.9033
20.1792 | 71.9559 | 74.3308 | 65.2935 | 2.1588 | 2.3183 | 1.9015
20.1834 | 71.7899 | 74.1467 | 65.0696 | 2.1575 | 2.3174 | 1.8997
20.1875 | 71.6246 | 73.948 | 64.8454 | 2.1563 | 2.316 | 1.898
20.1917 | 71.4436 | 73.7454 | 64.6185 | 2.1551 | 2.3146 | 1.8964
20.1959 | 71.2639 | 73.5948 | 64.3965 | 2.1538 | 2.3134 | 1.8947
20.2 | 71.0934 | 73.453 | 64.1835 | 2.1525 | 2.3123 | 1.893
20.2042 | 70.9366 | 73.2546 | 63.9756 | 2.1512 | 2.3113 | 1.8914
20.2084 | 70.7844 | 73.0522 | 63.7713 | 2.1501 | 2.3103 | 1.8898
20.2125 | 70.6176 | 72.892 | 63.5674 | 2.149 | 2.3089 | 1.8883
20.2167 | 70.4516 | 72.7337 | 63.3633 | 2.1479 | 2.3074 | 1.8868
20.2209 | 70.2977 | 72.585 | 63.1658 | 2.1466 | 2.3064 | 1.8853
20.225 | 70.1495 | 72.441 | 62.9766 | 2.1454 | 2.3056 | 1.8838
20.2292 | 70.0054 | 72.2514 | 62.7893 | 2.1443 | 2.3043 | 1.8823
20.2334 | 69.8558 | 72.0564 | 62.6025 | 2.1432 | 2.303 | 1.881
20.2375 | 69.6937 | 71.926 | 62.4186 | 2.1421 | 2.3016 | 1.8796
20.2417 | 69.5346 | 71.8014 | 62.2374 | 2.141 | 2.3003 | 1.8782
20.2459 | 69.3969 | 71.6344 | 62.0608 | 2.1398 | 2.2992 | 1.8768
20.25 | 69.2586 | 71.4672 | 61.8912 | 2.1387 | 2.2983 | 1.8755
20.2542 | 69.1148 | 71.3069 | 61.7343 | 2.1378 | 2.2967 | 1.8743
20.2584 | 68.9712 | 71.1453 | 61.5918 | 2.1368 | 2.2951 | 1.8733
20.2625 | 68.8217 | 71.0149 | 61.4597 | 2.1357 | 2.294 | 1.8724
20.2667 | 68.6903 | 70.8902 | 61.3418 | 2.1346 | 2.2929 | 1.8717
20.2709 | 68.5602 | 70.7097 | 61.2254 | 2.1335 | 2.2916 | 1.8709
20.275 | 68.4344 | 70.5265 | 61.1119 | 2.1326 | 2.2904 | 1.8702
20.2792 | 68.2945 | 70.3993 | 61.0097 | 2.1316 | 2.2889 | 1.8694
20.2834 | 68.1515 | 70.275 | 60.9138 | 2.1306 | 2.2873 | 1.8686
20.2875 | 68.0187 | 70.1109 | 60.8089 | 2.1296 | 2.2865 | 1.8679
20.2917 | 67.8877 | 69.9485 | 60.7048 | 2.1286 | 2.2856 | 1.8672
20.2959 | 67.7582 | 69.7757 | 60.6035 | 2.1277 | 2.2842 | 1.8664
20.3 | 67.63 | 69.6013 | 60.4994 | 2.1268 | 2.2827 | 1.8656
20.3042 | 67.5027 | 69.4969 | 60.4061 | 2.1259 | 2.2817 | 1.8648
20.3084 | 67.3783 | 69.3969 | 60.3133 | 2.125 | 2.2806 | 1.864
20.3125 | 67.2651 | 69.2084 | 60.2064 | 2.124 | 2.2798 | 1.8633
20.3167 | 67.1512 | 69.0182 | 60.1021 | 2.1231 | 2.279 | 1.8625
20.3209 | 67.0173 | 68.8677 | 59.9978 | 2.1224 | 2.2777 | 1.8617
20.325 | 66.8856 | 68.7186 | 59.8951 | 2.1216 | 2.2764 | 1.861
20.3292 | 66.7605 | 68.6152 | 59.8031 | 2.1207 | 2.2757 | 1.8602
20.3334 | 66.6441 | 68.5147 | 59.7072 | 2.1198 | 2.275 | 1.8595
20.3375 | 66.5424 | 68.3526 | 59.6183 | 2.119 | 2.274 | 1.8587
20.3417 | 66.4478 | 68.1884 | 59.5293 | 2.1182 | 2.273 | 1.858
20.3459 | 66.3287 | 68.052 | 59.4229 | 2.1174 | 2.272 | 1.8573
20.35 | 66.2114 | 67.9187 | 59.3264 | 2.1166 | 2.271 | 1.8566
20.3542 | 66.1017 | 67.7652 | 59.2273 | 2.1157 | 2.2704 | 1.8559
20.3584 | 65.9875 | 67.6107 | 59.1281 | 2.1149 | 2.2698 | 1.8551
20.3625 | 65.8677 | 67.4896 | 59.0504 | 2.1142 | 2.2688 | 1.8545
20.3667 | 65.7501 | 67.3684 | 58.9606 | 2.1136 | 2.2677 | 1.8538
20.3709 | 65.6453 | 67.2832 | 58.8762 | 2.1127 | 2.2669 | 1.8531
20.375 | 65.5542 | 67.1988 | 58.7973 | 2.1118 | 2.2661 | 1.8523
20.3792 | 65.4702 | 66.9806 | 58.693 | 2.1111 | 2.2654 | 1.8517
20.3834 | 65.3858 | 66.7602 | 58.6013 | 2.1105 | 2.2647 | 1.8511
20.3875 | 65.2728 | 66.5922 | 58.5099 | 2.1097 | 2.2633 | 1.8504
20.3917 | 65.1496 | 66.4276 | 58.4136 | 2.1089 | 2.2619 | 1.8497
20.3959 | 65.0415 | 66.3348 | 58.3436 | 2.1082 | 2.2611 | 1.8491
20.4 | 64.9418 | 66.2438 | 58.2666 | 2.1074 | 2.2604 | 1.8484
20.4042 | 64.8338 | 66.0607 | 58.179 | 2.1069 | 2.2594 | 1.8478
20.4084 | 64.7295 | 65.8807 | 58.0918 | 2.1063 | 2.2584 | 1.8472
20.4125 | 64.6489 | 65.7323 | 58.007 | 2.1056 | 2.2572 | 1.8465
20.4167 | 64.563 | 65.5881 | 57.9307 | 2.1048 | 2.256 | 1.8458
20.4209 | 64.4849 | 65.4232 | 57.8419 | 2.1042 | 2.2555 | 1.8453
20.425 | 64.4098 | 65.2597 | 57.7579 | 2.1036 | 2.255 | 1.8448
20.4292 | 64.3081 | 65.1119 | 57.6793 | 2.1028 | 2.2539 | 1.8441
20.4334 | 64.1991 | 64.9676 | 57.5936 | 2.1021 | 2.2528 | 1.8434
20.4375 | 64.1082 | 64.881 | 57.5218 | 2.1015 | 2.2521 | 1.8429
20.4417 | 64.0244 | 64.7962 | 57.4498 | 2.1008 | 2.2514 | 1.8423
20.4459 | 63.9173 | 64.6522 | 57.366 | 2.1002 | 2.2506 | 1.8417
20.45 | 63.8275 | 64.5092 | 57.2812 | 2.0997 | 2.2498 | 1.8411
20.4542 | 63.7312 | 64.3856 | 57.2121 | 2.0991 | 2.2488 | 1.8405
20.4584 | 63.645 | 64.2655 | 57.1458 | 2.0984 | 2.2477 | 1.8398
20.4625 | 63.5704 | 64.1257 | 57.0577 | 2.0979 | 2.2472 | 1.8394
20.4667 | 63.5047 | 63.9864 | 56.9794 | 2.0973 | 2.2468 | 1.8389
20.4709 | 63.4286 | 63.8567 | 56.9071 | 2.0968 | 2.2459 | 1.8382
20.475 | 63.3371 | 63.7283 | 56.8284 | 2.0962 | 2.245 | 1.8376
20.4792 | 63.2531 | 63.6613 | 56.7643 | 2.0956 | 2.2443 | 1.8371
20.4834 | 63.1621 | 63.5978 | 56.6976 | 2.095 | 2.2436 | 1.8366
20.4875 | 63.0729 | 63.4914 | 56.6169 | 2.0945 | 2.2428 | 1.836
20.4917 | 62.9946 | 63.3859 | 56.5366 | 2.094 | 2.242 | 1.8355
20.4959 | 62.9199 | 63.2872 | 56.476 | 2.0935 | 2.2409 | 1.8349
20.5 | 62.8404 | 63.1901 | 56.4123 | 2.093 | 2.2399 | 1.8344
20.5042 | 62.7612 | 63.0908 | 56.3334 | 2.0926 | 2.2391 | 1.8339
20.5084 | 62.6831 | 62.9937 | 56.2629 | 2.0921 | 2.2383 | 1.8335
20.5125 | 62.6105 | 62.8872 | 56.196 | 2.0915 | 2.2373 | 1.8328
20.5167 | 62.5384 | 62.7812 | 56.1285 | 2.091 | 2.2363 | 1.8322
20.5209 | 62.4799 | 62.7096 | 56.0627 | 2.0905 | 2.2354 | 1.8318
20.525 | 62.4059 | 62.6409 | 55.9968 | 2.0901 | 2.2344 | 1.8314
20.5292 | 62.315 | 62.5807 | 55.9214 | 2.0897 | 2.2333 | 1.8308
20.5334 | 62.2344 | 62.5156 | 55.8449 | 2.0892 | 2.2321 | 1.8303
20.5375 | 62.1431 | 62.463 | 55.7984 | 2.0888 | 2.2308 | 1.8298
20.5417 | 62.0575 | 62.4127 | 55.7412 | 2.0885 | 2.2294 | 1.8293
20.5459 | 61.9893 | 62.3275 | 55.6681 | 2.0882 | 2.2281 | 1.8289
20.55 | 61.9118 | 62.2347 | 55.6027 | 2.0879 | 2.2268 | 1.8285
20.5542 | 61.8336 | 62.119 | 55.5326 | 2.0877 | 2.2255 | 1.8279
20.5584 | 61.7801 | 62.0058 | 55.4693 | 2.0874 | 2.2243 | 1.8273
20.5625 | 61.7143 | 61.9011 | 55.411 | 2.0871 | 2.2233 | 1.827
20.5667 | 61.6525 | 61.7974 | 55.3508 | 2.0868 | 2.2223 | 1.8266
20.5709 | 61.5835 | 61.722 | 55.2861 | 2.0867 | 2.2214 | 1.826
20.575 | 61.5126 | 61.6449 | 55.2238 | 2.0863 | 2.2204 | 1.8255
20.5792 | 61.4377 | 61.5528 | 55.1696 | 2.086 | 2.2198 | 1.8251
20.5834 | 61.3787 | 61.4663 | 55.115 | 2.0857 | 2.2192 | 1.8246
20.5875 | 61.3343 | 61.3495 | 55.0441 | 2.0854 | 2.2186 | 1.8243
20.5917 | 61.2658 | 61.2324 | 54.976 | 2.085 | 2.2181 | 1.8238
20.5959 | 61.2169 | 61.1452 | 54.9239 | 2.0847 | 2.2177 | 1.8233
20.6 | 61.1739 | 61.0601 | 54.8681 | 2.0841 | 2.2173 | 1.8228
20.6042 | 61.1268 | 60.9283 | 54.8129 | 2.0836 | 2.2176 | 1.8225
20.6084 | 61.0788 | 60.8 | 54.7576 | 2.0831 | 2.2179 | 1.8221
20.6125 | 61.0302 | 60.6669 | 54.6859 | 2.0826 | 2.2181 | 1.8216
20.6167 | 60.9612 | 60.5329 | 54.6262 | 2.0821 | 2.2183 | 1.821
20.6209 | 60.8887 | 60.4578 | 54.5726 | 2.0815 | 2.219 | 1.8206
20.625 | 60.8296 | 60.3878 | 54.5211 | 2.081 | 2.2198 | 1.8202
20.6292 | 60.7695 | 60.338 | 54.4566 | 2.0805 | 2.2203 | 1.8198
20.6334 | 60.7161 | 60.2927 | 54.3923 | 2.08 | 2.2208 | 1.8194
20.6375 | 60.6641 | 60.3328 | 54.34 | 2.0796 | 2.2206 | 1.8189
20.6417 | 60.5983 | 60.3806 | 54.2847 | 2.0791 | 2.2205 | 1.8185
20.6459 | 60.5501 | 60.4334 | 54.2363 | 2.0786 | 2.2201 | 1.8181
20.65 | 60.4979 | 60.4917 | 54.1764 | 2.0781 | 2.2197 | 1.8178
20.6542 | 60.4396 | 60.5133 | 54.1225 | 2.0777 | 2.2185 | 1.8173
20.6584 | 60.3805 | 60.533 | 54.0645 | 2.0774 | 2.2172 | 1.8169
20.6625 | 60.3116 | 60.5242 | 54.0166 | 2.077 | 2.2159 | 1.8165
20.6667 | 60.2399 | 60.5173 | 53.9685 | 2.0766 | 2.2146 | 1.8162
20.6709 | 60.1924 | 60.4173 | 53.9111 | 2.0762 | 2.2134 | 1.8158
20.675 | 60.1532 | 60.3136 | 53.8533 | 2.0758 | 2.2123 | 1.8154
20.6792 | 60.0955 | 60.2153 | 53.8057 | 2.0756 | 2.2114 | 1.815
20.6834 | 60.0511 | 60.1154 | 53.7638 | 2.0754 | 2.2104 | 1.8146
20.6875 | 60.0033 | 60.0031 | 53.7084 | 2.075 | 2.2105 | 1.8143
20.6917 | 59.9408 | 59.8925 | 53.6587 | 2.0746 | 2.2106 | 1.814
20.6959 | 59.8941 | 59.7828 | 53.6012 | 2.0744 | 2.2108 | 1.8135
20.7 | 59.8454 | 59.6711 | 53.5533 | 2.0741 | 2.211 | 1.813
20.7042 | 59.7597 | 59.6476 | 53.5099 | 2.0739 | 2.2115 | 1.8128
20.7084 | 59.7023 | 59.6278 | 53.4696 | 2.0737 | 2.2121 | 1.8124
20.7125 | 59.6724 | 59.5974 | 53.4076 | 2.0734 | 2.2127 | 1.8121
20.7167 | 59.6226 | 59.5682 | 53.3531 | 2.0731 | 2.2134 | 1.8117
20.7209 | 59.6111 | 59.5769 | 53.3143 | 2.0729 | 2.2135 | 1.8113
20.725 | 59.5757 | 59.5851 | 53.2728 | 2.0727 | 2.2135 | 1.8109
20.7292 | 59.5194 | 59.6236 | 53.2274 | 2.0723 | 2.2135 | 1.8107
20.7334 | 59.4805 | 59.6654 | 53.1782 | 2.0719 | 2.2135 | 1.8105
20.7375 | 59.4501 | 59.6335 | 53.132 | 2.0714 | 2.2131 | 1.8101
20.7417 | 59.4053 | 59.5984 | 53.0842 | 2.0711 | 2.2128 | 1.8097
20.7459 | 59.3567 | 59.574 | 53.0482 | 2.0709 | 2.2122 | 1.8094
20.75 | 59.2921 | 59.5498 | 53.011 | 2.0706 | 2.2115 | 1.8091
20.7542 | 59.2327 | 59.4971 | 52.9613 | 2.0702 | 2.2114 | 1.8088
20.7584 | 59.1775 | 59.4464 | 52.9127 | 2.0699 | 2.2112 | 1.8085
20.7625 | 59.1417 | 59.3537 | 52.8733 | 2.0697 | 2.211 | 1.8082
20.7667 | 59.0973 | 59.2584 | 52.8374 | 2.0696 | 2.2108 | 1.8078
20.7709 | 59.0431 | 59.2262 | 52.7943 | 2.0694 | 2.2108 | 1.8076
20.775 | 59.0066 | 59.1972 | 52.7533 | 2.0692 | 2.2108 | 1.8073
20.7792 | 58.9765 | 59.1515 | 52.7119 | 2.0688 | 2.2112 | 1.807
20.7834 | 58.9538 | 59.106 | 52.6682 | 2.0686 | 2.2116 | 1.8066
20.7875 | 58.9242 | 59.0532 | 52.6312 | 2.0684 | 2.2118 | 1.8064
20.7917 | 58.8921 | 58.9987 | 52.5992 | 2.0681 | 2.2119 | 1.8061
20.7959 | 58.8471 | 58.9983 | 52.5543 | 2.0677 | 2.2121 | 1.8058
20.8 | 58.8123 | 59.0014 | 52.5083 | 2.0673 | 2.2123 | 1.8056
20.8042 | 58.7849 | 58.9727 | 52.4773 | 2.0669 | 2.2126 | 1.8053
20.8084 | 58.7424 | 58.9421 | 52.4422 | 2.0666 | 2.2129 | 1.8049
20.8125 | 58.6932 | 58.9238 | 52.4013 | 2.0663 | 2.2127 | 1.8047
20.8167 | 58.6531 | 58.9057 | 52.366 | 2.0659 | 2.2125 | 1.8045
20.8209 | 58.6128 | 58.9026 | 52.328 | 2.0655 | 2.2126 | 1.8042
20.825 | 58.5774 | 58.9023 | 52.2858 | 2.0652 | 2.2126 | 1.8039
20.8292 | 58.5456 | 58.8567 | 52.2551 | 2.065 | 2.2125 | 1.8037
20.8334 | 58.5007 | 58.8081 | 52.2262 | 2.0647 | 2.2124 | 1.8034
20.8375 | 58.4543 | 58.8096 | 52.1826 | 2.0645 | 2.2119 | 1.8032
20.8417 | 58.421 | 58.8127 | 52.141 | 2.0641 | 2.2114 | 1.803
20.8459 | 58.3958 | 58.8038 | 52.1155 | 2.0638 | 2.2113 | 1.8027
20.85 | 58.3584 | 58.7942 | 52.0818 | 2.0636 | 2.2112 | 1.8023
20.8542 | 58.3263 | 58.7382 | 52.0447 | 2.0634 | 2.2107 | 1.8022
20.8584 | 58.2911 | 58.6786 | 52.0142 | 2.0631 | 2.2103 | 1.802
20.8625 | 58.2539 | 58.6641 | 51.9765 | 2.0627 | 2.2099 | 1.8017
20.8667 | 58.2754 | 58.6774 | 51.9923 | 2.0621 | 2.2093 | 1.801
20.8709 | 58.3066 | 58.6679 | 52.0769 | 2.0613 | 2.209 | 1.7999
20.875 | 58.4317 | 58.7176 | 52.2851 | 2.0598 | 2.2082 | 1.7978
20.8792 | 58.5914 | 58.838 | 52.5938 | 2.0579 | 2.2065 | 1.7949
20.8834 | 58.778 | 58.9685 | 52.9215 | 2.0552 | 2.2044 | 1.7913
20.8875 | 58.9667 | 59.1442 | 53.2629 | 2.0523 | 2.2023 | 1.7869
20.8917 | 59.0817 | 59.2775 | 53.5063 | 2.0486 | 2.1998 | 1.7818
20.8959 | 59.1641 | 59.3218 | 53.6617 | 2.0447 | 2.1965 | 1.776
20.9 | 59.2176 | 59.3499 | 53.8086 | 2.0402 | 2.193 | 1.7698
20.9042 | 59.2644 | 59.4369 | 53.9415 | 2.0354 | 2.1887 | 1.763
20.9084 | 59.2695 | 59.4939 | 54.0245 | 2.031 | 2.1845 | 1.7568
20.9125 | 59.2567 | 59.4795 | 54.0754 | 2.0267 | 2.1809 | 1.751
20.9167 | 59.1963 | 59.4372 | 54.0792 | 2.0224 | 2.1774 | 1.7451
20.9209 | 59.1192 | 59.342 | 54.0286 | 2.0181 | 2.1732 | 1.7392
20.925 | 59.0885 | 59.2701 | 54.0389 | 2.014 | 2.1691 | 1.7336
20.9292 | 59.0724 | 59.3012 | 54.11 | 2.0101 | 2.1654 | 1.7281
20.9334 | 59.0346 | 59.3237 | 54.1444 | 2.0067 | 2.162 | 1.7232
20.9375 | 58.9994 | 59.2355 | 54.1495 | 2.0034 | 2.1592 | 1.7188
20.9417 | 58.9634 | 59.1508 | 54.1617 | 1.9999 | 2.1563 | 1.7141
20.9459 | 58.9342 | 59.1186 | 54.1679 | 1.9964 | 2.1525 | 1.709
20.95 | 58.95 | 59.1126 | 54.2185 | 1.9932 | 2.1489 | 1.7043
20.9542 | 58.9767 | 59.158 | 54.3228 | 1.99 | 2.1463 | 1.6999
20.9584 | 58.9537 | 59.1814 | 54.3689 | 1.9869 | 2.1438 | 1.6956
20.9625 | 58.9253 | 59.0955 | 54.3537 | 1.9839 | 2.1409 | 1.6915
20.9667 | 58.9227 | 59.0214 | 54.3737 | 1.9805 | 2.1379 | 1.6871
20.9709 | 58.9204 | 59.0622 | 54.425 | 1.9771 | 2.1345 | 1.6823
20.975 | 58.935 | 59.1103 | 54.4785 | 1.9742 | 2.1313 | 1.678
20.9792 | 58.9436 | 59.0979 | 54.5409 | 1.9713 | 2.1291 | 1.6743
20.9834 | 58.9082 | 59.0614 | 54.5612 | 1.9682 | 2.1268 | 1.6703
20.9875 | 58.8716 | 59.0047 | 54.5319 | 1.9652 | 2.1235 | 1.6662
20.9917 | 58.8726 | 58.97 | 54.5514 | 1.962 | 2.1201 | 1.662
20.9959 | 58.8906 | 59.0405 | 54.6258 | 1.9589 | 2.1173 | 1.6579
21 | 58.8798 | 59.1028 | 54.6685 | 1.9562 | 2.1147 | 1.6541
21.0042 | 58.8699 | 59.0311 | 54.6777 | 1.9536 | 2.1123 | 1.6507
21.0084 | 58.8402 | 58.9488 | 54.681 | 1.9506 | 2.1098 | 1.6471
21.0125 | 58.8126 | 58.9551 | 54.6746 | 1.9476 | 2.1063 | 1.643
21.0167 | 58.8239 | 58.9835 | 54.7023 | 1.9448 | 2.1029 | 1.6393
21.0209 | 58.8413 | 59.0259 | 54.7723 | 1.942 | 2.1006 | 1.6359
21.025 | 58.8207 | 59.0486 | 54.7985 | 1.9395 | 2.0985 | 1.6325
21.0292 | 58.7879 | 58.9551 | 54.7749 | 1.9369 | 2.0956 | 1.6293
21.0334 | 58.7739 | 58.8677 | 54.7754 | 1.9341 | 2.0926 | 1.6259
21.0375 | 58.7635 | 58.9156 | 54.8016 | 1.9313 | 2.0895 | 1.6222
21.0417 | 58.7697 | 58.9743 | 54.8331 | 1.9288 | 2.0866 | 1.6189
21.0459 | 58.7772 | 58.9485 | 54.872 | 1.9264 | 2.0846 | 1.616
21.05 | 58.7537 | 58.9015 | 54.88 | 1.9239 | 2.0826 | 1.6129
21.0542 | 58.7105 | 58.8383 | 54.8525 | 1.9214 | 2.0796 | 1.6098
21.0584 | 58.7107 | 58.7928 | 54.8586 | 1.9188 | 2.0765 | 1.6066
21.0625 | 58.715 | 58.8478 | 54.9026 | 1.9162 | 2.0742 | 1.6034
21.0667 | 58.709 | 58.8997 | 54.928 | 1.9139 | 2.072 | 1.6005
21.0709 | 58.7028 | 58.836 | 54.9321 | 1.9117 | 2.0699 | 1.5979
21.075 | 58.6746 | 58.7615 | 54.9288 | 1.9093 | 2.0677 | 1.5951
21.0792 | 58.64 | 58.7605 | 54.9181 | 1.9069 | 2.0649 | 1.592
21.0834 | 58.6403 | 58.7782 | 54.9315 | 1.9046 | 2.0621 | 1.5892
21.0875 | 58.6509 | 58.8018 | 54.9706 | 1.9023 | 2.0602 | 1.5865
21.0917 | 58.6388 | 58.8111 | 54.9835 | 1.9002 | 2.0584 | 1.5839
21.0959 | 58.6188 | 58.7548 | 54.9669 | 1.8981 | 2.0559 | 1.5814
21.1 | 58.602 | 58.7008 | 54.9613 | 1.8958 | 2.0533 | 1.5788
21.1042 | 58.589 | 58.7398 | 54.9708 | 1.8935 | 2.0508 | 1.5761
21.1084 | 58.5927 | 58.7885 | 54.9865 | 1.8914 | 2.0485 | 1.5735
21.1125 | 58.5994 | 58.7663 | 55.0014 | 1.8893 | 2.0465 | 1.5713
21.1167 | 58.5791 | 58.7278 | 54.9904 | 1.8873 | 2.0446 | 1.5691
21.1209 | 58.5498 | 58.7086 | 54.9487 | 1.8852 | 2.0419 | 1.5668
21.125 | 58.5304 | 58.7019 | 54.9089 | 1.8831 | 2.0391 | 1.5647
21.1292 | 58.5366 | 58.7366 | 54.8909 | 1.8809 | 2.037 | 1.5627
21.1334 | 58.5305 | 58.7693 | 54.8631 | 1.879 | 2.035 | 1.5609
21.1375 | 58.5218 | 58.7181 | 54.8284 | 1.8771 | 2.0327 | 1.5594
21.1417 | 58.5017 | 58.6579 | 54.7997 | 1.8753 | 2.0304 | 1.5579
21.1459 | 58.4729 | 58.6763 | 54.7743 | 1.8731 | 2.0278 | 1.5562
21.15 | 58.4753 | 58.7091 | 54.7647 | 1.8712 | 2.0252 | 1.5547
21.1542 | 58.4857 | 58.7121 | 54.7754 | 1.8692 | 2.0233 | 1.5534
21.1584 | 58.4827 | 58.7044 | 54.7796 | 1.8674 | 2.0215 | 1.552
21.1625 | 58.4596 | 58.654 | 54.7657 | 1.8657 | 2.019 | 1.5507
21.1667 | 58.4347 | 58.6052 | 54.7641 | 1.8638 | 2.0165 | 1.5492
21.1709 | 58.4131 | 58.6229 | 54.7677 | 1.8618 | 2.0143 | 1.5477
21.175 | 58.4052 | 58.6487 | 54.769 | 1.86 | 2.0123 | 1.5463
21.1792 | 58.4121 | 58.6296 | 54.7822 | 1.8583 | 2.0103 | 1.5449
21.1834 | 58.3993 | 58.5986 | 54.7843 | 1.8566 | 2.0084 | 1.5434
21.1875 | 58.3829 | 58.5822 | 54.7742 | 1.8549 | 2.0061 | 1.5419
21.1917 | 58.373 | 58.5746 | 54.7754 | 1.8531 | 2.0038 | 1.5405
21.1959 | 58.3654 | 58.5538 | 54.7667 | 1.8513 | 2.0021 | 1.539
21.2 | 58.3541 | 58.5316 | 54.7549 | 1.8497 | 2.0005 | 1.5376
21.2042 | 58.3417 | 58.5109 | 54.7546 | 1.8481 | 1.9985 | 1.5362
21.2084 | 58.3187 | 58.4835 | 54.7489 | 1.8465 | 1.9964 | 1.5348
21.2125 | 58.2947 | 58.5163 | 54.7503 | 1.8448 | 1.9945 | 1.5334
21.2167 | 58.294 | 58.5591 | 54.7521 | 1.8432 | 1.9926 | 1.5321
21.2209 | 58.3062 | 58.5236 | 54.7478 | 1.8415 | 1.9909 | 1.5307
21.225 | 58.3154 | 58.481 | 54.7459 | 1.84 | 1.9893 | 1.5293
21.2292 | 58.2965 | 58.4381 | 54.7259 | 1.8385 | 1.9874 | 1.5281
21.2334 | 58.2712 | 58.3968 | 54.7145 | 1.837 | 1.9854 | 1.5268
21.2375 | 58.2466 | 58.4286 | 54.7186 | 1.8353 | 1.9837 | 1.5254
21.2417 | 58.229 | 58.4673 | 54.7118 | 1.8337 | 1.982 | 1.524
21.2459 | 58.2265 | 58.4982 | 54.7234 | 1.8324 | 1.9801 | 1.5228
21.25 | 58.2235 | 58.5199 | 54.7285 | 1.831 | 1.9782 | 1.5216
21.2542 | 58.2049 | 58.5254 | 54.709 | 1.8296 | 1.976 | 1.5203
21.2584 | 58.1969 | 58.5335 | 54.7034 | 1.828 | 1.9739 | 1.519
21.2625 | 58.2082 | 58.5002 | 54.6978 | 1.8265 | 1.972 | 1.5177
21.2667 | 58.2171 | 58.4653 | 54.6926 | 1.825 | 1.9701 | 1.5165
21.2709 | 58.1949 | 58.4681 | 54.6907 | 1.8237 | 1.9678 | 1.5153
21.275 | 58.166 | 58.4651 | 54.6819 | 1.8224 | 1.9656 | 1.5141
21.2792 | 58.1372 | 58.4933 | 54.6828 | 1.8209 | 1.9636 | 1.5129
21.2834 | 58.1159 | 58.5271 | 54.6823 | 1.8194 | 1.9617 | 1.5116
21.2875 | 58.121 | 58.478 | 54.6789 | 1.8182 | 1.9598 | 1.5105
21.2917 | 58.121 | 58.4268 | 54.6758 | 1.817 | 1.958 | 1.5094
21.2959 | 58.1095 | 58.4146 | 54.6654 | 1.8157 | 1.9558 | 1.5081
21.3 | 58.0926 | 58.4031 | 54.6597 | 1.8144 | 1.9537 | 1.5069
21.3042 | 58.0957 | 58.3843 | 54.6576 | 1.813 | 1.9522 | 1.5058
21.3084 | 58.1013 | 58.3697 | 54.6578 | 1.8116 | 1.9509 | 1.5047
21.3125 | 58.0957 | 58.3345 | 54.6489 | 1.8103 | 1.949 | 1.5035
21.3167 | 58.0805 | 58.2953 | 54.6353 | 1.8092 | 1.9472 | 1.5024
21.3209 | 58.0572 | 58.3433 | 54.6394 | 1.8078 | 1.9455 | 1.5013
21.325 | 58.0413 | 58.3929 | 54.6408 | 1.8065 | 1.9437 | 1.5001
21.3292 | 58.0189 | 58.3649 | 54.6353 | 1.8054 | 1.9423 | 1.4991
21.3334 | 58.0159 | 58.338 | 54.6304 | 1.8043 | 1.941 | 1.4981
21.3375 | 57.9993 | 58.3114 | 54.6223 | 1.8031 | 1.939 | 1.4969
21.3417 | 57.988 | 58.2821 | 54.6167 | 1.8019 | 1.9371 | 1.4957
21.3459 | 57.9897 | 58.2861 | 54.6134 | 1.8007 | 1.9358 | 1.4947
21.35 | 57.992 | 58.2918 | 54.6148 | 1.7995 | 1.9345 | 1.4937
21.3542 | 57.9818 | 58.2525 | 54.6054 | 1.7985 | 1.933 | 1.4927
21.3584 | 57.9619 | 58.2127 | 54.5921 | 1.7974 | 1.9315 | 1.4916
21.3625 | 57.9481 | 58.2497 | 54.5974 | 1.7962 | 1.9298 | 1.4906
21.3667 | 57.9339 | 58.2867 | 54.5996 | 1.795 | 1.9282 | 1.4895
21.3709 | 57.9297 | 58.2821 | 54.5881 | 1.794 | 1.9269 | 1.4885
21.375 | 57.9272 | 58.2789 | 54.5779 | 1.793 | 1.9257 | 1.4876
21.3792 | 57.9057 | 58.2616 | 54.5771 | 1.792 | 1.9238 | 1.4865
21.3834 | 57.8828 | 58.2431 | 54.5718 | 1.7909 | 1.9219 | 1.4854
21.3875 | 57.8736 | 58.263 | 54.5723 | 1.7899 | 1.9205 | 1.4845
21.3917 | 57.8664 | 58.286 | 54.5776 | 1.7888 | 1.919 | 1.4836
21.3959 | 57.8756 | 58.2411 | 54.5601 | 1.7879 | 1.9176 | 1.4826
21.4 | 57.8723 | 58.2007 | 54.5464 | 1.7869 | 1.9161 | 1.4816
21.4042 | 57.8569 | 58.2168 | 54.5493 | 1.786 | 1.9143 | 1.4807
21.4084 | 57.8428 | 58.2331 | 54.5483 | 1.7849 | 1.9125 | 1.4797
21.4125 | 57.8206 | 58.2658 | 54.5421 | 1.784 | 1.9111 | 1.4788
21.4167 | 57.8032 | 58.3001 | 54.5337 | 1.783 | 1.9096 | 1.478
21.4209 | 57.7882 | 58.2952 | 54.5361 | 1.7822 | 1.9077 | 1.4769
21.425 | 57.7631 | 58.2874 | 54.5326 | 1.7814 | 1.9057 | 1.4759
21.4292 | 57.7479 | 58.2822 | 54.5257 | 1.7806 | 1.9041 | 1.4751
21.4334 | 57.7375 | 58.2709 | 54.5256 | 1.7798 | 1.9024 | 1.4743
21.4375 | 57.7314 | 58.2237 | 54.5091 | 1.779 | 1.9008 | 1.4733
21.4417 | 57.7339 | 58.1779 | 54.4962 | 1.7782 | 1.8993 | 1.4724
21.4459 | 57.7266 | 58.1615 | 54.5073 | 1.7775 | 1.8978 | 1.4715
21.45 | 57.7215 | 58.1425 | 54.512 | 1.7766 | 1.8963 | 1.4706
21.4542 | 57.707 | 58.1221 | 54.4977 | 1.7759 | 1.8953 | 1.4698
21.4584 | 57.704 | 58.1004 | 54.492 | 1.775 | 1.8942 | 1.469
21.4625 | 57.6949 | 58.0549 | 54.4856 | 1.7743 | 1.8931 | 1.468
21.4667 | 57.6847 | 58.0135 | 54.48 | 1.7735 | 1.8921 | 1.4671
21.4709 | 57.6887 | 58.003 | 54.4843 | 1.7727 | 1.8912 | 1.4664
21.475 | 57.6842 | 57.9893 | 54.4839 | 1.7717 | 1.8903 | 1.4656
21.4792 | 57.6869 | 57.9583 | 54.4749 | 1.7709 | 1.8897 | 1.4647
21.4834 | 57.6966 | 57.9287 | 54.4675 | 1.77 | 1.8891 | 1.4638
21.4875 | 57.7038 | 57.8762 | 54.472 | 1.769 | 1.8887 | 1.4629
21.4917 | 57.6886 | 57.8239 | 54.4746 | 1.7681 | 1.8882 | 1.4621
21.4959 | 57.6868 | 57.7846 | 54.4623 | 1.7672 | 1.8881 | 1.4613
21.5 | 57.6758 | 57.7392 | 54.4559 | 1.7662 | 1.8879 | 1.4605
21.5042 | 57.6482 | 57.7165 | 54.4506 | 1.7653 | 1.8879 | 1.4596
21.5084 | 57.6444 | 57.6954 | 54.4481 | 1.7644 | 1.8879 | 1.4587
21.5125 | 57.6407 | 57.7007 | 54.4445 | 1.7635 | 1.8878 | 1.458
21.5167 | 57.6205 | 57.7072 | 54.4388 | 1.7627 | 1.8878 | 1.4573
21.5209 | 57.6205 | 57.7667 | 54.43 | 1.7619 | 1.8873 | 1.4564
21.525 | 57.6194 | 57.8304 | 54.4191 | 1.761 | 1.8868 | 1.4556
21.5292 | 57.6023 | 57.9031 | 54.4258 | 1.7602 | 1.8859 | 1.4548
21.5334 | 57.5937 | 57.9816 | 54.4238 | 1.7594 | 1.8851 | 1.4541
21.5375 | 57.5892 | 58.0114 | 54.4136 | 1.7586 | 1.8838 | 1.4534
21.5417 | 57.5619 | 58.0387 | 54.4018 | 1.7578 | 1.8824 | 1.4527
21.5459 | 57.5408 | 58.044 | 54.4007 | 1.7572 | 1.8809 | 1.4519
21.55 | 57.536 | 58.0501 | 54.3989 | 1.7565 | 1.8793 | 1.4511
21.5542 | 57.5171 | 57.9957 | 54.3978 | 1.7557 | 1.8782 | 1.4504
21.5584 | 57.5159 | 57.9388 | 54.3934 | 1.7551 | 1.8771 | 1.4498
21.5625 | 57.5272 | 57.8549 | 54.3844 | 1.7544 | 1.8761 | 1.449
21.5667 | 57.5152 | 57.7669 | 54.3784 | 1.7537 | 1.8752 | 1.4482
21.5709 | 57.5065 | 57.7001 | 54.3778 | 1.7531 | 1.875 | 1.4475
21.575 | 57.5001 | 57.6361 | 54.3795 | 1.7524 | 1.8748 | 1.4469
21.5792 | 57.4717 | 57.5756 | 54.3699 | 1.7518 | 1.8749 | 1.4462
21.5834 | 57.4635 | 57.5134 | 54.3611 | 1.7511 | 1.875 | 1.4455
21.5875 | 57.4521 | 57.504 | 54.3553 | 1.7506 | 1.8753 | 1.4448
21.5917 | 57.4319 | 57.4962 | 54.3551 | 1.75 | 1.8754 | 1.4441
21.5959 | 57.4399 | 57.5125 | 54.3456 | 1.7494 | 1.8757 | 1.4435
21.6 | 57.4331 | 57.5324 | 54.3386 | 1.7488 | 1.876 | 1.4428
21.6042 | 57.4369 | 57.5688 | 54.3344 | 1.7482 | 1.8758 | 1.4422
21.6084 | 57.4438 | 57.6034 | 54.3257 | 1.7476 | 1.8756 | 1.4415
21.6125 | 57.4348 | 57.6501 | 54.3237 | 1.7469 | 1.8752 | 1.4409
21.6167 | 57.4304 | 57.6989 | 54.3219 | 1.7463 | 1.8748 | 1.4403
21.6209 | 57.4328 | 57.7041 | 54.3134 | 1.7455 | 1.8742 | 1.4397
21.625 | 57.4265 | 57.708 | 54.3017 | 1.7448 | 1.8736 | 1.4391
21.6292 | 57.4136 | 57.7019 | 54.3044 | 1.7442 | 1.8728 | 1.4384
21.6334 | 57.3936 | 57.6942 | 54.3035 | 1.7437 | 1.872 | 1.4378
21.6375 | 57.3722 | 57.6531 | 54.2921 | 1.743 | 1.8715 | 1.4373
21.6417 | 57.3521 | 57.614 | 54.2871 | 1.7424 | 1.8711 | 1.4367
21.6459 | 57.353 | 57.5672 | 54.2813 | 1.7418 | 1.8707 | 1.4361
21.65 | 57.3469 | 57.5186 | 54.2731 | 1.7414 | 1.8702 | 1.4354
21.6542 | 57.3315 | 57.5088 | 54.2742 | 1.7409 | 1.8701 | 1.4349
21.6584 | 57.3246 | 57.5008 | 54.2753 | 1.7405 | 1.8699 | 1.4344
21.6625 | 57.3219 | 57.4669 | 54.2602 | 1.7398 | 1.87 | 1.4338
21.6667 | 57.3348 | 57.4338 | 54.25 | 1.7392 | 1.8701 | 1.4333
21.6709 | 57.3414 | 57.4272 | 54.2515 | 1.7387 | 1.87 | 1.4327
21.675 | 57.3446 | 57.4192 | 54.249 | 1.7382 | 1.8698 | 1.4321
21.6792 | 57.3263 | 57.4383 | 54.2425 | 1.7375 | 1.8698 | 1.4316
21.6834 | 57.3175 | 57.4598 | 54.2375 | 1.7369 | 1.8699 | 1.4311
21.6875 | 57.3178 | 57.4557 | 54.2287 | 1.7362 | 1.8697 | 1.4305
21.6917 | 57.318 | 57.4499 | 54.2187 | 1.7355 | 1.8695 | 1.43
21.6959 | 57.3066 | 57.4664 | 54.2221 | 1.7351 | 1.8692 | 1.4295
21.7 | 57.2897 | 57.4822 | 54.2222 | 1.7345 | 1.8688 | 1.429
21.7042 | 57.2724 | 57.4797 | 54.2063 | 1.7339 | 1.8685 | 1.4285
21.7084 | 57.2614 | 57.4777 | 54.1915 | 1.7333 | 1.8683 | 1.4281
21.7125 | 57.2589 | 57.4649 | 54.1843 | 1.7328 | 1.8678 | 1.4276
21.7167 | 57.2625 | 57.4575 | 54.1918 | 1.7323 | 1.8673 | 1.4269
21.7209 | 57.2593 | 57.4893 | 54.2162 | 1.7317 | 1.8667 | 1.4263
21.725 | 57.2749 | 57.5317 | 54.2584 | 1.731 | 1.866 | 1.4256
21.7292 | 57.3136 | 57.5527 | 54.3101 | 1.7301 | 1.8654 | 1.4246
21.7334 | 57.3148 | 57.554 | 54.3175 | 1.7295 | 1.8648 | 1.4239
21.7375 | 57.305 | 57.5285 | 54.2946 | 1.729 | 1.8642 | 1.4233
21.7417 | 57.2891 | 57.4992 | 54.2662 | 1.7282 | 1.8634 | 1.4225
21.7459 | 57.2584 | 57.488 | 54.2231 | 1.7272 | 1.8626 | 1.4216
21.75 | 57.3265 | 57.5296 | 54.2786 | 1.726 | 1.8616 | 1.4203
21.7542 | 57.433 | 57.5908 | 54.436 | 1.7246 | 1.8606 | 1.4186
21.7584 | 57.5684 | 57.6749 | 54.6274 | 1.7228 | 1.8593 | 1.4166
21.7625 | 57.7083 | 57.785 | 54.846 | 1.721 | 1.8577 | 1.4143
21.7667 | 57.8443 | 57.8884 | 55.0502 | 1.7182 | 1.8555 | 1.4112
21.7709 | 57.9712 | 58.0168 | 55.2263 | 1.715 | 1.853 | 1.4073
21.775 | 58.0897 | 58.1396 | 55.3919 | 1.7114 | 1.8501 | 1.403
21.7792 | 58.207 | 58.24 | 55.5653 | 1.7077 | 1.8469 | 1.3984
21.7834 | 58.2518 | 58.3015 | 55.6812 | 1.7038 | 1.8435 | 1.3937
21.7875 | 58.2688 | 58.3402 | 55.7316 | 1.6998 | 1.8398 | 1.3891
21.7917 | 58.2618 | 58.3521 | 55.7517 | 1.6957 | 1.8361 | 1.3844
21.7959 | 58.2391 | 58.3428 | 55.7478 | 1.6916 | 1.8324 | 1.3796
21.8 | 58.2112 | 58.3317 | 55.7467 | 1.688 | 1.8289 | 1.3751
21.8042 | 58.1816 | 58.2948 | 55.7561 | 1.6845 | 1.8254 | 1.371
21.8084 | 58.139 | 58.2508 | 55.7613 | 1.6812 | 1.8222 | 1.3671
21.8125 | 58.0974 | 58.2267 | 55.7493 | 1.678 | 1.819 | 1.3634
21.8167 | 58.0766 | 58.2118 | 55.7445 | 1.675 | 1.8159 | 1.3598
21.8209 | 58.0675 | 58.1739 | 55.7589 | 1.6721 | 1.8133 | 1.3563
21.825 | 58.0651 | 58.1501 | 55.7886 | 1.6694 | 1.8107 | 1.3529
21.8292 | 58.0704 | 58.1409 | 55.8246 | 1.6667 | 1.808 | 1.3496
21.8334 | 58.0783 | 58.1325 | 55.8617 | 1.664 | 1.8052 | 1.3464
21.8375 | 58.0925 | 58.1616 | 55.8996 | 1.6613 | 1.8028 | 1.3432
21.8417 | 58.1054 | 58.1935 | 55.9278 | 1.6587 | 1.8003 | 1.3399
21.8459 | 58.1202 | 58.1716 | 55.9548 | 1.6561 | 1.7979 | 1.3368
21.85 | 58.1392 | 58.1538 | 55.995 | 1.6534 | 1.7956 | 1.3336
21.8542 | 58.1489 | 58.1789 | 56.0348 | 1.6507 | 1.7928 | 1.3303
21.8584 | 58.1608 | 58.1969 | 56.0643 | 1.6481 | 1.79 | 1.3272
21.8625 | 58.1699 | 58.2162 | 56.0942 | 1.6455 | 1.7878 | 1.3242
21.8667 | 58.166 | 58.2331 | 56.1137 | 1.6428 | 1.7855 | 1.3211
21.8709 | 58.168 | 58.2087 | 56.1207 | 1.6403 | 1.7829 | 1.3181
21.875 | 58.1775 | 58.1901 | 56.1488 | 1.6376 | 1.7803 | 1.3151
21.8792 | 58.1924 | 58.2322 | 56.1923 | 1.635 | 1.7777 | 1.312
21.8834 | 58.1876 | 58.2657 | 56.2128 | 1.6326 | 1.7751 | 1.3092
21.8875 | 58.1907 | 58.2472 | 56.2197 | 1.6302 | 1.773 | 1.3065
21.8917 | 58.1862 | 58.2312 | 56.2332 | 1.6277 | 1.7708 | 1.3037
21.8959 | 58.187 | 58.2358 | 56.2452 | 1.6252 | 1.7679 | 1.3007
21.9 | 58.2029 | 58.2461 | 56.2717 | 1.6229 | 1.7651 | 1.298
21.9042 | 58.2155 | 58.2822 | 56.3179 | 1.6205 | 1.7629 | 1.2954
21.9084 | 58.206 | 58.3074 | 56.3334 | 1.6182 | 1.7608 | 1.2928
21.9125 | 58.197 | 58.2572 | 56.3191 | 1.6159 | 1.7584 | 1.2903
21.9167 | 58.2029 | 58.2166 | 56.3315 | 1.6136 | 1.756 | 1.2877
21.9209 | 58.2143 | 58.2571 | 56.3648 | 1.6112 | 1.7533 | 1.2849
21.925 | 58.2232 | 58.2963 | 56.391 | 1.6091 | 1.7507 | 1.2824
21.9292 | 58.229 | 58.2859 | 56.418 | 1.607 | 1.7489 | 1.2802
21.9334 | 58.2178 | 58.2655 | 56.425 | 1.6048 | 1.7471 | 1.2778
21.9375 | 58.2031 | 58.2228 | 56.4056 | 1.6025 | 1.7446 | 1.2753
21.9417 | 58.2204 | 58.1951 | 56.4206 | 1.6003 | 1.742 | 1.2729
21.9459 | 58.2423 | 58.2613 | 56.4714 | 1.5982 | 1.7399 | 1.2704
21.95 | 58.2387 | 58.3179 | 56.4928 | 1.5962 | 1.7379 | 1.2682
21.9542 | 58.2316 | 58.2648 | 56.4889 | 1.5943 | 1.7362 | 1.2662
21.9584 | 58.2231 | 58.2098 | 56.49 | 1.5921 | 1.7344 | 1.264
21.9625 | 58.2121 | 58.2189 | 56.4871 | 1.59 | 1.7317 | 1.2615
21.9667 | 58.2282 | 58.2412 | 56.504 | 1.588 | 1.7292 | 1.2593
21.9709 | 58.2528 | 58.2939 | 56.5472 | 1.5861 | 1.7275 | 1.2573
21.975 | 58.2388 | 58.3307 | 56.5518 | 1.5842 | 1.726 | 1.2554
21.9792 | 58.2268 | 58.2645 | 56.5223 | 1.5824 | 1.7239 | 1.2535
21.9834 | 58.2335 | 58.2066 | 56.5253 | 1.5803 | 1.7217 | 1.2514
21.9875 | 58.2383 | 58.2652 | 56.5518 | 1.5783 | 1.7192 | 1.2491
21.9917 | 58.2516 | 58.3276 | 56.576 | 1.5765 | 1.7169 | 1.2472
21.9959 | 58.2659 | 58.3311 | 56.5967 | 1.5748 | 1.7154 | 1.2456
22 | 58.2492 | 58.3197 | 56.5816 | 1.5729 | 1.7139 | 1.2439
22.0042 | 58.2331 | 58.2811 | 56.5337 | 1.571 | 1.7114 | 1.2421
22.0084 | 58.2404 | 58.2584 | 56.5142 | 1.5692 | 1.7089 | 1.2403
22.0125 | 58.2574 | 58.3247 | 56.5299 | 1.5672 | 1.7069 | 1.2387
22.0167 | 58.254 | 58.3834 | 56.5244 | 1.5656 | 1.705 | 1.2373
22.0209 | 58.248 | 58.335 | 56.4995 | 1.564 | 1.7033 | 1.2362
22.025 | 58.2412 | 58.2814 | 56.4758 | 1.5623 | 1.7015 | 1.235
22.0292 | 58.2317 | 58.3038 | 56.4596 | 1.5604 | 1.6988 | 1.2334
22.0334 | 58.256 | 58.3417 | 56.4714 | 1.5586 | 1.6963 | 1.2321
22.0375 | 58.2791 | 58.3693 | 56.5068 | 1.557 | 1.6948 | 1.231
22.0417 | 58.2708 | 58.3809 | 56.5205 | 1.5554 | 1.6934 | 1.23
22.0459 | 58.2462 | 58.3033 | 56.4938 | 1.5539 | 1.6913 | 1.2289
22.05 | 58.2336 | 58.2324 | 56.4872 | 1.5521 | 1.6891 | 1.2276
22.0542 | 58.2363 | 58.3052 | 56.5177 | 1.5503 | 1.6869 | 1.226
22.0584 | 58.2458 | 58.3847 | 56.5438 | 1.5488 | 1.6848 | 1.2247
22.0625 | 58.2678 | 58.3691 | 56.5688 | 1.5473 | 1.6836 | 1.2237
22.0667 | 58.2579 | 58.3381 | 56.5744 | 1.5458 | 1.6823 | 1.2226
22.0709 | 58.2436 | 58.278 | 56.5421 | 1.5442 | 1.6801 | 1.2212
22.075 | 58.2477 | 58.2332 | 56.5398 | 1.5426 | 1.6778 | 1.2198
22.0792 | 58.2558 | 58.2856 | 56.5655 | 1.541 | 1.6763 | 1.2185
22.0834 | 58.2439 | 58.3324 | 56.5711 | 1.5397 | 1.6749 | 1.2173
22.0875 | 58.2409 | 58.3118 | 56.5779 | 1.5383 | 1.6733 | 1.2162
22.0917 | 58.2303 | 58.2842 | 56.5758 | 1.5368 | 1.6717 | 1.215
22.0959 | 58.2202 | 58.3086 | 56.5671 | 1.5352 | 1.6696 | 1.2136
22.1 | 58.2457 | 58.3473 | 56.5795 | 1.5338 | 1.6676 | 1.2124
22.1042 | 58.2697 | 58.3333 | 56.5908 | 1.5323 | 1.6664 | 1.2113
22.1084 | 58.2673 | 58.3052 | 56.5898 | 1.5309 | 1.6653 | 1.2101
22.1125 | 58.2509 | 58.2542 | 56.5763 | 1.5296 | 1.6635 | 1.209
22.1167 | 58.2417 | 58.2098 | 56.571 | 1.5282 | 1.6616 | 1.2079
22.1209 | 58.2224 | 58.3026 | 56.5877 | 1.5267 | 1.6597 | 1.2066
22.125 | 58.2223 | 58.4023 | 56.5972 | 1.5254 | 1.6581 | 1.2054
22.1292 | 58.2409 | 58.4057 | 56.612 | 1.5241 | 1.6567 | 1.2044
22.1334 | 58.24 | 58.3935 | 56.6185 | 1.5228 | 1.6553 | 1.2033
22.1375 | 58.2272 | 58.36 | 56.5936 | 1.5215 | 1.6531 | 1.2022
22.1417 | 58.2382 | 58.3383 | 56.5909 | 1.5202 | 1.6508 | 1.2011
22.1459 | 58.2508 | 58.3883 | 56.61 | 1.5187 | 1.6491 | 1.1999
22.15 | 58.2552 | 58.4322 | 56.616 | 1.5173 | 1.6475 | 1.1987
22.1542 | 58.2519 | 58.405 | 56.6183 | 1.5163 | 1.6458 | 1.1978
22.1584 | 58.234 | 58.3699 | 56.6175 | 1.515 | 1.6441 | 1.1968
22.1625 | 58.2108 | 58.3826 | 56.6095 | 1.5137 | 1.6419 | 1.1956
22.1667 | 58.2041 | 58.4088 | 56.6091 | 1.5124 | 1.6398 | 1.1945
22.1709 | 58.2283 | 58.4187 | 56.6318 | 1.5112 | 1.6384 | 1.1935
22.175 | 58.2315 | 58.418 | 56.6426 | 1.5101 | 1.637 | 1.1924
22.1792 | 58.2205 | 58.3597 | 56.6247 | 1.509 | 1.6353 | 1.1915
22.1834 | 58.2109 | 58.3059 | 56.6194 | 1.5079 | 1.6335 | 1.1905
22.1875 | 58.2216 | 58.3213 | 56.6249 | 1.5064 | 1.6319 | 1.1893
22.1917 | 58.2354 | 58.3437 | 56.6307 | 1.5052 | 1.6304 | 1.1882
22.1959 | 58.2506 | 58.3375 | 56.6406 | 1.5041 | 1.6292 | 1.1874
22.2 | 58.2438 | 58.3193 | 56.6402 | 1.5031 | 1.628 | 1.1865
22.2042 | 58.2081 | 58.3297 | 56.6313 | 1.5019 | 1.6262 | 1.1854
22.2084 | 58.1922 | 58.3501 | 56.6289 | 1.5007 | 1.6244 | 1.1843
22.2125 | 58.198 | 58.3694 | 56.6441 | 1.4995 | 1.6232 | 1.1833
22.2167 | 58.215 | 58.3862 | 56.6543 | 1.4984 | 1.622 | 1.1824
22.2209 | 58.2129 | 58.3456 | 56.6444 | 1.4975 | 1.6206 | 1.1815
22.225 | 58.2029 | 58.2978 | 56.6372 | 1.4965 | 1.619 | 1.1806
22.2292 | 58.1892 | 58.3146 | 56.6397 | 1.4954 | 1.6175 | 1.1795
22.2334 | 58.1893 | 58.3414 | 56.6475 | 1.4941 | 1.616 | 1.1785
22.2375 | 58.2055 | 58.3334 | 56.6549 | 1.4931 | 1.615 | 1.1777
22.2417 | 58.2085 | 58.3186 | 56.6555 | 1.4922 | 1.614 | 1.1768
22.2459 | 58.2005 | 58.3208 | 56.6472 | 1.4913 | 1.6123 | 1.1759
22.25 | 58.1894 | 58.3244 | 56.6415 | 1.4901 | 1.6107 | 1.1749
22.2542 | 58.178 | 58.3586 | 56.6505 | 1.4891 | 1.6094 | 1.1739
22.2584 | 58.184 | 58.3972 | 56.6571 | 1.4881 | 1.6082 | 1.1731
22.2625 | 58.1819 | 58.3806 | 56.6589 | 1.4873 | 1.6068 | 1.1722
22.2667 | 58.1639 | 58.3573 | 56.6552 | 1.4864 | 1.6053 | 1.1713
22.2709 | 58.1641 | 58.3679 | 56.6545 | 1.4854 | 1.6037 | 1.1704
22.275 | 58.1629 | 58.3862 | 56.6626 | 1.4844 | 1.6021 | 1.1695
22.2792 | 58.1745 | 58.3639 | 56.6569 | 1.4834 | 1.601 | 1.1687
22.2834 | 58.1864 | 58.3429 | 56.6529 | 1.4826 | 1.5999 | 1.1679
22.2875 | 58.1772 | 58.3521 | 56.6565 | 1.4817 | 1.5982 | 1.167
22.2917 | 58.1594 | 58.3599 | 56.6536 | 1.4808 | 1.5964 | 1.166
22.2959 | 58.1476 | 58.4106 | 56.6614 | 1.4799 | 1.5951 | 1.1652
22.3 | 58.1432 | 58.4657 | 56.6696 | 1.479 | 1.5938 | 1.1644
22.3042 | 58.1375 | 58.4368 | 56.6632 | 1.4782 | 1.5923 | 1.1636
22.3084 | 58.1277 | 58.4003 | 56.6562 | 1.4775 | 1.5908 | 1.1628
22.3125 | 58.1158 | 58.4011 | 56.6588 | 1.4768 | 1.5891 | 1.1619
22.3167 | 58.1073 | 58.4002 | 56.6635 | 1.476 | 1.5874 | 1.1611
22.3209 | 58.1142 | 58.3855 | 56.6619 | 1.4752 | 1.5863 | 1.1603
22.325 | 58.1321 | 58.3715 | 56.6608 | 1.4744 | 1.5852 | 1.1596
22.3292 | 58.1289 | 58.3325 | 56.6646 | 1.4738 | 1.5839 | 1.1587
22.3334 | 58.1264 | 58.2879 | 56.6659 | 1.473 | 1.5826 | 1.1578
22.3375 | 58.1198 | 58.2801 | 56.6627 | 1.4722 | 1.5817 | 1.1571
22.3417 | 58.115 | 58.2756 | 56.6678 | 1.4713 | 1.5808 | 1.1564
22.3459 | 58.1213 | 58.2398 | 56.6632 | 1.4706 | 1.5801 | 1.1555
22.35 | 58.1293 | 58.2043 | 56.6569 | 1.4698 | 1.5794 | 1.1547
22.3542 | 58.1269 | 58.2021 | 56.6689 | 1.4691 | 1.5786 | 1.154
22.3584 | 58.1254 | 58.1976 | 56.6758 | 1.4682 | 1.5778 | 1.1532
22.3625 | 58.1427 | 58.1801 | 56.668 | 1.4673 | 1.5774 | 1.1524
22.3667 | 58.1489 | 58.1676 | 56.6649 | 1.4664 | 1.5771 | 1.1517
22.3709 | 58.1592 | 58.1293 | 56.6711 | 1.4656 | 1.5766 | 1.1509
22.375 | 58.157 | 58.0878 | 56.6721 | 1.4647 | 1.5761 | 1.15
22.3792 | 58.1397 | 58.0821 | 56.6731 | 1.4638 | 1.576 | 1.1494
22.3834 | 58.1309 | 58.0719 | 56.6781 | 1.4629 | 1.5758 | 1.1487
22.3875 | 58.1277 | 58.0443 | 56.6657 | 1.4621 | 1.5757 | 1.1479
22.3917 | 58.1235 | 58.0199 | 56.6589 | 1.4613 | 1.5757 | 1.1471
22.3959 | 58.1227 | 58.0437 | 56.6697 | 1.4605 | 1.5753 | 1.1464
22.4 | 58.1158 | 58.0673 | 56.6735 | 1.4597 | 1.575 | 1.1456
22.4042 | 58.1111 | 58.1318 | 56.667 | 1.4589 | 1.5745 | 1.145
22.4084 | 58.1161 | 58.2004 | 56.6611 | 1.4581 | 1.5741 | 1.1444
22.4125 | 58.1211 | 58.2409 | 56.6641 | 1.4573 | 1.5731 | 1.1435
22.4167 | 58.1091 | 58.2861 | 56.662 | 1.4567 | 1.5722 | 1.1428
22.4209 | 58.0971 | 58.3271 | 56.6659 | 1.456 | 1.5709 | 1.1422
22.425 | 58.0833 | 58.3654 | 56.6665 | 1.4553 | 1.5696 | 1.1416
22.4292 | 58.0611 | 58.3609 | 56.6599 | 1.4546 | 1.5684 | 1.1408
22.4334 | 58.0709 | 58.3575 | 56.6553 | 1.4539 | 1.5671 | 1.1402
22.4375 | 58.0793 | 58.2995 | 56.6627 | 1.4533 | 1.566 | 1.1395
22.4417 | 58.0679 | 58.239 | 56.6671 | 1.4527 | 1.565 | 1.1388
22.4459 | 58.0788 | 58.1784 | 56.6598 | 1.4521 | 1.5643 | 1.1382
22.45 | 58.0786 | 58.1138 | 56.6565 | 1.4513 | 1.5636 | 1.1376
22.4542 | 58.0592 | 58.055 | 56.6587 | 1.4507 | 1.5634 | 1.1368
22.4584 | 58.0696 | 57.9992 | 56.6609 | 1.4501 | 1.5633 | 1.1362
22.4625 | 58.0583 | 57.9544 | 56.6598 | 1.4495 | 1.5634 | 1.1356
22.4667 | 58.0383 | 57.9072 | 56.6604 | 1.4489 | 1.5636 | 1.135
22.4709 | 58.045 | 57.911 | 56.651 | 1.4484 | 1.5638 | 1.1343
22.475 | 58.0395 | 57.9167 | 56.6474 | 1.4477 | 1.5639 | 1.1337
22.4792 | 58.0381 | 57.9431 | 56.6522 | 1.4472 | 1.5641 | 1.1331
22.4834 | 58.0394 | 57.9739 | 56.6543 | 1.4467 | 1.5643 | 1.1325
22.4875 | 58.0466 | 58.0095 | 56.6472 | 1.446 | 1.5641 | 1.1319
22.4917 | 58.0447 | 58.042 | 56.6409 | 1.4454 | 1.5639 | 1.1314
22.4959 | 58.0545 | 58.0923 | 56.6423 | 1.4448 | 1.5634 | 1.1307
22.5 | 58.0611 | 58.1453 | 56.6417 | 1.4442 | 1.5628 | 1.1301
22.5042 | 58.0546 | 58.155 | 56.6451 | 1.4435 | 1.5622 | 1.1296
22.5084 | 58.0489 | 58.164 | 56.6437 | 1.4429 | 1.5616 | 1.1291
22.5125 | 58.0445 | 58.1438 | 56.6368 | 1.4422 | 1.5608 | 1.1285
22.5167 | 58.0341 | 58.1201 | 56.633 | 1.4416 | 1.56 | 1.1279
22.5209 | 58.0243 | 58.0946 | 56.6356 | 1.4411 | 1.5595 | 1.1273
22.525 | 58.0136 | 58.0727 | 56.6383 | 1.4406 | 1.5591 | 1.1268
22.5292 | 58.0049 | 58.0366 | 56.6349 | 1.44 | 1.5587 | 1.1263
22.5334 | 57.9992 | 57.998 | 56.6298 | 1.4395 | 1.5584 | 1.1257
22.5375 | 57.9985 | 57.9798 | 56.6278 | 1.439 | 1.5582 | 1.1252
22.5417 | 58.0038 | 57.962 | 56.6292 | 1.4385 | 1.558 | 1.1246
22.5459 | 58.0025 | 57.9446 | 56.6278 | 1.438 | 1.5581 | 1.1241
22.55 | 58.0107 | 57.9298 | 56.6265 | 1.4374 | 1.5581 | 1.1236
22.5542 | 58.0155 | 57.9299 | 56.622 | 1.4368 | 1.558 | 1.1231
22.5584 | 58.02 | 57.9266 | 56.6148 | 1.4363 | 1.5579 | 1.1225
22.5625 | 58.0131 | 57.9489 | 56.6139 | 1.4358 | 1.5579 | 1.1221
22.5667 | 58.0173 | 57.9766 | 56.6217 | 1.4351 | 1.5577 | 1.1215
22.5709 | 58.0206 | 57.9885 | 56.6292 | 1.4344 | 1.5575 | 1.1209
22.575 | 58.0236 | 57.9992 | 56.6323 | 1.4338 | 1.5572 | 1.1204
22.5792 | 58.0281 | 58.0163 | 56.6408 | 1.4333 | 1.5568 | 1.1199
22.5834 | 58.0047 | 58.0209 | 56.6256 | 1.4328 | 1.5564 | 1.1194
22.5875 | 57.9719 | 58.0039 | 56.5846 | 1.4323 | 1.5561 | 1.1191
22.5917 | 57.964 | 58 | 56.5706 | 1.4317 | 1.5558 | 1.1187
22.5959 | 57.9707 | 58.0049 | 56.5776 | 1.4311 | 1.5552 | 1.118
22.6 | 58.0048 | 58.0292 | 56.6224 | 1.4304 | 1.5545 | 1.1172
22.6042 | 58.057 | 58.0875 | 56.7168 | 1.4298 | 1.5539 | 1.1164
22.6084 | 58.073 | 58.1302 | 56.7756 | 1.4291 | 1.5532 | 1.1156
22.6125 | 58.0884 | 58.1267 | 56.784 | 1.4283 | 1.5525 | 1.1149
22.6167 | 58.0839 | 58.1081 | 56.763 | 1.4274 | 1.5518 | 1.114
22.6209 | 58.0711 | 58.0964 | 56.724 | 1.4265 | 1.5508 | 1.1129
22.625 | 58.0838 | 58.1043 | 56.7196 | 1.4255 | 1.5497 | 1.1118
22.6292 | 58.104 | 58.1263 | 56.7543 | 1.4244 | 1.5489 | 1.1107
22.6334 | 58.1676 | 58.1741 | 56.8299 | 1.4231 | 1.548 | 1.1095
22.6375 | 58.2516 | 58.2154 | 56.9297 | 1.4216 | 1.5467 | 1.108
22.6417 | 58.36 | 58.2689 | 57.0449 | 1.4197 | 1.5452 | 1.1061
22.6459 | 58.4657 | 58.3719 | 57.185 | 1.4177 | 1.5434 | 1.1038
22.65 | 58.5758 | 58.4815 | 57.3333 | 1.415 | 1.5412 | 1.101
22.6542 | 58.6884 | 58.591 | 57.4781 | 1.4121 | 1.5388 | 1.0979
22.6584 | 58.7758 | 58.6827 | 57.5986 | 1.4089 | 1.5362 | 1.0945
22.6625 | 58.8578 | 58.755 | 57.6992 | 1.4055 | 1.5331 | 1.0908
22.6667 | 58.8836 | 58.7917 | 57.7495 | 1.4021 | 1.5299 | 1.0871
22.6709 | 58.8776 | 58.8133 | 57.7579 | 1.3986 | 1.5267 | 1.0834
22.675 | 58.859 | 58.8229 | 57.7628 | 1.3951 | 1.5235 | 1.0797
22.6792 | 58.8386 | 58.8076 | 57.7551 | 1.3916 | 1.5202 | 1.076
22.6834 | 58.8031 | 58.7811 | 57.7376 | 1.3885 | 1.5171 | 1.0726
22.6875 | 58.7654 | 58.7468 | 57.7242 | 1.3857 | 1.5142 | 1.0696
22.6917 | 58.7152 | 58.7071 | 57.7004 | 1.3831 | 1.5114 | 1.0666
22.6959 | 58.6595 | 58.6537 | 57.6573 | 1.3805 | 1.5088 | 1.0639
22.7 | 58.6446 | 58.6228 | 57.6499 | 1.378 | 1.5064 | 1.0612
22.7042 | 58.6503 | 58.6068 | 57.6771 | 1.3757 | 1.5041 | 1.0585
22.7084 | 58.6481 | 58.5929 | 57.6958 | 1.3736 | 1.5019 | 1.056
22.7125 | 58.648 | 58.5911 | 57.7134 | 1.3716 | 1.4999 | 1.0539
22.7167 | 58.6497 | 58.5934 | 57.7312 | 1.3694 | 1.4978 | 1.0515
22.7209 | 58.6576 | 58.5946 | 57.7378 | 1.3671 | 1.4957 | 1.0489
22.725 | 58.6903 | 58.6101 | 57.7646 | 1.3649 | 1.4936 | 1.0464
22.7292 | 58.7268 | 58.6304 | 57.8204 | 1.3628 | 1.4915 | 1.044
22.7334 | 58.7371 | 58.6366 | 57.8506 | 1.3607 | 1.4895 | 1.0416
22.7375 | 58.7293 | 58.645 | 57.8505 | 1.3586 | 1.4874 | 1.0394
22.7417 | 58.7362 | 58.6551 | 57.8595 | 1.3562 | 1.4852 | 1.0369
22.7459 | 58.7491 | 58.672 | 57.8769 | 1.3539 | 1.483 | 1.0343
22.75 | 58.7626 | 58.6923 | 57.8974 | 1.3517 | 1.4808 | 1.0319
22.7542 | 58.7779 | 58.6934 | 57.9282 | 1.3496 | 1.4788 | 1.0297
22.7584 | 58.7652 | 58.6814 | 57.9418 | 1.3475 | 1.4767 | 1.0275
22.7625 | 58.7533 | 58.6839 | 57.9272 | 1.3453 | 1.4744 | 1.0251
22.7667 | 58.7551 | 58.6952 | 57.9294 | 1.3431 | 1.4722 | 1.0229
22.7709 | 58.7756 | 58.7106 | 57.957 | 1.341 | 1.4701 | 1.0205
22.775 | 58.7796 | 58.7242 | 57.9769 | 1.339 | 1.4681 | 1.0183
22.7792 | 58.7763 | 58.7128 | 57.9868 | 1.3371 | 1.466 | 1.0164
22.7834 | 58.7733 | 58.696 | 57.9932 | 1.3351 | 1.4639 | 1.0143
22.7875 | 58.7666 | 58.7088 | 57.9914 | 1.3329 | 1.4617 | 1.0121
22.7917 | 58.7761 | 58.7313 | 57.999 | 1.331 | 1.4595 | 1.01
22.7959 | 58.7947 | 58.732 | 58.0255 | 1.3291 | 1.4577 | 1.008
22.8 | 58.7938 | 58.7267 | 58.0434 | 1.3272 | 1.4558 | 1.006
22.8042 | 58.7826 | 58.7149 | 58.0434 | 1.3254 | 1.4537 | 1.004
22.8084 | 58.7842 | 58.7023 | 58.0466 | 1.3234 | 1.4516 | 1.0021
22.8125 | 58.7855 | 58.7122 | 58.0565 | 1.3215 | 1.4497 | 1.0001
22.8167 | 58.7925 | 58.7272 | 58.066 | 1.3197 | 1.4479 | 0.99813
22.8209 | 58.8041 | 58.7151 | 58.0784 | 1.3179 | 1.4461 | 0.99633
22.825 | 58.8044 | 58.6977 | 58.0894 | 1.3161 | 1.4443 | 0.99451
22.8292 | 58.7974 | 58.7063 | 58.0938 | 1.3143 | 1.4423 | 0.99261
22.8334 | 58.8016 | 58.7163 | 58.1003 | 1.3125 | 1.4404 | 0.99076
22.8375 | 58.8013 | 58.7139 | 58.1112 | 1.3108 | 1.4387 | 0.989
22.8417 | 58.8041 | 58.7136 | 58.1201 | 1.309 | 1.4372 | 0.98724
22.8459 | 58.8056 | 58.7149 | 58.1222 | 1.3074 | 1.4352 | 0.9855
22.85 | 58.8058 | 58.7135 | 58.1206 | 1.3057 | 1.4333 | 0.98383
22.8542 | 58.8085 | 58.7359 | 58.1232 | 1.304 | 1.4316 | 0.98216
22.8584 | 58.8071 | 58.7589 | 58.1229 | 1.3023 | 1.4299 | 0.98053
22.8625 | 58.8105 | 58.7371 | 58.1223 | 1.3007 | 1.4282 | 0.97898
22.8667 | 58.8171 | 58.7168 | 58.1348 | 1.299 | 1.4265 | 0.97739
22.8709 | 58.8187 | 58.7449 | 58.1475 | 1.2974 | 1.4245 | 0.97578
22.875 | 58.8219 | 58.7709 | 58.1501 | 1.2958 | 1.4225 | 0.97429
22.8792 | 58.8295 | 58.7829 | 58.1528 | 1.2942 | 1.4209 | 0.97289
22.8834 | 58.8249 | 58.7942 | 58.1443 | 1.2926 | 1.4194 | 0.97144
22.8875 | 58.8234 | 58.7615 | 58.1202 | 1.2911 | 1.4175 | 0.97008
22.8917 | 58.8251 | 58.7316 | 58.1103 | 1.2895 | 1.4156 | 0.9688
22.8959 | 58.8224 | 58.7729 | 58.1119 | 1.2879 | 1.4137 | 0.96749
22.9 | 58.8174 | 58.8103 | 58.0958 | 1.2865 | 1.4118 | 0.96636
22.9042 | 58.8186 | 58.8014 | 58.0848 | 1.285 | 1.4103 | 0.96539
22.9084 | 58.8286 | 58.794 | 58.0804 | 1.2835 | 1.4088 | 0.96432
22.9125 | 58.8283 | 58.7845 | 58.0705 | 1.282 | 1.4067 | 0.96317
22.9167 | 58.8434 | 58.7782 | 58.0802 | 1.2805 | 1.4047 | 0.96216
22.9209 | 58.8453 | 58.7935 | 58.0976 | 1.2791 | 1.4032 | 0.9612
22.925 | 58.8322 | 58.8024 | 58.0994 | 1.2776 | 1.4018 | 0.96023
22.9292 | 58.8197 | 58.7666 | 58.0912 | 1.2763 | 1.4001 | 0.95929
22.9334 | 58.8153 | 58.7365 | 58.0969 | 1.2748 | 1.3985 | 0.95822
22.9375 | 58.8253 | 58.79 | 58.1283 | 1.2734 | 1.3965 | 0.95693
22.9417 | 58.836 | 58.8433 | 58.1527 | 1.272 | 1.3946 | 0.95581
22.9459 | 58.8481 | 58.816 | 58.1582 | 1.2708 | 1.3935 | 0.95497
22.95 | 58.8405 | 58.7825 | 58.1556 | 1.2694 | 1.3925 | 0.95396
22.9542 | 58.8323 | 58.7227 | 58.1289 | 1.268 | 1.3906 | 0.95273
22.9584 | 58.8307 | 58.6723 | 58.1259 | 1.2666 | 1.3888 | 0.95153
22.9625 | 58.8351 | 58.7529 | 58.1651 | 1.2653 | 1.3873 | 0.9504
22.9667 | 58.8251 | 58.8275 | 58.175 | 1.2642 | 1.3859 | 0.94941
22.9709 | 58.8192 | 58.8085 | 58.1665 | 1.2629 | 1.3848 | 0.94855
22.975 | 58.8173 | 58.7876 | 58.1608 | 1.2616 | 1.3835 | 0.94749
22.9792 | 58.8245 | 58.7739 | 58.1479 | 1.2602 | 1.3816 | 0.94624
22.9834 | 58.8484 | 58.7679 | 58.1597 | 1.259 | 1.3797 | 0.94515
22.9875 | 58.8592 | 58.7783 | 58.1789 | 1.2578 | 1.3787 | 0.94426
22.9917 | 58.847 | 58.7786 | 58.1735 | 1.2566 | 1.3777 | 0.94337
22.9959 | 58.8289 | 58.7503 | 58.1581 | 1.2554 | 1.3761 | 0.94242
23 | 58.8275 | 58.7293 | 58.1556 | 1.2541 | 1.3745 | 0.94133
23.0042 | 58.8214 | 58.8037 | 58.1734 | 1.2528 | 1.3728 | 0.94021
23.0084 | 58.8246 | 58.8799 | 58.1882 | 1.2518 | 1.3712 | 0.9393
23.0125 | 58.8347 | 58.8673 | 58.195 | 1.2507 | 1.3701 | 0.93847
23.0167 | 58.83 | 58.844 | 58.1894 | 1.2494 | 1.3689 | 0.93751
23.0209 | 58.8232 | 58.8187 | 58.1686 | 1.2483 | 1.3669 | 0.93649
23.025 | 58.8449 | 58.8043 | 58.1742 | 1.2471 | 1.3648 | 0.93548
23.0292 | 58.8494 | 58.8638 | 58.1973 | 1.2459 | 1.3634 | 0.93447
23.0334 | 58.8387 | 58.9146 | 58.2013 | 1.2448 | 1.362 | 0.93358
23.0375 | 58.8417 | 58.8676 | 58.1969 | 1.2438 | 1.3606 | 0.93282
23.0417 | 58.8316 | 58.8172 | 58.1917 | 1.2425 | 1.3592 | 0.93187
23.0459 | 58.8157 | 58.8372 | 58.1849 | 1.2415 | 1.3571 | 0.93079
23.05 | 58.8158 | 58.8687 | 58.1911 | 1.2405 | 1.3551 | 0.92987
23.0542 | 58.8291 | 58.8876 | 58.2172 | 1.2394 | 1.3541 | 0.92898
23.0584 | 58.8159 | 58.8946 | 58.2223 | 1.2383 | 1.353 | 0.92809
23.0625 | 58.8178 | 58.8078 | 58.1975 | 1.2374 | 1.3516 | 0.92732
23.0667 | 58.83 | 58.7291 | 58.1938 | 1.2363 | 1.35 | 0.92644
23.0709 | 58.834 | 58.7749 | 58.2016 | 1.2351 | 1.3485 | 0.92533
23.075 | 58.8387 | 58.8243 | 58.2064 | 1.2341 | 1.347 | 0.92441
23.0792 | 58.8457 | 58.8241 | 58.2248 | 1.2332 | 1.3463 | 0.92373
23.0834 | 58.8331 | 58.8124 | 58.2267 | 1.2321 | 1.3455 | 0.92292
23.0875 | 58.8069 | 58.7854 | 58.202 | 1.2311 | 1.3438 | 0.922
23.0917 | 58.8115 | 58.7722 | 58.1972 | 1.2301 | 1.3421 | 0.92113
23.0959 | 58.8215 | 58.8336 | 58.2222 | 1.229 | 1.3409 | 0.92014
23.1 | 58.8259 | 58.887 | 58.2319 | 1.2281 | 1.3399 | 0.91928
23.1042 | 58.819 | 58.8296 | 58.2241 | 1.2273 | 1.3389 | 0.91867
23.1084 | 58.808 | 58.7673 | 58.2196 | 1.2264 | 1.3379 | 0.91791
23.1125 | 58.7952 | 58.7766 | 58.211 | 1.2254 | 1.3361 | 0.91685
23.1167 | 58.7983 | 58.7994 | 58.2146 | 1.2243 | 1.3345 | 0.91592
23.1209 | 58.8293 | 58.8272 | 58.2374 | 1.2235 | 1.3338 | 0.91522
23.125 | 58.8338 | 58.8417 | 58.2438 | 1.2226 | 1.3331 | 0.91449
23.1292 | 58.8119 | 58.7946 | 58.219 | 1.2218 | 1.3317 | 0.91375
23.1334 | 58.8034 | 58.7535 | 58.2055 | 1.2209 | 1.3303 | 0.91294
23.1375 | 58.7912 | 58.8279 | 58.2256 | 1.2199 | 1.3288 | 0.91193
23.1417 | 58.791 | 58.9075 | 58.2384 | 1.2189 | 1.3274 | 0.91108
23.1459 | 58.8082 | 58.8898 | 58.2449 | 1.2182 | 1.3266 | 0.91052
23.15 | 58.7967 | 58.8595 | 58.2442 | 1.2174 | 1.3257 | 0.90986
23.1542 | 58.7809 | 58.8197 | 58.2202 | 1.2167 | 1.324 | 0.90894
23.1584 | 58.7807 | 58.7941 | 58.2156 | 1.2157 | 1.3222 | 0.90805
23.1625 | 58.7969 | 58.8394 | 58.2374 | 1.2148 | 1.3212 | 0.90729
23.1667 | 58.806 | 58.8821 | 58.2469 | 1.214 | 1.3202 | 0.90659
23.1709 | 58.8067 | 58.8561 | 58.2399 | 1.2134 | 1.3191 | 0.90595
23.175 | 58.791 | 58.826 | 58.2305 | 1.2126 | 1.3178 | 0.90522
23.1792 | 58.767 | 58.8581 | 58.2304 | 1.2118 | 1.3162 | 0.90431
23.1834 | 58.7631 | 58.9003 | 58.2389 | 1.2109 | 1.3146 | 0.9035
23.1875 | 58.7728 | 58.9002 | 58.2466 | 1.2102 | 1.3137 | 0.90288
23.1917 | 58.7661 | 58.8865 | 58.2447 | 1.2096 | 1.3128 | 0.90226
23.1959 | 58.753 | 58.8521 | 58.2346 | 1.2091 | 1.3112 | 0.90148
23.2 | 58.7496 | 58.8195 | 58.2299 | 1.2083 | 1.3096 | 0.90066
23.2042 | 58.7491 | 58.8377 | 58.241 | 1.2075 | 1.3086 | 0.89992
23.2084 | 58.7685 | 58.8581 | 58.2523 | 1.2067 | 1.3077 | 0.89925
23.2125 | 58.7813 | 58.8 | 58.2476 | 1.2062 | 1.3069 | 0.89861
23.2167 | 58.7737 | 58.7316 | 58.2402 | 1.2055 | 1.3061 | 0.89793
23.2209 | 58.7562 | 58.7175 | 58.2368 | 1.2049 | 1.3051 | 0.89715
23.225 | 58.7554 | 58.7126 | 58.2428 | 1.204 | 1.304 | 0.89637
23.2292 | 58.7636 | 58.7125 | 58.2488 | 1.2032 | 1.3038 | 0.89574
23.2334 | 58.7763 | 58.7085 | 58.2499 | 1.2025 | 1.3036 | 0.89513
23.2375 | 58.7864 | 58.6702 | 58.2474 | 1.2019 | 1.3029 | 0.89443
23.2417 | 58.7758 | 58.6309 | 58.2429 | 1.2011 | 1.3022 | 0.89366
23.2459 | 58.7841 | 58.6477 | 58.2465 | 1.2003 | 1.3018 | 0.89298
23.25 | 58.7945 | 58.6739 | 58.2535 | 1.1993 | 1.3014 | 0.89233
23.2542 | 58.8047 | 58.6502 | 58.2562 | 1.1986 | 1.3012 | 0.89165
23.2584 | 58.8051 | 58.6162 | 58.2519 | 1.1979 | 1.3011 | 0.89098
23.2625 | 58.7879 | 58.5927 | 58.249 | 1.1971 | 1.3007 | 0.89031
23.2667 | 58.7665 | 58.5708 | 58.2529 | 1.1963 | 1.3002 | 0.8896
23.2709 | 58.7644 | 58.5805 | 58.2486 | 1.1955 | 1.3002 | 0.88895
23.275 | 58.7711 | 58.5935 | 58.2471 | 1.1947 | 1.3002 | 0.88835
23.2792 | 58.7697 | 58.6052 | 58.2536 | 1.1941 | 1.2998 | 0.88767
23.2834 | 58.7664 | 58.6116 | 58.2513 | 1.1935 | 1.2994 | 0.88697
23.2875 | 58.7678 | 58.6624 | 58.2469 | 1.1927 | 1.2988 | 0.88641
23.2917 | 58.7565 | 58.7228 | 58.2481 | 1.192 | 1.2982 | 0.88583
23.2959 | 58.7637 | 58.7643 | 58.2486 | 1.1913 | 1.2974 | 0.88512
23.3 | 58.7672 | 58.8059 | 58.2431 | 1.1907 | 1.2966 | 0.88449
23.3042 | 58.7364 | 58.8294 | 58.2514 | 1.1901 | 1.2954 | 0.88392
23.3084 | 58.7287 | 58.8498 | 58.2547 | 1.1895 | 1.2941 | 0.88331
23.3125 | 58.7254 | 58.838 | 58.2439 | 1.1889 | 1.2931 | 0.8827
23.3167 | 58.7229 | 58.8308 | 58.2411 | 1.1882 | 1.292 | 0.88216
23.3209 | 58.7448 | 58.7771 | 58.2488 | 1.1877 | 1.2911 | 0.88147
23.325 | 58.7443 | 58.7164 | 58.2499 | 1.1872 | 1.2902 | 0.88084
23.3292 | 58.728 | 58.6649 | 58.249 | 1.1866 | 1.2897 | 0.88034
23.3334 | 58.729 | 58.6127 | 58.2514 | 1.186 | 1.2892 | 0.87981
23.3375 | 58.7264 | 58.5565 | 58.2442 | 1.1853 | 1.2891 | 0.87913
23.3417 | 58.7321 | 58.5026 | 58.2414 | 1.1847 | 1.2891 | 0.87853
23.3459 | 58.735 | 58.4747 | 58.2496 | 1.1843 | 1.2892 | 0.87798
23.35 | 58.7178 | 58.4423 | 58.2537 | 1.1838 | 1.2894 | 0.8774
23.3542 | 58.7065 | 58.4529 | 58.2425 | 1.1832 | 1.2896 | 0.87689
23.3584 | 58.7054 | 58.4688 | 58.2393 | 1.1826 | 1.2899 | 0.87635
23.3625 | 58.7144 | 58.4898 | 58.2411 | 1.182 | 1.29 | 0.87573
23.3667 | 58.7178 | 58.5122 | 58.2406 | 1.1816 | 1.2901 | 0.87513
23.3709 | 58.7239 | 58.5607 | 58.2427 | 1.1811 | 1.2898 | 0.8747
23.375 | 58.7149 | 58.6067 | 58.242 | 1.1805 | 1.2895 | 0.87419
23.3792 | 58.7185 | 58.6492 | 58.2361 | 1.1799 | 1.289 | 0.87361
23.3834 | 58.7308 | 58.6961 | 58.2314 | 1.1793 | 1.2885 | 0.87307
23.3875 | 58.7346 | 58.6941 | 58.2398 | 1.1787 | 1.2878 | 0.87255
23.3917 | 58.7257 | 58.6885 | 58.2429 | 1.1782 | 1.2872 | 0.87203
23.3959 | 58.7197 | 58.6731 | 58.2353 | 1.1776 | 1.2865 | 0.87156
23.4 | 58.7066 | 58.656 | 58.2314 | 1.177 | 1.2858 | 0.87109
23.4042 | 58.7004 | 58.6321 | 58.2324 | 1.1764 | 1.2853 | 0.8705
23.4084 | 58.6991 | 58.6115 | 58.2322 | 1.176 | 1.2849 | 0.86996
23.4125 | 58.6902 | 58.5748 | 58.2345 | 1.1755 | 1.2846 | 0.86953
23.4167 | 58.6807 | 58.5351 | 58.2386 | 1.1751 | 1.2843 | 0.86906
23.4209 | 58.6838 | 58.5193 | 58.2344 | 1.1745 | 1.2841 | 0.8685
23.425 | 58.6936 | 58.5042 | 58.2312 | 1.174 | 1.284 | 0.86799
23.4292 | 58.6937 | 58.4932 | 58.2341 | 1.1735 | 1.284 | 0.86752
23.4334 | 58.6936 | 58.4809 | 58.2274 | 1.1732 | 1.2841 | 0.86707
23.4375 | 58.6835 | 58.4761 | 58.206 | 1.1726 | 1.2841 | 0.86672
23.4417 | 58.6907 | 58.4764 | 58.2053 | 1.172 | 1.284 | 0.86624
23.4459 | 58.7051 | 58.516 | 58.2269 | 1.1714 | 1.2837 | 0.86556
23.45 | 58.7286 | 58.5622 | 58.2526 | 1.1708 | 1.2835 | 0.86495
23.4542 | 58.7428 | 58.5843 | 58.2866 | 1.1703 | 1.2833 | 0.86449
23.4584 | 58.7231 | 58.587 | 58.2809 | 1.1697 | 1.2831 | 0.86407
23.4625 | 58.6971 | 58.5729 | 58.2306 | 1.1692 | 1.2826 | 0.86366
23.4667 | 58.676 | 58.5591 | 58.19 | 1.1686 | 1.2821 | 0.86319
23.4709 | 58.6524 | 58.5602 | 58.1679 | 1.1681 | 1.2817 | 0.86265
23.475 | 58.6724 | 58.5906 | 58.1922 | 1.1675 | 1.2812 | 0.86207
23.4792 | 58.7101 | 58.6156 | 58.2572 | 1.1669 | 1.2807 | 0.8615
23.4834 | 58.7403 | 58.6374 | 58.3179 | 1.1662 | 1.2801 | 0.86085
23.4875 | 58.7849 | 58.6735 | 58.3728 | 1.1656 | 1.2793 | 0.86004
23.4917 | 58.7999 | 58.6938 | 58.3955 | 1.1647 | 1.2784 | 0.85911
23.4959 | 58.7997 | 58.6963 | 58.3888 | 1.1638 | 1.2776 | 0.85815
23.5 | 58.8057 | 58.7042 | 58.3861 | 1.1628 | 1.2768 | 0.85712
23.5042 | 58.8198 | 58.7076 | 58.387 | 1.1617 | 1.2757 | 0.85595
23.5084 | 58.8418 | 58.7169 | 58.4016 | 1.1606 | 1.2746 | 0.85482
23.5125 | 58.8721 | 58.7392 | 58.4362 | 1.1595 | 1.2737 | 0.85372
23.5167 | 58.9251 | 58.7763 | 58.4863 | 1.1581 | 1.2725 | 0.85239
23.5209 | 58.9766 | 58.8078 | 58.5403 | 1.1565 | 1.2712 | 0.85089
23.525 | 59.0657 | 58.8611 | 58.6287 | 1.1545 | 1.2696 | 0.84904
23.5292 | 59.1721 | 58.9628 | 58.7546 | 1.1524 | 1.2677 | 0.84679
23.5334 | 59.2603 | 59.0581 | 58.8699 | 1.1499 | 1.2655 | 0.84433
23.5375 | 59.3447 | 59.1417 | 58.974 | 1.1474 | 1.2633 | 0.84178
23.5417 | 59.4013 | 59.2053 | 59.0472 | 1.1444 | 1.2609 | 0.83894
23.5459 | 59.4396 | 59.2424 | 59.0833 | 1.1413 | 1.258 | 0.83575
23.55 | 59.4589 | 59.2618 | 59.1074 | 1.1381 | 1.255 | 0.83256
23.5542 | 59.4668 | 59.2964 | 59.1336 | 1.1351 | 1.252 | 0.82939
23.5584 | 59.4337 | 59.3077 | 59.1324 | 1.1321 | 1.2491 | 0.8264
23.5625 | 59.3917 | 59.2689 | 59.0958 | 1.1293 | 1.2464 | 0.82364
23.5667 | 59.3448 | 59.2225 | 59.054 | 1.1266 | 1.2438 | 0.82101
23.5709 | 59.2944 | 59.1728 | 59.0117 | 1.1241 | 1.2411 | 0.81837
23.575 | 59.2579 | 59.1313 | 58.9846 | 1.122 | 1.2386 | 0.81596
23.5792 | 59.2227 | 59.0982 | 58.9756 | 1.1199 | 1.2366 | 0.81389
23.5834 | 59.1969 | 59.0728 | 58.9713 | 1.118 | 1.2347 | 0.81191
23.5875 | 59.1807 | 59.0401 | 58.9605 | 1.1162 | 1.2328 | 0.80995
23.5917 | 59.1823 | 59.0179 | 58.9576 | 1.1144 | 1.231 | 0.80803
23.5959 | 59.1901 | 59.0255 | 58.9753 | 1.1127 | 1.2292 | 0.8061
23.6 | 59.2057 | 59.0435 | 59.0008 | 1.1109 | 1.2275 | 0.80417
23.6042 | 59.2242 | 59.0469 | 59.0241 | 1.1092 | 1.2259 | 0.80231
23.6084 | 59.2466 | 59.0506 | 59.0459 | 1.1073 | 1.2243 | 0.80044
23.6125 | 59.2672 | 59.0702 | 59.066 | 1.1055 | 1.2224 | 0.79842
23.6167 | 59.2817 | 59.0851 | 59.078 | 1.1036 | 1.2204 | 0.7964
23.6209 | 59.2886 | 59.1076 | 59.0911 | 1.1017 | 1.2187 | 0.79447
23.625 | 59.2967 | 59.131 | 59.1092 | 1.0997 | 1.2169 | 0.79249
23.6292 | 59.3067 | 59.1286 | 59.1194 | 1.0978 | 1.215 | 0.79045
23.6334 | 59.3109 | 59.1206 | 59.1243 | 1.0958 | 1.2131 | 0.78851
23.6375 | 59.3157 | 59.1351 | 59.1341 | 1.094 | 1.2111 | 0.78662
23.6417 | 59.3032 | 59.1452 | 59.1369 | 1.0921 | 1.2092 | 0.78469
23.6459 | 59.2969 | 59.1434 | 59.1295 | 1.0903 | 1.2074 | 0.78284
23.65 | 59.2985 | 59.1477 | 59.1362 | 1.0884 | 1.2056 | 0.78101
23.6542 | 59.3078 | 59.146 | 59.1526 | 1.0865 | 1.2036 | 0.7791
23.6584 | 59.3095 | 59.1381 | 59.1564 | 1.0849 | 1.2017 | 0.77731
23.6625 | 59.3009 | 59.1431 | 59.1572 | 1.0832 | 1.1999 | 0.7757
23.6667 | 59.2973 | 59.1503 | 59.1602 | 1.0815 | 1.1981 | 0.77398
23.6709 | 59.2969 | 59.1475 | 59.1563 | 1.0797 | 1.1963 | 0.77215
23.675 | 59.3095 | 59.1513 | 59.1645 | 1.078 | 1.1945 | 0.77044
23.6792 | 59.3205 | 59.1549 | 59.1908 | 1.0764 | 1.1927 | 0.76878
23.6834 | 59.3166 | 59.1486 | 59.1987 | 1.0748 | 1.191 | 0.76713
23.6875 | 59.2973 | 59.137 | 59.1851 | 1.0732 | 1.1893 | 0.76561
23.6917 | 59.2995 | 59.1327 | 59.1844 | 1.0715 | 1.1876 | 0.76401
23.6959 | 59.313 | 59.1401 | 59.1932 | 1.0698 | 1.1859 | 0.76222
23.7 | 59.3215 | 59.1485 | 59.1995 | 1.0682 | 1.1842 | 0.76061
23.7042 | 59.3301 | 59.1451 | 59.2152 | 1.0668 | 1.1827 | 0.75922
23.7084 | 59.3201 | 59.1326 | 59.2215 | 1.0652 | 1.1812 | 0.75772
23.7125 | 59.302 | 59.1209 | 59.2057 | 1.0636 | 1.1795 | 0.75614
23.7167 | 59.3127 | 59.1202 | 59.2101 | 1.062 | 1.1778 | 0.75459
23.7209 | 59.329 | 59.1438 | 59.2346 | 1.0605 | 1.1762 | 0.75301
23.725 | 59.3266 | 59.1616 | 59.237 | 1.0591 | 1.1748 | 0.75157
23.7292 | 59.324 | 59.152 | 59.2276 | 1.0577 | 1.1733 | 0.75033
23.7334 | 59.3144 | 59.1393 | 59.219 | 1.0562 | 1.1718 | 0.74895
23.7375 | 59.3071 | 59.1385 | 59.2029 | 1.0546 | 1.1701 | 0.74743
23.7417 | 59.3188 | 59.1476 | 59.2057 | 1.0532 | 1.1684 | 0.74607
23.7459 | 59.3346 | 59.1701 | 59.2333 | 1.0518 | 1.1669 | 0.74479
23.75 | 59.3299 | 59.1824 | 59.2397 | 1.0504 | 1.1655 | 0.74353
23.7542 | 59.3231 | 59.1773 | 59.2259 | 1.049 | 1.1639 | 0.74236
23.7584 | 59.3276 | 59.1761 | 59.2219 | 1.0476 | 1.1622 | 0.74112
23.7625 | 59.3345 | 59.1807 | 59.2187 | 1.046 | 1.1605 | 0.73974
23.7667 | 59.3372 | 59.1891 | 59.2167 | 1.0447 | 1.159 | 0.73854
23.7709 | 59.3406 | 59.1834 | 59.2182 | 1.0435 | 1.1575 | 0.73757
23.775 | 59.3245 | 59.1683 | 59.2034 | 1.0421 | 1.156 | 0.73656
23.7792 | 59.3086 | 59.1802 | 59.1795 | 1.0407 | 1.1543 | 0.73549
23.7834 | 59.3174 | 59.2008 | 59.1663 | 1.0394 | 1.1526 | 0.73449
23.7875 | 59.3345 | 59.2168 | 59.1775 | 1.038 | 1.1511 | 0.73348
23.7917 | 59.3493 | 59.2305 | 59.1873 | 1.0367 | 1.1497 | 0.73256
23.7959 | 59.3416 | 59.1904 | 59.1721 | 1.0356 | 1.1482 | 0.73186
23.8 | 59.3344 | 59.1458 | 59.1644 | 1.0343 | 1.1467 | 0.73108
23.8042 | 59.3207 | 59.1568 | 59.1632 | 1.0329 | 1.1451 | 0.73003
23.8084 | 59.3188 | 59.1758 | 59.1678 | 1.0316 | 1.1434 | 0.72905
23.8125 | 59.3288 | 59.2009 | 59.2008 | 1.0305 | 1.1421 | 0.72824
23.8167 | 59.3282 | 59.22 | 59.2217 | 1.0293 | 1.1409 | 0.72739
23.8209 | 59.3255 | 59.2033 | 59.2156 | 1.0281 | 1.1393 | 0.72645
23.825 | 59.3295 | 59.1871 | 59.218 | 1.0268 | 1.1377 | 0.72546
23.8292 | 59.3396 | 59.1661 | 59.2183 | 1.0255 | 1.1365 | 0.72444
23.8334 | 59.342 | 59.1491 | 59.2221 | 1.0244 | 1.1353 | 0.72345
23.8375 | 59.3389 | 59.136 | 59.229 | 1.0232 | 1.134 | 0.72256
23.8417 | 59.3235 | 59.1183 | 59.2265 | 1.0221 | 1.1327 | 0.72163
23.8459 | 59.3116 | 59.1662 | 59.2333 | 1.0209 | 1.1312 | 0.72061
23.85 | 59.3116 | 59.2172 | 59.2356 | 1.0198 | 1.1298 | 0.71962
23.8542 | 59.3207 | 59.2095 | 59.2332 | 1.0186 | 1.1287 | 0.71875
23.8584 | 59.3259 | 59.2007 | 59.2356 | 1.0176 | 1.1277 | 0.71788
23.8625 | 59.3338 | 59.1672 | 59.228 | 1.0165 | 1.1261 | 0.71692
23.8667 | 59.3408 | 59.1315 | 59.2268 | 1.0153 | 1.1246 | 0.71598
23.8709 | 59.3336 | 59.1594 | 59.2329 | 1.0142 | 1.1234 | 0.71513
23.875 | 59.3325 | 59.19 | 59.2317 | 1.0131 | 1.1222 | 0.71429
23.8792 | 59.3261 | 59.1851 | 59.2308 | 1.012 | 1.121 | 0.71344
23.8834 | 59.3174 | 59.1789 | 59.232 | 1.0109 | 1.1199 | 0.71255
23.8875 | 59.3155 | 59.2026 | 59.2392 | 1.0099 | 1.1183 | 0.71163
23.8917 | 59.3209 | 59.2264 | 59.2457 | 1.0089 | 1.1167 | 0.71079
23.8959 | 59.3177 | 59.2389 | 59.246 | 1.0078 | 1.1155 | 0.71
23.9 | 59.3187 | 59.2512 | 59.2428 | 1.0068 | 1.1143 | 0.70916
23.9042 | 59.3226 | 59.2296 | 59.2378 | 1.0058 | 1.1127 | 0.70827
23.9084 | 59.3327 | 59.2069 | 59.2449 | 1.0047 | 1.1112 | 0.70737
23.9125 | 59.3331 | 59.2303 | 59.2521 | 1.0037 | 1.1097 | 0.70654
23.9167 | 59.3294 | 59.2517 | 59.25 | 1.0027 | 1.1083 | 0.70579
23.9209 | 59.3279 | 59.2434 | 59.2486 | 1.0017 | 1.107 | 0.705
23.925 | 59.3164 | 59.2345 | 59.2452 | 1.0006 | 1.1058 | 0.7041
23.9292 | 59.3087 | 59.2355 | 59.248 | 0.99974 | 1.1041 | 0.70324
23.9334 | 59.3072 | 59.2389 | 59.2581 | 0.99885 | 1.1026 | 0.70246
23.9375 | 59.3099 | 59.2355 | 59.2634 | 0.99783 | 1.1014 | 0.70167
23.9417 | 59.3027 | 59.2305 | 59.2576 | 0.99693 | 1.1003 | 0.70089
23.9459 | 59.3146 | 59.1819 | 59.2475 | 0.996 | 1.0991 | 0.70012
23.95 | 59.3275 | 59.136 | 59.2508 | 0.99502 | 1.0979 | 0.69927
23.9542 | 59.3215 | 59.1605 | 59.2574 | 0.99408 | 1.0967 | 0.69841
23.9584 | 59.3153 | 59.1858 | 59.2605 | 0.99327 | 1.0954 | 0.69769
23.9625 | 59.3176 | 59.188 | 59.2676 | 0.99227 | 1.0946 | 0.69698
23.9667 | 59.3111 | 59.188 | 59.2639 | 0.99124 | 1.0938 | 0.69616
23.9709 | 59.3062 | 59.1704 | 59.2501 | 0.99042 | 1.0925 | 0.6954
23.975 | 59.3212 | 59.157 | 59.2531 | 0.98954 | 1.0912 | 0.69466
23.9792 | 59.3076 | 59.2022 | 59.2681 | 0.98867 | 1.09 | 0.6938
23.9834 | 59.2928 | 59.2427 | 59.2675 | 0.98781 | 1.0889 | 0.69305
23.9875 | 59.2926 | 59.2076 | 59.2667 | 0.98705 | 1.088 | 0.69244
23.9917 | 59.2906 | 59.1725 | 59.2693 | 0.98607 | 1.0871 | 0.69168
23.9959 | 59.2941 | 59.1655 | 59.2568 | 0.98528 | 1.0857 | 0.69083
24 | 59.3024 | 59.1636 | 59.2584 | 0.98448 | 1.0842 | 0.69011
24.0042 | 59.3089 | 59.1898 | 59.2753 | 0.98367 | 1.0835 | 0.68939
24.0084 | 59.303 | 59.2095 | 59.2737 | 0.98276 | 1.0827 | 0.68865
24.0125 | 59.2895 | 59.1786 | 59.2598 | 0.98206 | 1.0816 | 0.68805
24.0167 | 59.292 | 59.1535 | 59.2567 | 0.98119 | 1.0804 | 0.68736
24.0209 | 59.2857 | 59.2141 | 59.2685 | 0.98038 | 1.0789 | 0.68643
24.025 | 59.2772 | 59.2749 | 59.2745 | 0.97961 | 1.0775 | 0.68568
24.0292 | 59.2835 | 59.2541 | 59.2804 | 0.97897 | 1.0769 | 0.68517
24.0334 | 59.2745 | 59.2263 | 59.2805 | 0.97815 | 1.0761 | 0.68452
24.0375 | 59.2668 | 59.1803 | 59.2546 | 0.97746 | 1.0746 | 0.68375
24.0417 | 59.273 | 59.1459 | 59.2488 | 0.97669 | 1.073 | 0.68302
24.0459 | 59.2858 | 59.215 | 59.2782 | 0.9759 | 1.0719 | 0.68223
24.05 | 59.2848 | 59.2797 | 59.2878 | 0.97515 | 1.0709 | 0.68154
24.0542 | 59.2819 | 59.2312 | 59.2757 | 0.97456 | 1.0702 | 0.68109
24.0584 | 59.274 | 59.1812 | 59.269 | 0.97379 | 1.0693 | 0.68048
24.0625 | 59.2563 | 59.1942 | 59.2594 | 0.97307 | 1.0676 | 0.67957
24.0667 | 59.2497 | 59.215 | 59.2607 | 0.97238 | 1.0659 | 0.6788
24.0709 | 59.2584 | 59.251 | 59.2859 | 0.97173 | 1.0653 | 0.67826
24.075 | 59.2526 | 59.2731 | 59.2911 | 0.97108 | 1.0646 | 0.67769
24.0792 | 59.2401 | 59.2003 | 59.2657 | 0.97058 | 1.0634 | 0.67708
24.0834 | 59.2459 | 59.1315 | 59.2555 | 0.96989 | 1.0622 | 0.6764
24.0875 | 59.2485 | 59.1637 | 59.2707 | 0.96914 | 1.061 | 0.67555
24.0917 | 59.2558 | 59.1975 | 59.2827 | 0.96848 | 1.0599 | 0.67486
24.0959 | 59.2673 | 59.1534 | 59.285 | 0.96795 | 1.0597 | 0.67445
24.1 | 59.2662 | 59.0981 | 59.2802 | 0.96724 | 1.0595 | 0.67391
24.1042 | 59.2402 | 59.0519 | 59.261 | 0.96666 | 1.0584 | 0.67312
24.1084 | 59.2451 | 59.0164 | 59.2594 | 0.96591 | 1.0573 | 0.67236
24.1125 | 59.259 | 59.0545 | 59.2817 | 0.96516 | 1.0571 | 0.67176
24.1167 | 59.2595 | 59.0878 | 59.2913 | 0.96445 | 1.057 | 0.6712
24.1209 | 59.272 | 59.0292 | 59.2772 | 0.96397 | 1.0568 | 0.67069
24.125 | 59.2724 | 58.9702 | 59.2643 | 0.96317 | 1.0565 | 0.67007
24.1292 | 59.2651 | 58.9983 | 59.2692 | 0.96235 | 1.0557 | 0.66926
24.1334 | 59.2745 | 59.0364 | 59.2791 | 0.96158 | 1.055 | 0.66856
24.1375 | 59.2931 | 59.0372 | 59.2886 | 0.96081 | 1.0552 | 0.6681
24.1417 | 59.2802 | 59.0253 | 59.2866 | 0.96013 | 1.0554 | 0.66761
24.1459 | 59.2579 | 58.9715 | 59.2688 | 0.95955 | 1.0548 | 0.66693
24.15 | 59.2495 | 58.923 | 59.2628 | 0.95878 | 1.0542 | 0.66621
24.1542 | 59.2346 | 58.9767 | 59.2752 | 0.95798 | 1.0539 | 0.66558
24.1584 | 59.2421 | 59.0324 | 59.2851 | 0.95734 | 1.0537 | 0.66504
24.1625 | 59.2631 | 59.0199 | 59.2805 | 0.95676 | 1.0536 | 0.66455
24.1667 | 59.2465 | 58.9995 | 59.2693 | 0.95616 | 1.0535 | 0.66399
24.1709 | 59.2394 | 59.0312 | 59.2635 | 0.95556 | 1.0524 | 0.66332
24.175 | 59.236 | 59.0768 | 59.2665 | 0.95485 | 1.0514 | 0.66268
24.1792 | 59.2254 | 59.1461 | 59.2779 | 0.9542 | 1.0508 | 0.66214
24.1834 | 59.2343 | 59.2107 | 59.2782 | 0.95365 | 1.0503 | 0.66167
24.1875 | 59.2219 | 59.1808 | 59.2708 | 0.95319 | 1.0493 | 0.66112
24.1917 | 59.2062 | 59.1487 | 59.2642 | 0.95264 | 1.0481 | 0.66052
24.1959 | 59.2047 | 59.154 | 59.263 | 0.95205 | 1.047 | 0.65991
24.2 | 59.2049 | 59.1673 | 59.2694 | 0.95142 | 1.0458 | 0.65939
24.2042 | 59.2141 | 59.1241 | 59.2758 | 0.95094 | 1.0454 | 0.65885
24.2084 | 59.2227 | 59.0685 | 59.2717 | 0.95045 | 1.045 | 0.65834
24.2125 | 59.208 | 58.9891 | 59.2642 | 0.94997 | 1.0444 | 0.65781
24.2167 | 59.2008 | 58.9136 | 59.2652 | 0.94939 | 1.0438 | 0.65724
24.2209 | 59.2059 | 58.9003 | 59.2654 | 0.94878 | 1.0438 | 0.65665
24.225 | 59.2096 | 58.8885 | 59.2675 | 0.94816 | 1.0439 | 0.65616
24.2292 | 59.2093 | 58.8527 | 59.2715 | 0.94778 | 1.0442 | 0.65566
24.2334 | 59.201 | 58.8095 | 59.2686 | 0.9473 | 1.0445 | 0.65511
24.2375 | 59.1847 | 58.8113 | 59.2573 | 0.94677 | 1.0445 | 0.65462
24.2417 | 59.1762 | 58.8239 | 59.2591 | 0.94618 | 1.0445 | 0.65411
24.2459 | 59.1937 | 58.8737 | 59.2625 | 0.94564 | 1.0447 | 0.65355
24.25 | 59.1995 | 58.9203 | 59.2591 | 0.94517 | 1.0449 | 0.65305
24.2542 | 59.1969 | 58.9504 | 59.2619 | 0.94476 | 1.0446 | 0.65263
24.2584 | 59.1899 | 58.9793 | 59.2604 | 0.94429 | 1.0442 | 0.65211
24.2625 | 59.1881 | 59.0151 | 59.2517 | 0.94359 | 1.0436 | 0.6516
24.2667 | 59.1957 | 59.0583 | 59.2515 | 0.94299 | 1.043 | 0.65113
24.2709 | 59.2123 | 59.0608 | 59.2626 | 0.94244 | 1.0424 | 0.6506
24.275 | 59.2078 | 59.0535 | 59.2602 | 0.94203 | 1.0418 | 0.65011
24.2792 | 59.1866 | 59.0252 | 59.2514 | 0.94152 | 1.0411 | 0.64974
24.2834 | 59.1685 | 58.9998 | 59.2474 | 0.94099 | 1.0404 | 0.6493
24.2875 | 59.1626 | 58.979 | 59.2398 | 0.94034 | 1.04 | 0.64874
24.2917 | 59.1716 | 58.9646 | 59.2443 | 0.93987 | 1.0395 | 0.64824
24.2959 | 59.1794 | 58.9356 | 59.2682 | 0.93944 | 1.0393 | 0.64774
24.3 | 59.1718 | 58.8968 | 59.2777 | 0.93909 | 1.0391 | 0.64725
24.3042 | 59.1593 | 58.8725 | 59.2646 | 0.93858 | 1.0389 | 0.64686
24.3084 | 59.1521 | 58.8472 | 59.2454 | 0.93807 | 1.0388 | 0.64648
24.3125 | 59.1439 | 58.833 | 59.2184 | 0.93763 | 1.0389 | 0.64601
24.3167 | 59.1548 | 58.8267 | 59.2086 | 0.93721 | 1.0389 | 0.64552
24.3209 | 59.1565 | 58.8392 | 59.222 | 0.93678 | 1.0389 | 0.64512
24.325 | 59.1723 | 58.8604 | 59.2541 | 0.93617 | 1.0387 | 0.64461
24.3292 | 59.2024 | 58.9078 | 59.2959 | 0.93552 | 1.0384 | 0.644
24.3334 | 59.2154 | 58.9451 | 59.3097 | 0.93489 | 1.0382 | 0.64348
24.3375 | 59.2138 | 58.9506 | 59.3042 | 0.93444 | 1.0379 | 0.64302
24.3417 | 59.1831 | 58.9399 | 59.2721 | 0.93392 | 1.0376 | 0.64253
24.3459 | 59.1397 | 58.9211 | 59.2121 | 0.93339 | 1.0371 | 0.6421
24.35 | 59.1326 | 58.924 | 59.1961 | 0.93269 | 1.0365 | 0.64161
24.3542 | 59.149 | 58.9486 | 59.225 | 0.9321 | 1.0359 | 0.64095
24.3584 | 59.1818 | 58.9861 | 59.268 | 0.93155 | 1.0354 | 0.64036
24.3625 | 59.2165 | 59.0015 | 59.3268 | 0.93106 | 1.0349 | 0.63991
24.3667 | 59.231 | 59.0049 | 59.3671 | 0.9303 | 1.0342 | 0.63922
24.3709 | 59.249 | 59.0252 | 59.3788 | 0.92941 | 1.0333 | 0.63825
24.375 | 59.276 | 59.0512 | 59.3973 | 0.92837 | 1.0322 | 0.6372
24.3792 | 59.3059 | 59.0808 | 59.434 | 0.92734 | 1.0313 | 0.63603
24.3834 | 59.3202 | 59.104 | 59.4524 | 0.92637 | 1.0304 | 0.63492
24.3875 | 59.3258 | 59.0923 | 59.4491 | 0.92529 | 1.0294 | 0.63396
24.3917 | 59.3398 | 59.0803 | 59.4511 | 0.92396 | 1.0282 | 0.63282
24.3959 | 59.3571 | 59.0986 | 59.4561 | 0.92258 | 1.027 | 0.6314
24.4 | 59.4174 | 59.1433 | 59.4963 | 0.92104 | 1.0255 | 0.6299
24.4042 | 59.4805 | 59.1964 | 59.5764 | 0.91944 | 1.0242 | 0.62839
24.4084 | 59.5438 | 59.2528 | 59.6587 | 0.91754 | 1.0227 | 0.62667
24.4125 | 59.6157 | 59.3143 | 59.7328 | 0.91549 | 1.0208 | 0.62472
24.4167 | 59.6829 | 59.3695 | 59.8014 | 0.91301 | 1.0186 | 0.62248
24.4209 | 59.7435 | 59.4394 | 59.87 | 0.91052 | 1.0163 | 0.61994
24.425 | 59.7929 | 59.5017 | 59.9261 | 0.90784 | 1.0139 | 0.6173
24.4292 | 59.8245 | 59.5357 | 59.9675 | 0.90509 | 1.0114 | 0.61465
24.4334 | 59.817 | 59.5416 | 59.9817 | 0.90229 | 1.0088 | 0.61199
24.4375 | 59.8063 | 59.5509 | 59.9707 | 0.89955 | 1.006 | 0.60924
24.4417 | 59.7722 | 59.5438 | 59.9417 | 0.89694 | 1.0033 | 0.60664
24.4459 | 59.7239 | 59.5027 | 59.9008 | 0.89448 | 1.0008 | 0.60424
24.45 | 59.6782 | 59.4625 | 59.8644 | 0.89228 | 0.99866 | 0.602
24.4542 | 59.6304 | 59.4053 | 59.8258 | 0.89015 | 0.99636 | 0.59988
24.4584 | 59.5873 | 59.3479 | 59.7933 | 0.8883 | 0.99427 | 0.59797
24.4625 | 59.5509 | 59.3223 | 59.7733 | 0.88663 | 0.99249 | 0.59624
24.4667 | 59.5308 | 59.309 | 59.7581 | 0.88507 | 0.99081 | 0.59457
24.4709 | 59.5107 | 59.2721 | 59.7433 | 0.88356 | 0.98935 | 0.59302
24.475 | 59.5165 | 59.2514 | 59.7478 | 0.88208 | 0.98794 | 0.59147
24.4792 | 59.5345 | 59.2567 | 59.7705 | 0.88062 | 0.98637 | 0.58982
24.4834 | 59.5517 | 59.2638 | 59.7905 | 0.87912 | 0.98478 | 0.58822
24.4875 | 59.5676 | 59.2847 | 59.8103 | 0.8777 | 0.98347 | 0.58674
24.4917 | 59.5873 | 59.3081 | 59.826 | 0.87606 | 0.98207 | 0.58513
24.4959 | 59.602 | 59.3155 | 59.832 | 0.87439 | 0.98044 | 0.58337
24.5 | 59.622 | 59.3224 | 59.8448 | 0.87266 | 0.97877 | 0.58163
24.5042 | 59.6423 | 59.3519 | 59.8723 | 0.871 | 0.97709 | 0.57988
24.5084 | 59.6451 | 59.3721 | 59.8849 | 0.86926 | 0.97538 | 0.57817
24.5125 | 59.6425 | 59.3694 | 59.8769 | 0.86757 | 0.97375 | 0.57655
24.5167 | 59.6372 | 59.3661 | 59.8713 | 0.86578 | 0.9721 | 0.57488
24.5209 | 59.642 | 59.3713 | 59.87 | 0.86401 | 0.97019 | 0.57305
24.525 | 59.6348 | 59.3748 | 59.8726 | 0.86236 | 0.96834 | 0.57133
24.5292 | 59.6341 | 59.378 | 59.8834 | 0.86077 | 0.96675 | 0.56981
24.5334 | 59.625 | 59.3772 | 59.8854 | 0.85918 | 0.96518 | 0.56828
24.5375 | 59.6121 | 59.3585 | 59.8685 | 0.85753 | 0.96344 | 0.56671
24.5417 | 59.6131 | 59.3444 | 59.8591 | 0.856 | 0.96172 | 0.56516
24.5459 | 59.6207 | 59.3611 | 59.8694 | 0.85441 | 0.96002 | 0.56357
24.55 | 59.6196 | 59.3782 | 59.8786 | 0.85296 | 0.95836 | 0.56205
24.5542 | 59.6152 | 59.3646 | 59.8815 | 0.8515 | 0.95692 | 0.56069
24.5584 | 59.6178 | 59.3501 | 59.8841 | 0.85001 | 0.95547 | 0.55929
24.5625 | 59.6082 | 59.3425 | 59.8806 | 0.84848 | 0.95374 | 0.55774
24.5667 | 59.6137 | 59.3373 | 59.8787 | 0.84706 | 0.95202 | 0.55626
24.5709 | 59.618 | 59.3524 | 59.8878 | 0.84564 | 0.9506 | 0.55489
24.575 | 59.6142 | 59.3669 | 59.8912 | 0.8442 | 0.94919 | 0.55353
24.5792 | 59.616 | 59.3453 | 59.8842 | 0.84278 | 0.94773 | 0.55216
24.5834 | 59.6193 | 59.3223 | 59.8815 | 0.84133 | 0.94627 | 0.55079
24.5875 | 59.6159 | 59.3254 | 59.8859 | 0.83996 | 0.94474 | 0.5494
24.5917 | 59.6156 | 59.3289 | 59.8928 | 0.83859 | 0.9432 | 0.54803
24.5959 | 59.6133 | 59.337 | 59.8989 | 0.83721 | 0.94188 | 0.54675
24.6 | 59.6138 | 59.3463 | 59.9012 | 0.83578 | 0.94056 | 0.54546
24.6042 | 59.6192 | 59.3403 | 59.8978 | 0.83442 | 0.93908 | 0.54414
24.6084 | 59.6172 | 59.3316 | 59.8886 | 0.83312 | 0.93761 | 0.54287
24.6125 | 59.6134 | 59.333 | 59.8802 | 0.83184 | 0.93624 | 0.54167
24.6167 | 59.6037 | 59.336 | 59.8774 | 0.8305 | 0.93484 | 0.54046
24.6209 | 59.601 | 59.338 | 59.8731 | 0.82918 | 0.93342 | 0.53927
24.625 | 59.6061 | 59.3417 | 59.8707 | 0.82788 | 0.93203 | 0.53816
24.6292 | 59.6145 | 59.3603 | 59.8804 | 0.8266 | 0.93051 | 0.53701
24.6334 | 59.6149 | 59.3745 | 59.8807 | 0.82537 | 0.929 | 0.53588
24.6375 | 59.614 | 59.3667 | 59.871 | 0.82412 | 0.92766 | 0.53486
24.6417 | 59.6164 | 59.3631 | 59.8743 | 0.82278 | 0.92629 | 0.53379
24.6459 | 59.615 | 59.3482 | 59.866 | 0.82148 | 0.92478 | 0.53269
24.65 | 59.6085 | 59.3317 | 59.8515 | 0.82033 | 0.92332 | 0.53172
24.6542 | 59.6077 | 59.3551 | 59.8563 | 0.81913 | 0.92187 | 0.53079
24.6584 | 59.5958 | 59.3748 | 59.847 | 0.8179 | 0.9204 | 0.52982
24.6625 | 59.5904 | 59.3779 | 59.8304 | 0.8167 | 0.91901 | 0.52896
24.6667 | 59.6065 | 59.3881 | 59.8297 | 0.81549 | 0.91763 | 0.52815
24.6709 | 59.6176 | 59.3722 | 59.8283 | 0.81423 | 0.91615 | 0.52722
24.675 | 59.6202 | 59.3505 | 59.8227 | 0.8131 | 0.91473 | 0.5264
24.6792 | 59.6091 | 59.3299 | 59.8133 | 0.81206 | 0.9135 | 0.52578
24.6834 | 59.5957 | 59.31 | 59.8098 | 0.81086 | 0.91223 | 0.52503
24.6875 | 59.5832 | 59.3296 | 59.8158 | 0.80963 | 0.91074 | 0.52409
24.6917 | 59.5864 | 59.3554 | 59.8267 | 0.80847 | 0.90929 | 0.52325
24.6959 | 59.6018 | 59.3795 | 59.8572 | 0.80742 | 0.90806 | 0.52247
24.7 | 59.599 | 59.3943 | 59.8719 | 0.80635 | 0.90684 | 0.52166
24.7042 | 59.5939 | 59.3423 | 59.8482 | 0.8053 | 0.90563 | 0.52089
24.7084 | 59.5936 | 59.2959 | 59.8453 | 0.80414 | 0.90438 | 0.52001
24.7125 | 59.6017 | 59.2921 | 59.8571 | 0.8029 | 0.90299 | 0.51892
24.7167 | 59.604 | 59.2903 | 59.8626 | 0.80187 | 0.90167 | 0.51797
24.7209 | 59.5965 | 59.3133 | 59.8781 | 0.80092 | 0.9007 | 0.5173
24.725 | 59.5752 | 59.3288 | 59.8742 | 0.79994 | 0.8997 | 0.51651
24.7292 | 59.561 | 59.3263 | 59.853 | 0.79878 | 0.89836 | 0.51553
24.7334 | 59.566 | 59.3326 | 59.8508 | 0.79767 | 0.89701 | 0.51458
24.7375 | 59.5869 | 59.3378 | 59.866 | 0.79664 | 0.89581 | 0.51368
24.7417 | 59.5942 | 59.3375 | 59.8716 | 0.79575 | 0.89469 | 0.5129
24.7459 | 59.5862 | 59.3155 | 59.8587 | 0.79479 | 0.89356 | 0.51222
24.75 | 59.5783 | 59.2911 | 59.8477 | 0.7937 | 0.89236 | 0.51141
24.7542 | 59.5706 | 59.3018 | 59.8423 | 0.79257 | 0.89103 | 0.51046
24.7584 | 59.5788 | 59.3207 | 59.8478 | 0.79156 | 0.88975 | 0.50961
24.7625 | 59.5832 | 59.334 | 59.8652 | 0.79063 | 0.88869 | 0.50891
24.7667 | 59.5686 | 59.3383 | 59.8646 | 0.78973 | 0.88766 | 0.50822
24.7709 | 59.5529 | 59.3382 | 59.852 | 0.7888 | 0.88625 | 0.50743
24.775 | 59.5541 | 59.3425 | 59.85 | 0.78771 | 0.88478 | 0.50658
24.7792 | 59.5542 | 59.3588 | 59.8553 | 0.78675 | 0.88348 | 0.50571
24.7834 | 59.5635 | 59.3776 | 59.8633 | 0.78588 | 0.88226 | 0.50497
24.7875 | 59.5729 | 59.3556 | 59.8658 | 0.785 | 0.88103 | 0.50429
24.7917 | 59.5658 | 59.3242 | 59.8605 | 0.78395 | 0.87979 | 0.50351
24.7959 | 59.5581 | 59.3296 | 59.8499 | 0.78304 | 0.87832 | 0.50271
24.8 | 59.5614 | 59.3418 | 59.8496 | 0.78206 | 0.87686 | 0.50193
24.8042 | 59.5588 | 59.3589 | 59.8625 | 0.78111 | 0.87567 | 0.50113
24.8084 | 59.5411 | 59.3726 | 59.8645 | 0.78028 | 0.87458 | 0.5004
24.8125 | 59.5395 | 59.3446 | 59.8623 | 0.77944 | 0.8733 | 0.49972
24.8167 | 59.5351 | 59.3146 | 59.8615 | 0.77847 | 0.87199 | 0.49896
24.8209 | 59.5313 | 59.3064 | 59.8516 | 0.77757 | 0.87074 | 0.49816
24.825 | 59.5399 | 59.3054 | 59.8498 | 0.77679 | 0.86954 | 0.49745
24.8292 | 59.5455 | 59.2922 | 59.8615 | 0.77591 | 0.8686 | 0.4967
24.8334 | 59.536 | 59.2729 | 59.8645 | 0.77504 | 0.86768 | 0.49594
24.8375 | 59.5303 | 59.2588 | 59.8578 | 0.77421 | 0.86661 | 0.49529
24.8417 | 59.5332 | 59.2487 | 59.8575 | 0.77333 | 0.8655 | 0.49461
24.8459 | 59.5338 | 59.2628 | 59.8546 | 0.77239 | 0.86453 | 0.49381
24.85 | 59.5383 | 59.2794 | 59.8503 | 0.77156 | 0.86362 | 0.49307
24.8542 | 59.5315 | 59.2782 | 59.8581 | 0.77082 | 0.86266 | 0.49242
24.8584 | 59.5274 | 59.2705 | 59.8615 | 0.76993 | 0.86167 | 0.49172
24.8625 | 59.5058 | 59.2819 | 59.8556 | 0.76916 | 0.86048 | 0.49101
24.8667 | 59.4977 | 59.2983 | 59.852 | 0.76834 | 0.85929 | 0.49035
24.8709 | 59.5089 | 59.2956 | 59.8577 | 0.76755 | 0.85834 | 0.4896
24.875 | 59.5072 | 59.2903 | 59.8625 | 0.7667 | 0.85745 | 0.48885
24.8792 | 59.5086 | 59.259 | 59.8542 | 0.76607 | 0.85642 | 0.48826
24.8834 | 59.5099 | 59.226 | 59.853 | 0.76528 | 0.85535 | 0.48765
24.8875 | 59.4995 | 59.2451 | 59.8515 | 0.76447 | 0.85425 | 0.48688
24.8917 | 59.4967 | 59.2698 | 59.8441 | 0.76364 | 0.85318 | 0.48616
24.8959 | 59.4996 | 59.2825 | 59.8556 | 0.76294 | 0.85228 | 0.48555
24.9 | 59.4995 | 59.2912 | 59.8636 | 0.76214 | 0.85139 | 0.48489
24.9042 | 59.4831 | 59.2877 | 59.8535 | 0.76151 | 0.85015 | 0.48422
24.9084 | 59.4713 | 59.2849 | 59.8482 | 0.76079 | 0.84889 | 0.48361
24.9125 | 59.4682 | 59.2852 | 59.851 | 0.76006 | 0.84787 | 0.48289
24.9167 | 59.4644 | 59.2878 | 59.8504 | 0.75928 | 0.84687 | 0.48218
24.9209 | 59.4714 | 59.2688 | 59.8485 | 0.75868 | 0.84581 | 0.48162
24.925 | 59.478 | 59.2485 | 59.8514 | 0.75798 | 0.84473 | 0.48103
24.9292 | 59.4702 | 59.2629 | 59.8516 | 0.7573 | 0.84357 | 0.4803
24.9334 | 59.4632 | 59.2803 | 59.8473 | 0.75659 | 0.84239 | 0.47963
24.9375 | 59.4642 | 59.2656 | 59.8488 | 0.75589 | 0.84158 | 0.47907
24.9417 | 59.4584 | 59.2507 | 59.852 | 0.75517 | 0.84077 | 0.47845
24.9459 | 59.4491 | 59.2457 | 59.8433 | 0.7546 | 0.83952 | 0.47779
24.95 | 59.4413 | 59.2386 | 59.8397 | 0.75398 | 0.83824 | 0.47719
24.9542 | 59.4304 | 59.2595 | 59.8513 | 0.75333 | 0.83736 | 0.47653
24.9584 | 59.4243 | 59.2776 | 59.8519 | 0.75268 | 0.8365 | 0.47587
24.9625 | 59.4311 | 59.2267 | 59.8413 | 0.75208 | 0.83568 | 0.47537
24.9667 | 59.4365 | 59.1752 | 59.8401 | 0.75145 | 0.83486 | 0.47481
24.9709 | 59.4349 | 59.1793 | 59.8427 | 0.75086 | 0.83375 | 0.47404
24.975 | 59.4357 | 59.1826 | 59.8423 | 0.75021 | 0.83268 | 0.47338
24.9792 | 59.4304 | 59.1593 | 59.8494 | 0.74957 | 0.83243 | 0.47291
24.9834 | 59.4309 | 59.1322 | 59.852 | 0.74884 | 0.83221 | 0.47234
24.9875 | 59.4245 | 59.0737 | 59.8316 | 0.74828 | 0.8315 | 0.47172
24.9917 | 59.423 | 59.0187 | 59.8265 | 0.74761 | 0.83081 | 0.4711
24.9959 | 59.4238 | 59.0537 | 59.8446 | 0.74696 | 0.83039 | 0.47042
25 | 59.4222 | 59.0886 | 59.8492 | 0.74622 | 0.83003 | 0.4698
25.0042 | 59.4305 | 59.0526 | 59.8414 | 0.74559 | 0.83002 | 0.4694
25.0084 | 59.4371 | 59.0172 | 59.8357 | 0.74486 | 0.83001 | 0.46888
25.0125 | 59.4416 | 59.0204 | 59.8304 | 0.74412 | 0.82921 | 0.4681
25.0167 | 59.4336 | 59.028 | 59.8308 | 0.74344 | 0.82844 | 0.46743
25.0209 | 59.4339 | 59.0527 | 59.8472 | 0.74272 | 0.82845 | 0.46696
25.025 | 59.4235 | 59.0715 | 59.8502 | 0.74197 | 0.82849 | 0.46646
25.0292 | 59.3974 | 59.0155 | 59.8279 | 0.74141 | 0.82807 | 0.46591
25.0334 | 59.4009 | 58.9614 | 59.8192 | 0.74072 | 0.82763 | 0.46531
25.0375 | 59.398 | 59.0056 | 59.831 | 0.74 | 0.827 | 0.46461
25.0417 | 59.384 | 59.0506 | 59.8388 | 0.73941 | 0.82645 | 0.46402
25.0459 | 59.4035 | 59.0487 | 59.8369 | 0.73886 | 0.82643 | 0.46366
25.05 | 59.3928 | 59.0434 | 59.8288 | 0.7382 | 0.82639 | 0.46319
25.0542 | 59.3698 | 59.0502 | 59.8165 | 0.73765 | 0.82531 | 0.4625
25.0584 | 59.3777 | 59.0661 | 59.8142 | 0.73708 | 0.8242 | 0.46186
25.0625 | 59.3693 | 59.1373 | 59.8326 | 0.73639 | 0.82356 | 0.46136
25.0667 | 59.358 | 59.205 | 59.8379 | 0.73588 | 0.82295 | 0.46091
25.0709 | 59.3597 | 59.1573 | 59.8214 | 0.73544 | 0.82216 | 0.46045
25.075 | 59.352 | 59.109 | 59.8097 | 0.73485 | 0.8213 | 0.45992
25.0792 | 59.3339 | 59.1098 | 59.8131 | 0.73432 | 0.82004 | 0.45924
25.0834 | 59.3399 | 59.1157 | 59.8213 | 0.73381 | 0.8188 | 0.45867
25.0875 | 59.3469 | 59.0804 | 59.828 | 0.73325 | 0.81864 | 0.45828
25.0917 | 59.3423 | 59.0349 | 59.8247 | 0.73271 | 0.8185 | 0.45787
25.0959 | 59.3393 | 58.9423 | 59.8079 | 0.7323 | 0.81794 | 0.4573
25.1 | 59.3381 | 58.8538 | 59.8025 | 0.7317 | 0.81734 | 0.4567
25.1042 | 59.3289 | 58.8686 | 59.8152 | 0.73112 | 0.81726 | 0.45615
25.1084 | 59.3276 | 58.8836 | 59.8242 | 0.73058 | 0.81728 | 0.45568
25.1125 | 59.3318 | 58.8326 | 59.8169 | 0.73011 | 0.8178 | 0.45529
25.1167 | 59.3206 | 58.7753 | 59.8075 | 0.72957 | 0.81828 | 0.45481
25.1209 | 59.3101 | 58.777 | 59.7985 | 0.7291 | 0.81798 | 0.45422
25.125 | 59.3028 | 58.7888 | 59.8001 | 0.72859 | 0.81767 | 0.45366
25.1292 | 59.3059 | 58.8656 | 59.8096 | 0.72801 | 0.81786 | 0.45324
25.1334 | 59.3052 | 58.9382 | 59.8088 | 0.72752 | 0.8181 | 0.45284
25.1375 | 59.3074 | 58.9288 | 59.7986 | 0.72706 | 0.81777 | 0.4524
25.1417 | 59.3067 | 58.921 | 59.7937 | 0.72657 | 0.81734 | 0.45185
25.1459 | 59.306 | 58.9694 | 59.8014 | 0.72592 | 0.81643 | 0.45129
25.15 | 59.3051 | 59.0212 | 59.8069 | 0.72539 | 0.81558 | 0.45083
25.1542 | 59.3097 | 59.0208 | 59.8054 | 0.72483 | 0.81526 | 0.45047
25.1584 | 59.2997 | 59.0089 | 59.789 | 0.72437 | 0.81493 | 0.4501
25.1625 | 59.2746 | 58.9476 | 59.7665 | 0.72389 | 0.81409 | 0.44964
25.1667 | 59.2678 | 58.8998 | 59.7702 | 0.72338 | 0.81316 | 0.4491
25.1709 | 59.2723 | 58.9164 | 59.7963 | 0.72269 | 0.81264 | 0.44852
25.175 | 59.2808 | 58.9324 | 59.8189 | 0.72219 | 0.81221 | 0.44808
25.1792 | 59.2908 | 58.8845 | 59.835 | 0.72177 | 0.81218 | 0.44766
25.1834 | 59.273 | 58.8161 | 59.8168 | 0.72142 | 0.81213 | 0.44723
25.1875 | 59.2314 | 58.7679 | 59.7673 | 0.72098 | 0.8118 | 0.44684
25.1917 | 59.2183 | 58.7339 | 59.7424 | 0.72046 | 0.81143 | 0.44641
25.1959 | 59.2172 | 58.7534 | 59.7341 | 0.71991 | 0.81152 | 0.44591
25.2 | 59.2458 | 58.786 | 59.7531 | 0.71939 | 0.81165 | 0.44545
25.2042 | 59.2747 | 58.7941 | 59.8061 | 0.71899 | 0.81153 | 0.44501
25.2084 | 59.2848 | 58.7934 | 59.8391 | 0.71842 | 0.81134 | 0.44449
25.2125 | 59.2884 | 58.8287 | 59.8463 | 0.71779 | 0.81087 | 0.44399
25.2167 | 59.2794 | 58.8554 | 59.8337 | 0.71705 | 0.81041 | 0.44347
25.2209 | 59.2667 | 58.8604 | 59.8035 | 0.71647 | 0.81007 | 0.44284
25.225 | 59.251 | 58.865 | 59.7777 | 0.71588 | 0.80974 | 0.44225
25.2292 | 59.2293 | 58.8467 | 59.7661 | 0.71535 | 0.80905 | 0.44178
25.2334 | 59.2226 | 58.8419 | 59.7754 | 0.71468 | 0.80831 | 0.44127
25.2375 | 59.2367 | 58.8654 | 59.7943 | 0.71401 | 0.80765 | 0.44071
25.2417 | 59.262 | 58.8941 | 59.8205 | 0.71328 | 0.80696 | 0.44011
25.2459 | 59.2892 | 58.8995 | 59.8592 | 0.71264 | 0.80629 | 0.4394
25.25 | 59.3082 | 58.9047 | 59.8972 | 0.71181 | 0.80547 | 0.4385
25.2542 | 59.3317 | 58.9276 | 59.9316 | 0.71079 | 0.80436 | 0.43751
25.2584 | 59.352 | 58.9513 | 59.9618 | 0.70964 | 0.80317 | 0.43646
25.2625 | 59.3829 | 58.9771 | 59.9869 | 0.70849 | 0.80217 | 0.43525
25.2667 | 59.3988 | 58.9909 | 59.9906 | 0.70733 | 0.80114 | 0.43404
25.2709 | 59.3938 | 58.9666 | 59.9796 | 0.70615 | 0.79999 | 0.4329
25.275 | 59.4064 | 58.9522 | 59.9863 | 0.70472 | 0.79868 | 0.43159
25.2792 | 59.4285 | 58.9818 | 60.0028 | 0.70313 | 0.79718 | 0.43009
25.2834 | 59.4753 | 59.0275 | 60.0405 | 0.70146 | 0.79561 | 0.4286
25.2875 | 59.532 | 59.0727 | 60.1054 | 0.69985 | 0.79424 | 0.42706
25.2917 | 59.5794 | 59.113 | 60.16 | 0.69796 | 0.79269 | 0.42531
25.2959 | 59.6153 | 59.1375 | 60.1979 | 0.69591 | 0.79074 | 0.42344
25.3 | 59.6668 | 59.1681 | 60.2506 | 0.6935 | 0.78854 | 0.4213
25.3042 | 59.7258 | 59.2432 | 60.3161 | 0.69102 | 0.78622 | 0.41881
25.3084 | 59.7588 | 59.3025 | 60.3591 | 0.68857 | 0.78389 | 0.41638
25.3125 | 59.7769 | 59.3231 | 60.3871 | 0.68618 | 0.78162 | 0.4141
25.3167 | 59.7519 | 59.315 | 60.3817 | 0.68367 | 0.77931 | 0.41171
25.3209 | 59.7196 | 59.2928 | 60.3372 | 0.68113 | 0.77667 | 0.40921
25.325 | 59.6903 | 59.2703 | 60.3022 | 0.67878 | 0.77415 | 0.40687
25.3292 | 59.6625 | 59.2509 | 60.2847 | 0.67662 | 0.77197 | 0.40465
25.3334 | 59.6124 | 59.2206 | 60.2514 | 0.67483 | 0.77006 | 0.40271
25.3375 | 59.5534 | 59.1534 | 60.1995 | 0.67314 | 0.76824 | 0.40112
25.3417 | 59.5062 | 59.0892 | 60.1561 | 0.67151 | 0.7665 | 0.39953
25.3459 | 59.4697 | 59.0584 | 60.1199 | 0.66995 | 0.76479 | 0.39785
25.35 | 59.4681 | 59.0511 | 60.1086 | 0.66864 | 0.76323 | 0.39636
25.3542 | 59.4701 | 59.0356 | 60.1271 | 0.66746 | 0.76211 | 0.39511
25.3584 | 59.4685 | 59.0216 | 60.139 | 0.66625 | 0.76103 | 0.39384
25.3625 | 59.4713 | 59.0115 | 60.1353 | 0.66501 | 0.75967 | 0.39255
25.3667 | 59.4901 | 59.0106 | 60.1434 | 0.66357 | 0.7582 | 0.39116
25.3709 | 59.5171 | 59.0489 | 60.1706 | 0.66218 | 0.75689 | 0.38962
25.375 | 59.548 | 59.0927 | 60.1984 | 0.66076 | 0.75556 | 0.38813
25.3792 | 59.5674 | 59.0986 | 60.224 | 0.65936 | 0.75425 | 0.38676
25.3834 | 59.576 | 59.0915 | 60.2375 | 0.65775 | 0.75286 | 0.3853
25.3875 | 59.5825 | 59.11 | 60.2361 | 0.65614 | 0.75111 | 0.38366
25.3917 | 59.5898 | 59.1291 | 60.2369 | 0.65447 | 0.7493 | 0.38205
25.3959 | 59.6 | 59.1478 | 60.2485 | 0.65287 | 0.74781 | 0.3805
25.4 | 59.5926 | 59.1628 | 60.2567 | 0.65131 | 0.74637 | 0.37898
25.4042 | 59.5866 | 59.1404 | 60.253 | 0.64974 | 0.74468 | 0.3775
25.4084 | 59.5715 | 59.1101 | 60.2474 | 0.64817 | 0.74299 | 0.37604
25.4125 | 59.5623 | 59.1189 | 60.2438 | 0.64662 | 0.74129 | 0.37454
25.4167 | 59.5582 | 59.1337 | 60.24 | 0.64519 | 0.73963 | 0.37309
25.4209 | 59.5549 | 59.1229 | 60.2374 | 0.64372 | 0.73821 | 0.37177
25.425 | 59.5469 | 59.1122 | 60.2375 | 0.64237 | 0.73685 | 0.37045
25.4292 | 59.5467 | 59.0996 | 60.2397 | 0.64092 | 0.73519 | 0.36906
25.4334 | 59.5454 | 59.0853 | 60.2436 | 0.63954 | 0.73353 | 0.3677
25.4375 | 59.5344 | 59.089 | 60.2488 | 0.63822 | 0.73216 | 0.36645
25.4417 | 59.5386 | 59.0983 | 60.2538 | 0.63689 | 0.7308 | 0.36517
25.4459 | 59.5351 | 59.0871 | 60.2533 | 0.6355 | 0.72933 | 0.36386
25.45 | 59.5344 | 59.0745 | 60.2514 | 0.63415 | 0.72789 | 0.36257
25.4542 | 59.5409 | 59.0774 | 60.2574 | 0.63286 | 0.72645 | 0.36131
25.4584 | 59.5378 | 59.078 | 60.2587 | 0.63155 | 0.725 | 0.36007
25.4625 | 59.5274 | 59.0616 | 60.2514 | 0.63027 | 0.72374 | 0.3589
25.4667 | 59.5282 | 59.0486 | 60.2539 | 0.62893 | 0.72248 | 0.3577
25.4709 | 59.5282 | 59.0515 | 60.2628 | 0.6276 | 0.72098 | 0.3564
25.475 | 59.5282 | 59.0519 | 60.2681 | 0.62631 | 0.7195 | 0.35518
25.4792 | 59.5312 | 59.0632 | 60.2776 | 0.62509 | 0.71826 | 0.35407
25.4834 | 59.5274 | 59.0733 | 60.2781 | 0.62378 | 0.717 | 0.35291
25.4875 | 59.5181 | 59.0453 | 60.2595 | 0.62252 | 0.71568 | 0.35177
25.4917 | 59.5141 | 59.0203 | 60.2521 | 0.62127 | 0.71438 | 0.35065
25.4959 | 59.5126 | 59.0313 | 60.256 | 0.62003 | 0.71293 | 0.3495
25.5 | 59.5006 | 59.0395 | 60.2512 | 0.61885 | 0.7115 | 0.34845
25.5042 | 59.4971 | 59.0532 | 60.2543 | 0.61767 | 0.71024 | 0.34749
25.5084 | 59.5006 | 59.0677 | 60.2544 | 0.6164 | 0.70897 | 0.34648
25.5125 | 59.4986 | 59.0538 | 60.2443 | 0.61515 | 0.7075 | 0.34544
25.5167 | 59.5039 | 59.0414 | 60.2464 | 0.614 | 0.70605 | 0.34446
25.5209 | 59.5048 | 59.0321 | 60.2502 | 0.61279 | 0.70468 | 0.34349
25.525 | 59.4908 | 59.0197 | 60.2475 | 0.61155 | 0.70331 | 0.34254
25.5292 | 59.4748 | 59.007 | 60.2371 | 0.61042 | 0.70197 | 0.3417
25.5334 | 59.4627 | 58.9959 | 60.2236 | 0.60925 | 0.70063 | 0.34085
25.5375 | 59.4599 | 59.0194 | 60.2274 | 0.60801 | 0.69906 | 0.33985
25.5417 | 59.4563 | 59.0432 | 60.2283 | 0.60685 | 0.69752 | 0.33895
25.5459 | 59.4593 | 59.0274 | 60.2232 | 0.60576 | 0.69632 | 0.33826
25.55 | 59.4616 | 59.0098 | 60.2201 | 0.60461 | 0.69512 | 0.33756
25.5542 | 59.4494 | 58.9585 | 60.1948 | 0.60344 | 0.69369 | 0.33676
25.5584 | 59.4412 | 58.9086 | 60.1797 | 0.60231 | 0.69228 | 0.33599
25.5625 | 59.4323 | 58.9303 | 60.1965 | 0.6012 | 0.69093 | 0.33521
25.5667 | 59.4204 | 58.9523 | 60.2081 | 0.60006 | 0.68958 | 0.33445
25.5709 | 59.4056 | 58.9583 | 60.2151 | 0.59903 | 0.68842 | 0.3338
25.575 | 59.3984 | 58.9633 | 60.2206 | 0.59794 | 0.68726 | 0.33312
25.5792 | 59.4025 | 58.9385 | 60.2203 | 0.5968 | 0.68583 | 0.33222
25.5834 | 59.3993 | 58.9131 | 60.2271 | 0.5957 | 0.68441 | 0.33132
25.5875 | 59.401 | 58.8866 | 60.2324 | 0.5947 | 0.68329 | 0.33058
25.5917 | 59.395 | 58.861 | 60.2392 | 0.59363 | 0.68217 | 0.32981
25.5959 | 59.3808 | 58.85 | 60.2405 | 0.59249 | 0.68091 | 0.32892
25.6 | 59.3675 | 58.8385 | 60.2342 | 0.59142 | 0.67967 | 0.32804
25.6042 | 59.3599 | 58.8546 | 60.2415 | 0.5904 | 0.67853 | 0.32722
25.6084 | 59.3455 | 58.8699 | 60.2447 | 0.58942 | 0.67737 | 0.32639
25.6125 | 59.3372 | 58.8543 | 60.2357 | 0.58839 | 0.67622 | 0.32559
25.6167 | 59.3338 | 58.8404 | 60.2322 | 0.58737 | 0.67508 | 0.32481
25.6209 | 59.3366 | 58.8366 | 60.2349 | 0.58633 | 0.67374 | 0.32394
25.625 | 59.3387 | 58.8301 | 60.2334 | 0.58537 | 0.67243 | 0.32312
25.6292 | 59.3293 | 58.8199 | 60.2264 | 0.58443 | 0.67139 | 0.32247
25.6334 | 59.3193 | 58.81 | 60.2244 | 0.58344 | 0.67034 | 0.32176
25.6375 | 59.3141 | 58.7975 | 60.2211 | 0.58236 | 0.66904 | 0.32091
25.6417 | 59.3132 | 58.7868 | 60.2204 | 0.58132 | 0.66778 | 0.32013
25.6459 | 59.3065 | 58.808 | 60.2336 | 0.58043 | 0.66655 | 0.31944
25.65 | 59.2922 | 58.8252 | 60.2346 | 0.57956 | 0.66533 | 0.31875
25.6542 | 59.2717 | 58.8169 | 60.2243 | 0.57862 | 0.66411 | 0.31803
25.6584 | 59.2639 | 58.8125 | 60.225 | 0.57757 | 0.66287 | 0.31727
25.6625 | 59.2689 | 58.8004 | 60.2305 | 0.57661 | 0.66147 | 0.31644
25.6667 | 59.2798 | 58.787 | 60.2356 | 0.57568 | 0.66012 | 0.31571
25.6709 | 59.2765 | 58.7805 | 60.2353 | 0.57484 | 0.65892 | 0.31509
25.675 | 59.2602 | 58.7687 | 60.2284 | 0.5739 | 0.6577 | 0.31439
25.6792 | 59.2446 | 58.7619 | 60.2216 | 0.57294 | 0.65636 | 0.31359
25.6834 | 59.2375 | 58.7604 | 60.2255 | 0.57189 | 0.65503 | 0.3128
25.6875 | 59.2366 | 58.7594 | 60.2383 | 0.57099 | 0.65377 | 0.31209
25.6917 | 59.2237 | 58.7543 | 60.2385 | 0.57019 | 0.65258 | 0.31145
25.6959 | 59.2144 | 58.7271 | 60.2279 | 0.56934 | 0.65141 | 0.3108
25.7 | 59.2011 | 58.6997 | 60.221 | 0.56836 | 0.6502 | 0.31005
25.7042 | 59.1882 | 58.6816 | 60.2195 | 0.56745 | 0.64897 | 0.30925
25.7084 | 59.1887 | 58.6688 | 60.2264 | 0.56662 | 0.64778 | 0.30855
25.7125 | 59.1879 | 58.6532 | 60.2372 | 0.56573 | 0.6468 | 0.3079
25.7167 | 59.1674 | 58.6318 | 60.2334 | 0.56491 | 0.64583 | 0.30724
25.7209 | 59.1603 | 58.6021 | 60.2176 | 0.56403 | 0.64481 | 0.30658
25.725 | 59.1642 | 58.5777 | 60.2166 | 0.56303 | 0.64375 | 0.30584
25.7292 | 59.1495 | 58.5804 | 60.2188 | 0.56212 | 0.64268 | 0.30508
25.7334 | 59.147 | 58.5834 | 60.2173 | 0.56134 | 0.64167 | 0.30445
25.7375 | 59.1267 | 58.5876 | 60.2271 | 0.56052 | 0.64066 | 0.30383
25.7417 | 59.1032 | 58.5857 | 60.2228 | 0.55955 | 0.63961 | 0.30312
25.7459 | 59.084 | 58.5732 | 60.21 | 0.55875 | 0.63843 | 0.30244
25.75 | 59.0811 | 58.5668 | 60.214 | 0.55786 | 0.63724 | 0.30179
25.7542 | 59.0781 | 58.5485 | 60.2184 | 0.55706 | 0.63614 | 0.30104
25.7584 | 59.0602 | 58.5248 | 60.2153 | 0.55627 | 0.63509 | 0.30038
25.7625 | 59.0496 | 58.493 | 60.2103 | 0.55553 | 0.63406 | 0.29984
25.7667 | 59.0391 | 58.4614 | 60.2068 | 0.55458 | 0.63297 | 0.29916
25.7709 | 59.026 | 58.4666 | 60.2002 | 0.55374 | 0.63176 | 0.29842
25.775 | 59.0231 | 58.4782 | 60.1988 | 0.55293 | 0.63059 | 0.29779
25.7792 | 59.013 | 58.4791 | 60.2132 | 0.55217 | 0.62958 | 0.29714
25.7834 | 58.9869 | 58.4716 | 60.2132 | 0.55133 | 0.62857 | 0.29647
25.7875 | 58.9609 | 58.4367 | 60.1948 | 0.55061 | 0.62738 | 0.29592
25.7917 | 58.9461 | 58.4063 | 60.1898 | 0.54975 | 0.62614 | 0.29532
25.7959 | 58.9359 | 58.4098 | 60.1921 | 0.54895 | 0.62485 | 0.29451
25.8 | 58.9265 | 58.4144 | 60.1905 | 0.5482 | 0.62362 | 0.29384
25.8042 | 58.9215 | 58.3904 | 60.1995 | 0.54753 | 0.62269 | 0.29334
25.8084 | 58.9076 | 58.3607 | 60.2013 | 0.54672 | 0.62172 | 0.29274
25.8125 | 58.8895 | 58.3267 | 60.1794 | 0.54596 | 0.62048 | 0.29209
25.8167 | 58.879 | 58.302 | 60.1715 | 0.54518 | 0.6192 | 0.29148
25.8209 | 58.8735 | 58.3134 | 60.1869 | 0.54442 | 0.61817 | 0.29076
25.825 | 58.8578 | 58.3193 | 60.1909 | 0.54369 | 0.61718 | 0.29009
25.8292 | 58.8352 | 58.2849 | 60.1823 | 0.54307 | 0.6163 | 0.28965
25.8334 | 58.8178 | 58.2459 | 60.1772 | 0.54235 | 0.61534 | 0.28911
25.8375 | 58.7999 | 58.2322 | 60.1665 | 0.54158 | 0.61412 | 0.28833
25.8417 | 58.7904 | 58.2241 | 60.1604 | 0.54088 | 0.61294 | 0.28765
25.8459 | 58.7951 | 58.2108 | 60.1764 | 0.54019 | 0.6122 | 0.28711
25.85 | 58.7905 | 58.1888 | 60.1813 | 0.53946 | 0.61149 | 0.28654
25.8542 | 58.7689 | 58.137 | 60.1618 | 0.53881 | 0.61059 | 0.28597
25.8584 | 58.7604 | 58.0864 | 60.1515 | 0.53806 | 0.60965 | 0.28539
25.8625 | 58.7476 | 58.0655 | 60.1556 | 0.53724 | 0.60892 | 0.28466
25.8667 | 58.7334 | 58.0455 | 60.1586 | 0.53646 | 0.60827 | 0.28398
25.8709 | 58.7235 | 57.9966 | 60.1559 | 0.53584 | 0.60789 | 0.28355
25.875 | 58.7129 | 57.9422 | 60.1525 | 0.53505 | 0.60751 | 0.28304
25.8792 | 58.6871 | 57.9226 | 60.141 | 0.53431 | 0.60681 | 0.28233
25.8834 | 58.6804 | 57.9101 | 60.1329 | 0.5335 | 0.60611 | 0.28166
25.8875 | 58.6924 | 57.9032 | 60.1426 | 0.53264 | 0.60583 | 0.28112
25.8917 | 58.6765 | 57.8949 | 60.146 | 0.53184 | 0.60559 | 0.28056
25.8959 | 58.6681 | 57.862 | 60.1326 | 0.53116 | 0.60499 | 0.28001
25.9 | 58.6494 | 57.8282 | 60.122 | 0.53032 | 0.60434 | 0.27945
25.9042 | 58.6076 | 57.8319 | 60.1248 | 0.52947 | 0.60369 | 0.27876
25.9084 | 58.5956 | 57.8384 | 60.1246 | 0.52865 | 0.60307 | 0.27812
25.9125 | 58.5824 | 57.7969 | 60.1186 | 0.52788 | 0.60268 | 0.27766
25.9167 | 58.5583 | 57.7495 | 60.1146 | 0.52713 | 0.60229 | 0.27716
25.9209 | 58.5432 | 57.7303 | 60.104 | 0.52645 | 0.60137 | 0.27648
25.925 | 58.5136 | 57.7132 | 60.0954 | 0.52567 | 0.60044 | 0.27585
25.9292 | 58.4935 | 57.7169 | 60.0998 | 0.52488 | 0.59989 | 0.27533
25.9334 | 58.4797 | 57.7218 | 60.0989 | 0.52413 | 0.59939 | 0.2748
25.9375 | 58.4584 | 57.6935 | 60.0844 | 0.52343 | 0.59845 | 0.27425
25.9417 | 58.4358 | 57.6639 | 60.0739 | 0.52275 | 0.59748 | 0.27371
25.9459 | 58.41 | 57.683 | 60.0765 | 0.522 | 0.59632 | 0.27306
25.95 | 58.3794 | 57.7056 | 60.0734 | 0.52128 | 0.59515 | 0.27248
25.9542 | 58.3562 | 57.6646 | 60.0664 | 0.52059 | 0.59433 | 0.27203
25.9584 | 58.3413 | 57.6213 | 60.06 | 0.51986 | 0.59351 | 0.27154
25.9625 | 58.3125 | 57.5621 | 60.0492 | 0.51919 | 0.59227 | 0.27089
25.9667 | 58.2896 | 57.502 | 60.043 | 0.51853 | 0.59098 | 0.2703
25.9709 | 58.2722 | 57.4568 | 60.046 | 0.51779 | 0.59037 | 0.26979
25.975 | 58.2461 | 57.4094 | 60.0424 | 0.51701 | 0.58977 | 0.26929
25.9792 | 58.2232 | 57.3115 | 60.0256 | 0.51637 | 0.5893 | 0.26877
25.9834 | 58.2082 | 57.2113 | 60.0158 | 0.5156 | 0.5888 | 0.26822
25.9875 | 58.1776 | 57.1688 | 60.0166 | 0.51486 | 0.58832 | 0.26759
25.9917 | 58.1449 | 57.1266 | 60.0171 | 0.51414 | 0.58785 | 0.26701
25.9959 | 58.1284 | 57.0718 | 60.0098 | 0.51339 | 0.58794 | 0.26658
26 | 58.0942 | 57.0134 | 59.9977 | 0.51259 | 0.58806 | 0.26611
26.0042 | 58.0634 | 56.985 | 59.9786 | 0.51197 | 0.58759 | 0.26554
26.0084 | 58.0396 | 56.9604 | 59.9681 | 0.51132 | 0.58709 | 0.26497
26.0125 | 58.013 | 56.9929 | 59.972 | 0.51054 | 0.58672 | 0.26447
26.0167 | 57.9865 | 57.0287 | 59.9761 | 0.50985 | 0.58636 | 0.26397
26.0209 | 57.9869 | 57.0095 | 59.9754 | 0.50913 | 0.58578 | 0.26348
26.025 | 57.9744 | 56.9855 | 59.9678 | 0.50843 | 0.58518 | 0.26298
26.0292 | 57.9475 | 56.9896 | 59.9623 | 0.50775 | 0.58405 | 0.26242
26.0334 | 57.9153 | 56.9896 | 59.946 | 0.50717 | 0.58291 | 0.26193
26.0375 | 57.8811 | 56.9523 | 59.9187 | 0.50639 | 0.58229 | 0.26159
26.0417 | 57.8552 | 56.9205 | 59.9058 | 0.50565 | 0.58163 | 0.26117
26.0459 | 57.8405 | 56.8534 | 59.9076 | 0.50493 | 0.58058 | 0.26056
26.05 | 57.8374 | 56.7941 | 59.9275 | 0.50426 | 0.57949 | 0.25995
26.0542 | 57.8251 | 56.7855 | 59.9698 | 0.50347 | 0.57872 | 0.25939
26.0584 | 57.7904 | 56.7594 | 59.9747 | 0.50284 | 0.578 | 0.25893
26.0625 | 57.7525 | 56.6604 | 59.932 | 0.50215 | 0.57774 | 0.25857
26.0667 | 57.7113 | 56.5546 | 59.8845 | 0.50144 | 0.57744 | 0.25811
26.0709 | 57.6566 | 56.4906 | 59.8392 | 0.5008 | 0.5767 | 0.25749
26.075 | 57.6435 | 56.4489 | 59.8365 | 0.50013 | 0.57596 | 0.25692
26.0792 | 57.6381 | 56.4581 | 59.8726 | 0.49937 | 0.57574 | 0.25649
26.0834 | 57.6363 | 56.4651 | 59.9017 | 0.49858 | 0.57555 | 0.25606
26.0875 | 57.6389 | 56.4224 | 59.9184 | 0.49791 | 0.57504 | 0.25557
26.0917 | 57.6245 | 56.3696 | 59.918 | 0.49702 | 0.57443 | 0.25493
26.0959 | 57.59 | 56.378 | 59.9076 | 0.49616 | 0.57342 | 0.2542
26.1 | 57.5582 | 56.3883 | 59.8983 | 0.49521 | 0.57241 | 0.25352
26.1042 | 57.5281 | 56.3603 | 59.8855 | 0.49423 | 0.57169 | 0.25288
26.1084 | 57.4899 | 56.3275 | 59.8659 | 0.49327 | 0.57098 | 0.25229
26.1125 | 57.4505 | 56.2604 | 59.8471 | 0.49245 | 0.56974 | 0.25168
26.1167 | 57.4224 | 56.2018 | 59.8433 | 0.49147 | 0.56842 | 0.25098
26.1209 | 57.3881 | 56.1849 | 59.8478 | 0.4904 | 0.56719 | 0.25027
26.125 | 57.3756 | 56.1797 | 59.8722 | 0.48923 | 0.5659 | 0.24949
26.1292 | 57.3826 | 56.1412 | 59.9148 | 0.48803 | 0.56467 | 0.24855
26.1334 | 57.3735 | 56.0982 | 59.9475 | 0.48672 | 0.56332 | 0.24749
26.1375 | 57.3614 | 56.0678 | 59.9754 | 0.48539 | 0.56164 | 0.24639
26.1417 | 57.3429 | 56.0327 | 59.9928 | 0.48386 | 0.55984 | 0.24516
26.1459 | 57.3196 | 56.0002 | 59.9908 | 0.48219 | 0.55829 | 0.2438
26.15 | 57.3016 | 55.9653 | 59.9874 | 0.4805 | 0.55668 | 0.24242
26.1542 | 57.281 | 55.9042 | 59.9923 | 0.47882 | 0.55489 | 0.24097
26.1584 | 57.2581 | 55.8457 | 59.9998 | 0.47704 | 0.55301 | 0.23947
26.1625 | 57.2345 | 55.8224 | 60.006 | 0.47516 | 0.55102 | 0.23801
26.1667 | 57.2287 | 55.8069 | 60.0244 | 0.4731 | 0.54894 | 0.23644
26.1709 | 57.2277 | 55.7757 | 60.0508 | 0.471 | 0.54699 | 0.23469
26.175 | 57.2371 | 55.7491 | 60.0852 | 0.46876 | 0.5449 | 0.23281
26.1792 | 57.2389 | 55.7238 | 60.1323 | 0.4665 | 0.54246 | 0.23087
26.1834 | 57.2355 | 55.6965 | 60.1776 | 0.46398 | 0.53989 | 0.22876
26.1875 | 57.2326 | 55.7015 | 60.2118 | 0.4614 | 0.53728 | 0.22652
26.1917 | 57.2117 | 55.6895 | 60.2261 | 0.45875 | 0.53463 | 0.22425
26.1959 | 57.1809 | 55.6336 | 60.2293 | 0.4562 | 0.532 | 0.22192
26.2 | 57.1244 | 55.5621 | 60.2152 | 0.45366 | 0.52939 | 0.21959
26.2042 | 57.071 | 55.5031 | 60.1855 | 0.45124 | 0.52669 | 0.21738
26.2084 | 57.0042 | 55.4351 | 60.1525 | 0.44899 | 0.52413 | 0.21534
26.2125 | 56.9353 | 55.3651 | 60.1131 | 0.44688 | 0.52189 | 0.21336
26.2167 | 56.8529 | 55.2843 | 60.062 | 0.44505 | 0.51984 | 0.21161
26.2209 | 56.7805 | 55.1896 | 60.0116 | 0.44342 | 0.51798 | 0.21013
26.225 | 56.725 | 55.1054 | 59.9775 | 0.44185 | 0.51622 | 0.20868
26.2292 | 56.6732 | 55.0428 | 59.9502 | 0.44039 | 0.51453 | 0.20729
26.2334 | 56.6416 | 54.9917 | 59.9378 | 0.43906 | 0.51295 | 0.20606
26.2375 | 56.6171 | 54.9441 | 59.9443 | 0.43777 | 0.51158 | 0.20491
26.2417 | 56.5881 | 54.8985 | 59.9443 | 0.43641 | 0.51017 | 0.20372
26.2459 | 56.5691 | 54.8536 | 59.9389 | 0.43504 | 0.50865 | 0.20257
26.25 | 56.5679 | 54.8219 | 59.9536 | 0.43348 | 0.50702 | 0.20129
26.2542 | 56.5649 | 54.8111 | 59.9822 | 0.43191 | 0.50536 | 0.19983
26.2584 | 56.5594 | 54.795 | 60.0004 | 0.43032 | 0.50367 | 0.19846
26.2625 | 56.5444 | 54.7627 | 60.0146 | 0.42872 | 0.50201 | 0.19719
26.2667 | 56.5198 | 54.7227 | 60.0158 | 0.42691 | 0.50024 | 0.19576
26.2709 | 56.4972 | 54.6927 | 60.0004 | 0.42509 | 0.49821 | 0.1942
26.275 | 56.4766 | 54.6662 | 59.9998 | 0.42326 | 0.49618 | 0.19267
26.2792 | 56.4559 | 54.6359 | 60.0174 | 0.42148 | 0.49429 | 0.19113
26.2834 | 56.4109 | 54.592 | 60.0166 | 0.41977 | 0.49245 | 0.18968
26.2875 | 56.3618 | 54.5249 | 59.9931 | 0.41807 | 0.49053 | 0.18842
26.2917 | 56.3154 | 54.4576 | 59.9725 | 0.4163 | 0.48857 | 0.18705
26.2959 | 56.2811 | 54.4217 | 59.9561 | 0.4145 | 0.4865 | 0.1855
26.3 | 56.2456 | 54.3906 | 59.9473 | 0.4129 | 0.48452 | 0.1841
26.3042 | 56.2211 | 54.3411 | 59.9553 | 0.41139 | 0.48293 | 0.18295
26.3084 | 56.1802 | 54.2833 | 59.9527 | 0.40992 | 0.48136 | 0.18176
26.3125 | 56.134 | 54.2214 | 59.9293 | 0.40838 | 0.47953 | 0.18054
26.3167 | 56.1088 | 54.1669 | 59.922 | 0.40682 | 0.47766 | 0.17928
26.3209 | 56.0927 | 54.1619 | 59.9366 | 0.40533 | 0.47601 | 0.17796
26.325 | 56.0766 | 54.1576 | 59.9421 | 0.40396 | 0.47442 | 0.17676
26.3292 | 56.0551 | 54.1058 | 59.9406 | 0.40262 | 0.473 | 0.17574
26.3334 | 56.0253 | 54.048 | 59.9321 | 0.40117 | 0.47155 | 0.17462
26.3375 | 55.9957 | 54.0063 | 59.9119 | 0.3997 | 0.46978 | 0.17337
26.3417 | 55.9778 | 53.9706 | 59.9075 | 0.39823 | 0.468 | 0.17218
26.3459 | 55.9578 | 53.9543 | 59.9237 | 0.39682 | 0.46651 | 0.17103
26.35 | 55.9342 | 53.9339 | 59.9284 | 0.39542 | 0.46505 | 0.16994
26.3542 | 55.9088 | 53.8905 | 59.9241 | 0.39401 | 0.46344 | 0.16889
26.3584 | 55.8856 | 53.8442 | 59.9198 | 0.3925 | 0.46179 | 0.16777
26.3625 | 55.8595 | 53.8075 | 59.9087 | 0.39105 | 0.46012 | 0.16659
26.3667 | 55.8332 | 53.7742 | 59.9048 | 0.38963 | 0.45847 | 0.16549
26.3709 | 55.8051 | 53.727 | 59.9028 | 0.38822 | 0.45696 | 0.16447
26.375 | 55.7661 | 53.6757 | 59.892 | 0.3868 | 0.45546 | 0.16347
26.3792 | 55.7336 | 53.6526 | 59.8815 | 0.38539 | 0.45369 | 0.16246
26.3834 | 55.7029 | 53.6297 | 59.8692 | 0.38398 | 0.4519 | 0.16147
26.3875 | 55.6812 | 53.6131 | 59.8701 | 0.38253 | 0.45024 | 0.16044
26.3917 | 55.6656 | 53.5981 | 59.8752 | 0.38108 | 0.44859 | 0.15946
26.3959 | 55.6376 | 53.5263 | 59.8611 | 0.37969 | 0.44697 | 0.15861
26.4 | 55.6073 | 53.451 | 59.8516 | 0.37829 | 0.44534 | 0.15776
26.4042 | 55.5713 | 53.4119 | 59.8426 | 0.37683 | 0.4435 | 0.15678
26.4084 | 55.5292 | 53.3733 | 59.8295 | 0.37536 | 0.44165 | 0.15582
26.4125 | 55.4922 | 53.3584 | 59.8354 | 0.37398 | 0.44001 | 0.15499
26.4167 | 55.4603 | 53.3444 | 59.8358 | 0.37256 | 0.43838 | 0.15415
26.4209 | 55.4302 | 53.2987 | 59.823 | 0.37112 | 0.43658 | 0.1533
26.425 | 55.3978 | 53.2497 | 59.811 | 0.36973 | 0.43479 | 0.1525
26.4292 | 55.371 | 53.1816 | 59.7956 | 0.36831 | 0.43309 | 0.15169
26.4334 | 55.3398 | 53.1137 | 59.7852 | 0.36685 | 0.43137 | 0.15088
26.4375 | 55.2929 | 53.0505 | 59.7722 | 0.36547 | 0.42972 | 0.15017
26.4417 | 55.2532 | 52.9884 | 59.763 | 0.36407 | 0.42807 | 0.14947
26.4459 | 55.2109 | 52.9744 | 59.7727 | 0.36263 | 0.42627 | 0.14864
26.45 | 55.1671 | 52.9573 | 59.7744 | 0.36118 | 0.42447 | 0.14784
26.4542 | 55.1258 | 52.9019 | 59.7711 | 0.35987 | 0.42291 | 0.14717
26.4584 | 55.0882 | 52.8465 | 59.7741 | 0.35846 | 0.42133 | 0.14644
26.4625 | 55.0552 | 52.769 | 59.766 | 0.357 | 0.4195 | 0.14554
26.4667 | 55.0201 | 52.6912 | 59.7654 | 0.35557 | 0.41767 | 0.14467
26.4709 | 54.9814 | 52.6406 | 59.7766 | 0.35419 | 0.41603 | 0.14386
26.475 | 54.935 | 52.587 | 59.7776 | 0.35279 | 0.41438 | 0.14302
26.4792 | 54.8786 | 52.5183 | 59.7632 | 0.35137 | 0.41282 | 0.14225
26.4834 | 54.8247 | 52.4506 | 59.7513 | 0.34996 | 0.41123 | 0.14142
26.4875 | 54.7835 | 52.4056 | 59.753 | 0.34851 | 0.40942 | 0.14045
26.4917 | 54.7355 | 52.3591 | 59.7511 | 0.34712 | 0.40762 | 0.13956
26.4959 | 54.6825 | 52.3005 | 59.7463 | 0.34581 | 0.40601 | 0.13885
26.5 | 54.6305 | 52.2396 | 59.7365 | 0.34446 | 0.40439 | 0.13812
26.5042 | 54.5806 | 52.1646 | 59.7163 | 0.34299 | 0.40258 | 0.13725
26.5084 | 54.5375 | 52.0902 | 59.7066 | 0.34153 | 0.40077 | 0.13639
26.5125 | 54.494 | 52.0256 | 59.7074 | 0.34014 | 0.39905 | 0.13563
26.5167 | 54.4434 | 51.9578 | 59.7046 | 0.33876 | 0.39734 | 0.1349
26.5209 | 54.3828 | 51.8926 | 59.6937 | 0.33734 | 0.39559 | 0.1342
26.525 | 54.321 | 51.8261 | 59.6801 | 0.33588 | 0.39383 | 0.13345
26.5292 | 54.2592 | 51.7772 | 59.6777 | 0.33445 | 0.39192 | 0.13261
26.5334 | 54.201 | 51.7288 | 59.6783 | 0.33303 | 0.39002 | 0.1318
26.5375 | 54.1418 | 51.6517 | 59.6745 | 0.33163 | 0.38824 | 0.13111
26.5417 | 54.0843 | 51.5721 | 59.6682 | 0.3302 | 0.38645 | 0.13041
26.5459 | 54.0282 | 51.4918 | 59.655 | 0.32875 | 0.38448 | 0.12961
26.55 | 53.9779 | 51.4093 | 59.6452 | 0.32724 | 0.3825 | 0.12879
26.5542 | 53.911 | 51.3436 | 59.643 | 0.32583 | 0.38062 | 0.12802
26.5584 | 53.8406 | 51.2751 | 59.6399 | 0.3244 | 0.37874 | 0.12728
26.5625 | 53.7759 | 51.1912 | 59.6327 | 0.32289 | 0.37685 | 0.12654
26.5667 | 53.7074 | 51.1055 | 59.6229 | 0.32132 | 0.37496 | 0.12578
26.5709 | 53.6438 | 51.023 | 59.6125 | 0.31986 | 0.37297 | 0.125
26.575 | 53.5793 | 50.9383 | 59.6032 | 0.31839 | 0.37099 | 0.12423
26.5792 | 53.5003 | 50.8491 | 59.5952 | 0.31691 | 0.36909 | 0.12348
26.5834 | 53.4192 | 50.7582 | 59.5853 | 0.31543 | 0.36719 | 0.12274
26.5875 | 53.3473 | 50.6598 | 59.5808 | 0.31387 | 0.36525 | 0.12196
26.5917 | 53.2754 | 50.5606 | 59.5758 | 0.31231 | 0.3633 | 0.12117
26.5959 | 53.2094 | 50.4534 | 59.5627 | 0.31077 | 0.36144 | 0.12044
26.6 | 53.1319 | 50.3443 | 59.5516 | 0.30929 | 0.35956 | 0.11972
26.6042 | 53.0536 | 50.2337 | 59.5367 | 0.30769 | 0.35768 | 0.11894
26.6084 | 52.9808 | 50.1233 | 59.5253 | 0.30605 | 0.35578 | 0.11815
26.6125 | 52.8921 | 50.0358 | 59.5211 | 0.30444 | 0.35379 | 0.11739
26.6167 | 52.8131 | 49.9462 | 59.5105 | 0.30284 | 0.3518 | 0.11667
26.6209 | 52.7205 | 49.8592 | 59.5016 | 0.30125 | 0.34976 | 0.11592
26.625 | 52.6268 | 49.769 | 59.4887 | 0.29959 | 0.34769 | 0.11516
26.6292 | 52.5326 | 49.6503 | 59.474 | 0.29801 | 0.34561 | 0.11439
26.6334 | 52.4449 | 49.5297 | 59.4677 | 0.29631 | 0.3435 | 0.11361
26.6375 | 52.3532 | 49.4061 | 59.454 | 0.29469 | 0.34135 | 0.11286
26.6417 | 52.2557 | 49.2791 | 59.4362 | 0.29304 | 0.33919 | 0.11215
26.6459 | 52.1623 | 49.1685 | 59.4251 | 0.29138 | 0.33706 | 0.11139
26.65 | 52.0712 | 49.0575 | 59.4136 | 0.2896 | 0.33489 | 0.11057
26.6542 | 51.97 | 48.939 | 59.4005 | 0.28788 | 0.33273 | 0.10982
26.6584 | 51.8689 | 48.8189 | 59.3897 | 0.28616 | 0.33056 | 0.10911
26.6625 | 51.7579 | 48.697 | 59.3763 | 0.28443 | 0.32827 | 0.10833
26.6667 | 51.6389 | 48.5715 | 59.3557 | 0.28265 | 0.32597 | 0.10756
26.6709 | 51.5204 | 48.4433 | 59.3386 | 0.28091 | 0.32367 | 0.10682
26.675 | 51.4115 | 48.314 | 59.3279 | 0.27908 | 0.32135 | 0.10604
26.6792 | 51.2938 | 48.1758 | 59.3125 | 0.27731 | 0.31901 | 0.10526
26.6834 | 51.1734 | 48.0341 | 59.2934 | 0.27554 | 0.31666 | 0.10455
26.6875 | 51.0543 | 47.8815 | 59.2798 | 0.27373 | 0.31433 | 0.10379
26.6917 | 50.9293 | 47.728 | 59.2629 | 0.27183 | 0.31196 | 0.10297
26.6959 | 50.8032 | 47.5714 | 59.2396 | 0.26996 | 0.3096 | 0.10223
26.7 | 50.6777 | 47.4148 | 59.2247 | 0.26806 | 0.30721 | 0.1015
26.7042 | 50.5384 | 47.2629 | 59.2137 | 0.26616 | 0.3048 | 0.10067
26.7084 | 50.3927 | 47.1043 | 59.1936 | 0.26426 | 0.30236 | 0.099885
26.7125 | 50.2476 | 46.9236 | 59.1712 | 0.26232 | 0.3 | 0.099194
26.7167 | 50.1031 | 46.7407 | 59.1538 | 0.26032 | 0.29759 | 0.098412
26.7209 | 49.9583 | 46.5694 | 59.1301 | 0.25833 | 0.29503 | 0.097577
26.725 | 49.8159 | 46.3948 | 59.1073 | 0.25631 | 0.29247 | 0.096814
26.7292 | 49.6688 | 46.2102 | 59.1005 | 0.25424 | 0.29 | 0.096009
26.7334 | 49.5186 | 46.0166 | 59.0823 | 0.25213 | 0.28752 | 0.095183
26.7375 | 49.3619 | 45.7888 | 59.0451 | 0.24999 | 0.28505 | 0.094478
26.7417 | 49.2 | 45.5582 | 59.02 | 0.24781 | 0.28254 | 0.093721
26.7459 | 49.0301 | 45.3476 | 59.003 | 0.24561 | 0.27993 | 0.092777
26.75 | 48.8646 | 45.1291 | 58.9807 | 0.24334 | 0.27732 | 0.091916
26.7542 | 48.6812 | 44.8825 | 58.9588 | 0.24112 | 0.2749 | 0.091226
26.7584 | 48.5135 | 44.6291 | 58.9344 | 0.23878 | 0.27243 | 0.090433
26.7625 | 48.3428 | 44.3895 | 58.8943 | 0.23642 | 0.26974 | 0.089577
26.7667 | 48.1603 | 44.1486 | 58.8624 | 0.23403 | 0.26701 | 0.088733
26.7709 | 47.9942 | 43.9194 | 58.8516 | 0.23157 | 0.26427 | 0.087831
26.775 | 47.8049 | 43.6825 | 58.8279 | 0.22907 | 0.26149 | 0.086955
26.7792 | 47.5971 | 43.4201 | 58.7876 | 0.22659 | 0.25867 | 0.086227
26.7834 | 47.4057 | 43.1545 | 58.7508 | 0.22401 | 0.25577 | 0.085417
26.7875 | 47.1949 | 42.9111 | 58.7203 | 0.22137 | 0.25266 | 0.084401
26.7917 | 46.9849 | 42.6621 | 58.6893 | 0.21875 | 0.24951 | 0.083457
26.7959 | 46.7789 | 42.3804 | 58.6604 | 0.2161 | 0.24648 | 0.082639
26.8 | 46.554 | 42.0903 | 58.6251 | 0.21339 | 0.24341 | 0.081776
26.8042 | 46.3217 | 41.811 | 58.5738 | 0.21068 | 0.24012 | 0.08085
26.8084 | 46.0964 | 41.5297 | 58.5285 | 0.20787 | 0.23677 | 0.079904
26.8125 | 45.8652 | 41.26 | 58.4983 | 0.20497 | 0.23339 | 0.078888
26.8167 | 45.6236 | 40.9829 | 58.4606 | 0.20211 | 0.22997 | 0.077909
26.8209 | 45.3772 | 40.6907 | 58.4092 | 0.19918 | 0.22646 | 0.077036
26.825 | 45.1197 | 40.3945 | 58.3557 | 0.19618 | 0.22289 | 0.076107
26.8292 | 44.8529 | 40.1211 | 58.3076 | 0.19315 | 0.21911 | 0.075014
26.8334 | 44.5894 | 39.8448 | 58.2589 | 0.19003 | 0.21527 | 0.073949
26.8375 | 44.3174 | 39.5157 | 58.2115 | 0.18687 | 0.21154 | 0.07295
26.8417 | 44.038 | 39.1777 | 58.1584 | 0.18367 | 0.20775 | 0.071937
26.8459 | 43.7512 | 38.8307 | 58.0927 | 0.18042 | 0.20385 | 0.070875
26.85 | 43.4597 | 38.4788 | 58.0264 | 0.17707 | 0.19988 | 0.06979
26.8542 | 43.1593 | 38.1109 | 57.9692 | 0.17368 | 0.19596 | 0.068632
26.8584 | 42.8601 | 37.7348 | 57.9091 | 0.17019 | 0.19197 | 0.067471
26.8625 | 42.5467 | 37.3076 | 57.8392 | 0.16666 | 0.18805 | 0.066365
26.8667 | 42.2316 | 36.8707 | 57.7697 | 0.16304 | 0.18404 | 0.065211
26.8709 | 41.9023 | 36.4424 | 57.7005 | 0.15937 | 0.1799 | 0.063957
26.875 | 41.555 | 36.0022 | 57.6225 | 0.15565 | 0.17568 | 0.062711
26.8792 | 41.198 | 35.5376 | 57.5316 | 0.15186 | 0.17146 | 0.061521
26.8834 | 40.8319 | 35.061 | 57.4374 | 0.148 | 0.16716 | 0.060278
26.8875 | 40.4511 | 34.6046 | 57.3341 | 0.14407 | 0.16267 | 0.059
26.8917 | 40.0729 | 34.1489 | 57.2454 | 0.14006 | 0.15807 | 0.057638
26.8959 | 39.7004 | 33.7167 | 57.175 | 0.13593 | 0.1533 | 0.056191
26.9 | 39.305 | 33.2723 | 57.0899 | 0.13176 | 0.14847 | 0.054749
26.9042 | 38.9045 | 32.8001 | 56.9819 | 0.12748 | 0.14351 | 0.053342
26.9084 | 38.4755 | 32.3089 | 56.848 | 0.12313 | 0.13849 | 0.0519
26.9125 | 38.0276 | 31.8241 | 56.6951 | 0.11869 | 0.13331 | 0.050373
26.9167 | 37.5771 | 31.3408 | 56.5539 | 0.11416 | 0.12804 | 0.048772
26.9209 | 37.1319 | 30.8256 | 56.4223 | 0.10949 | 0.12272 | 0.047105
26.925 | 36.688 | 30.3109 | 56.3054 | 0.10474 | 0.1173 | 0.045378
26.9292 | 36.2418 | 29.7835 | 56.2037 | 0.099877 | 0.11177 | 0.043564
26.9334 | 35.7626 | 29.2353 | 56.073 | 0.094937 | 0.10614 | 0.041704
26.9375 | 35.2642 | 28.6496 | 55.9157 | 0.089901 | 0.10044 | 0.039787
26.9417 | 34.736 | 28.0401 | 55.7286 | 0.084759 | 0.094622 | 0.037802
26.9459 | 34.1935 | 27.3917 | 55.5062 | 0.079501 | 0.088721 | 0.035759
26.95 | 33.6582 | 26.7397 | 55.2977 | 0.074122 | 0.082695 | 0.033627
26.9542 | 33.1048 | 26.1037 | 55.1114 | 0.068641 | 0.076532 | 0.031383
26.9584 | 32.5558 | 25.4614 | 54.9255 | 0.063037 | 0.070247 | 0.029071
26.9625 | 32.0041 | 24.8014 | 54.7283 | 0.057311 | 0.063845 | 0.026706
26.9667 | 31.4518 | 24.1283 | 54.5206 | 0.051439 | 0.057299 | 0.024201
26.9709 | 30.8816 | 23.4819 | 54.3068 | 0.045452 | 0.050587 | 0.021554
26.975 | 30.302 | 22.8245 | 54.0836 | 0.039329 | 0.043738 | 0.018788
26.9792 | 29.7082 | 22.1797 | 53.8529 | 0.033084 | 0.036755 | 0.015909
26.9834 | 29.094 | 21.5146 | 53.5934 | 0.026722 | 0.029652 | 0.012954
26.9875 | 28.467 | 20.8165 | 53.3025 | 0.020233 | 0.022432 | 0.0099088
26.9917 | 27.837 | 20.1083 | 53.0039 | 0.013618 | 0.015086 | 0.0067399
26.9959 | 27.1792 | 19.413 | 52.7066 | 0.0068689 | 0.0075986 | 0.0034346
27 | 26.533 | 18.7217 | 52.4168 | 0 | 0 | 0
27.0042 | 26.744 | 18.9615 | 52.5606 | 0 | 0 | 0
27.0084 | 26.9718 | 19.2147 | 52.722 | 0 | 0 | 0
27.0125 | 26.6407 | 18.8464 | 52.6174 | 0 | 0 | 0
27.0167 | 26.309 | 18.4801 | 52.5079 | 0 | 0 | 0
27.0209 | 26.9209 | 19.1626 | 52.8716 | 0 | 0 | 0
27.025 | 27.5511 | 19.8591 | 53.2485 | 0 | 0 | 0
27.0292 | 27.3745 | 19.652 | 53.2193 | 0 | 0 | 0
27.0334 | 27.1911 | 19.443 | 53.1805 | 0 | 0 | 0
27.0375 | 27.868 | 20.1956 | 53.579 | 0 | 0 | 0
27.0417 | 28.5626 | 20.9642 | 53.9917 | 0 | 0 | 0
27.0459 | 28.4185 | 20.7957 | 53.9779 | 0 | 0 | 0
27.05 | 28.2985 | 20.6403 | 53.9808 | 0 | 0 | 0
27.0542 | 29.0346 | 21.4389 | 54.4398 | 0 | 0 | 0
27.0584 | 29.7936 | 22.2569 | 54.9186 | 0 | 0 | 0
27.0625 | 29.6913 | 22.1457 | 54.9752 | 0 | 0 | 0
27.0667 | 29.5979 | 22.0355 | 55.0305 | 0 | 0 | 0
27.0709 | 30.3438 | 22.8494 | 55.5133 | 0 | 0 | 0
27.075 | 31.0968 | 23.6675 | 55.9993 | 0 | 0 | 0
27.0792 | 30.9774 | 23.5359 | 56.0564 | 0 | 0 | 0
27.0834 | 30.8264 | 23.383 | 56.0829 | 0 | 0 | 0
27.0875 | 31.5012 | 24.1394 | 56.5034 | 0 | 0 | 0
27.0917 | 32.163 | 24.8852 | 56.9144 | 0 | 0 | 0
27.0959 | 31.9646 | 24.6793 | 56.8901 | 0 | 0 | 0
27.1 | 31.746 | 24.4557 | 56.843 | 0 | 0 | 0
27.1042 | 32.3579 | 25.1495 | 57.2044 | 0 | 0 | 0
27.1084 | 32.9796 | 25.8446 | 57.5697 | 0 | 0 | 0
27.1125 | 32.7499 | 25.6036 | 57.5032 | 0 | 0 | 0
27.1167 | 32.5206 | 25.3609 | 57.431 | 0 | 0 | 0
27.1209 | 33.1459 | 26.0564 | 57.7937 | 0 | 0 | 0
27.125 | 33.7859 | 26.7672 | 58.1733 | 0 | 0 | 0
27.1292 | 33.58 | 26.5405 | 58.1279 | 0 | 0 | 0
27.1334 | 33.3868 | 26.3158 | 58.0824 | 0 | 0 | 0
27.1375 | 34.0403 | 27.0475 | 58.4713 | 0 | 0 | 0
27.1417 | 34.7102 | 27.791 | 58.8635 | 0 | 0 | 0
27.1459 | 34.5352 | 27.6007 | 58.8329 | 0 | 0 | 0
27.15 | 34.3581 | 27.4084 | 58.8002 | 0 | 0 | 0
27.1542 | 35.0219 | 28.1484 | 59.1883 | 0 | 0 | 0
27.1584 | 35.6919 | 28.892 | 59.5809 | 0 | 0 | 0
27.1625 | 35.5059 | 28.7057 | 59.5539 | 0 | 0 | 0
27.1667 | 35.3099 | 28.511 | 59.5098 | 0 | 0 | 0
27.1709 | 35.9467 | 29.2277 | 59.8643 | 0 | 0 | 0
27.175 | 36.5853 | 29.9498 | 60.2269 | 0 | 0 | 0
27.1792 | 36.3886 | 29.735 | 60.1843 | 0 | 0 | 0
27.1834 | 36.1698 | 29.5097 | 60.1273 | 0 | 0 | 0
27.1875 | 36.7726 | 30.1867 | 60.4655 | 0 | 0 | 0
27.1917 | 37.3852 | 30.8708 | 60.8175 | 0 | 0 | 0
27.1959 | 37.171 | 30.6524 | 60.7682 | 0 | 0 | 0
27.2 | 36.9544 | 30.4294 | 60.7083 | 0 | 0 | 0
27.2042 | 37.5667 | 31.1161 | 61.0567 | 0 | 0 | 0
27.2084 | 38.1793 | 31.8068 | 61.4047 | 0 | 0 | 0
27.2125 | 37.9564 | 31.5558 | 61.3264 | 0 | 0 | 0
27.2167 | 37.7322 | 31.3024 | 61.2491 | 0 | 0 | 0
27.2209 | 38.3456 | 32.0053 | 61.5973 | 0 | 0 | 0
27.225 | 38.9668 | 32.7139 | 61.9452 | 0 | 0 | 0
27.2292 | 38.7486 | 32.4939 | 61.8807 | 0 | 0 | 0
27.2334 | 38.5298 | 32.2675 | 61.8047 | 0 | 0 | 0
27.2375 | 39.1505 | 32.9539 | 62.1381 | 0 | 0 | 0
27.2417 | 39.7878 | 33.6489 | 62.4882 | 0 | 0 | 0
27.2459 | 39.5644 | 33.4064 | 62.4071 | 0 | 0 | 0
27.25 | 39.3244 | 33.1562 | 62.3088 | 0 | 0 | 0
27.2542 | 39.9428 | 33.8721 | 62.6445 | 0 | 0 | 0
27.2584 | 40.5706 | 34.5953 | 62.9824 | 0 | 0 | 0
27.2625 | 40.3475 | 34.3917 | 62.8907 | 0 | 0 | 0
27.2667 | 40.1227 | 34.1835 | 62.7883 | 0 | 0 | 0
27.2709 | 40.7624 | 34.8859 | 63.1166 | 0 | 0 | 0
27.275 | 41.4067 | 35.593 | 63.4549 | 0 | 0 | 0
27.2792 | 41.1785 | 35.3455 | 63.3379 | 0 | 0 | 0
27.2834 | 40.9469 | 35.094 | 63.2167 | 0 | 0 | 0
27.2875 | 41.5742 | 35.8459 | 63.5551 | 0 | 0 | 0
27.2917 | 42.2077 | 36.6047 | 63.8902 | 0 | 0 | 0
27.2959 | 41.9873 | 36.4041 | 63.7862 | 0 | 0 | 0
27.3 | 41.765 | 36.1969 | 63.6709 | 0 | 0 | 0
27.3042 | 42.4024 | 36.8976 | 63.9714 | 0 | 0 | 0
27.3084 | 43.0437 | 37.6058 | 64.2839 | 0 | 0 | 0
27.3125 | 42.8372 | 37.3879 | 64.1764 | 0 | 0 | 0
27.3167 | 42.6247 | 37.1654 | 64.0591 | 0 | 0 | 0
27.3209 | 43.2395 | 37.8883 | 64.357 | 0 | 0 | 0
27.325 | 43.8669 | 38.6183 | 64.6602 | 0 | 0 | 0
27.3292 | 43.6617 | 38.4362 | 64.5626 | 0 | 0 | 0
27.3334 | 43.4511 | 38.2498 | 64.4574 | 0 | 0 | 0
27.3375 | 44.08 | 38.9643 | 64.7588 | 0 | 0 | 0
27.3417 | 44.7214 | 39.6862 | 65.0745 | 0 | 0 | 0
27.3459 | 44.524 | 39.482 | 64.9761 | 0 | 0 | 0
27.35 | 44.3202 | 39.2732 | 64.8713 | 0 | 0 | 0
27.3542 | 44.9557 | 39.9976 | 65.1855 | 0 | 0 | 0
27.3584 | 45.6009 | 40.73 | 65.5089 | 0 | 0 | 0
27.3625 | 45.3971 | 40.5288 | 65.4025 | 0 | 0 | 0
27.3667 | 45.1821 | 40.323 | 65.286 | 0 | 0 | 0
27.3709 | 45.8234 | 41.0835 | 65.612 | 0 | 0 | 0
27.375 | 46.4731 | 41.8519 | 65.9394 | 0 | 0 | 0
27.3792 | 46.2661 | 41.6534 | 65.8199 | 0 | 0 | 0
27.3834 | 46.0588 | 41.4512 | 65.6962 | 0 | 0 | 0
27.3875 | 46.7199 | 42.1924 | 66.0095 | 0 | 0 | 0
27.3917 | 47.3901 | 42.9407 | 66.332 | 0 | 0 | 0
27.3959 | 47.1944 | 42.7632 | 66.2185 | 0 | 0 | 0
27.4 | 46.9917 | 42.5802 | 66.0941 | 0 | 0 | 0
27.4042 | 47.6425 | 43.3453 | 66.4021 | 0 | 0 | 0
27.4084 | 48.2995 | 44.1197 | 66.7194 | 0 | 0 | 0
27.4125 | 48.1153 | 43.9609 | 66.6163 | 0 | 0 | 0
27.4167 | 47.9302 | 43.7987 | 66.5029 | 0 | 0 | 0
27.4209 | 48.5891 | 44.5615 | 66.8025 | 0 | 0 | 0
27.425 | 49.2585 | 45.3321 | 67.112 | 0 | 0 | 0
27.4292 | 49.0804 | 45.1846 | 67.0102 | 0 | 0 | 0
27.4334 | 48.9067 | 45.034 | 66.9023 | 0 | 0 | 0
27.4375 | 49.5773 | 45.8144 | 67.211 | 0 | 0 | 0
27.4417 | 50.2517 | 46.6017 | 67.5254 | 0 | 0 | 0
27.4459 | 50.0908 | 46.4557 | 67.4134 | 0 | 0 | 0
27.45 | 49.9263 | 46.3064 | 67.2971 | 0 | 0 | 0
27.4542 | 50.5991 | 47.107 | 67.6104 | 0 | 0 | 0
27.4584 | 51.2886 | 47.9158 | 67.9294 | 0 | 0 | 0
27.4625 | 51.1266 | 47.7909 | 67.8242 | 0 | 0 | 0
27.4667 | 50.9559 | 47.6618 | 67.7057 | 0 | 0 | 0
27.4709 | 51.6521 | 48.461 | 68.0198 | 0 | 0 | 0
27.475 | 52.3566 | 49.2699 | 68.3475 | 0 | 0 | 0
27.4792 | 52.2163 | 49.126 | 68.2316 | 0 | 0 | 0
27.4834 | 52.0635 | 48.9795 | 68.1102 | 0 | 0 | 0
27.4875 | 52.7723 | 49.8003 | 68.4281 | 0 | 0 | 0
27.4917 | 53.4961 | 50.6321 | 68.7517 | 0 | 0 | 0
27.4959 | 53.36 | 50.54 | 68.6464 | 0 | 0 | 0
27.5 | 53.2262 | 50.4468 | 68.5319 | 0 | 0 | 0
27.5042 | 53.9394 | 51.2867 | 68.847 | 0 | 0 | 0
27.5084 | 54.6631 | 52.1357 | 69.1691 | 0 | 0 | 0
27.5125 | 54.5378 | 52.0446 | 69.0635 | 0 | 0 | 0
27.5167 | 54.4175 | 51.952 | 68.9535 | 0 | 0 | 0
27.5209 | 55.1526 | 52.8039 | 69.2665 | 0 | 0 | 0
27.525 | 55.9009 | 53.6663 | 69.5869 | 0 | 0 | 0
27.5292 | 55.8015 | 53.6002 | 69.4893 | 0 | 0 | 0
27.5334 | 55.7006 | 53.5332 | 69.3832 | 0 | 0 | 0
27.5375 | 56.4534 | 54.4025 | 69.6969 | 0 | 0 | 0
27.5417 | 57.2157 | 55.2843 | 70.0207 | 0 | 0 | 0
27.5459 | 57.1266 | 55.2493 | 69.9214 | 0 | 0 | 0
27.55 | 57.038 | 55.2124 | 69.8121 | 0 | 0 | 0
27.5542 | 57.8015 | 56.1112 | 70.1349 | 0 | 0 | 0
27.5584 | 58.5814 | 57.0197 | 70.4669 | 0 | 0 | 0
27.5625 | 58.519 | 56.9882 | 70.3602 | 0 | 0 | 0
27.5667 | 58.4548 | 56.9582 | 70.2461 | 0 | 0 | 0
27.5709 | 59.25 | 57.8902 | 70.5779 | 0 | 0 | 0
27.575 | 60.0594 | 58.8336 | 70.9158 | 0 | 0 | 0
27.5792 | 60.0205 | 58.8215 | 70.812 | 0 | 0 | 0
27.5834 | 59.9767 | 58.81 | 70.7042 | 0 | 0 | 0
27.5875 | 60.7868 | 59.7568 | 71.0303 | 0 | 0 | 0
27.5917 | 61.6077 | 60.7181 | 71.3653 | 0 | 0 | 0
27.5959 | 61.589 | 60.7536 | 71.2758 | 0 | 0 | 0
27.6 | 61.5782 | 60.7905 | 71.18 | 0 | 0 | 0
27.6042 | 62.4191 | 61.7653 | 71.5036 | 0 | 0 | 0
27.6084 | 63.2759 | 62.7566 | 71.8356 | 0 | 0 | 0
27.6125 | 63.3063 | 62.8387 | 71.7583 | 0 | 0 | 0
27.6167 | 63.32 | 62.9241 | 71.6723 | 0 | 0 | 0
27.6209 | 64.1913 | 63.9284 | 71.9977 | 0 | 0 | 0
27.625 | 65.0791 | 64.9474 | 72.3359 | 0 | 0 | 0
27.6292 | 65.1074 | 65.0507 | 72.2612 | 0 | 0 | 0
27.6334 | 65.1602 | 65.1584 | 72.1785 | 0 | 0 | 0
27.6375 | 66.0714 | 66.206 | 72.5157 | 0 | 0 | 0
27.6417 | 66.9889 | 67.2689 | 72.8667 | 0 | 0 | 0
27.6459 | 67.0793 | 67.4006 | 72.7903 | 0 | 0 | 0
27.65 | 67.1645 | 67.5381 | 72.7084 | 0 | 0 | 0
27.6542 | 68.1092 | 68.6487 | 73.066 | 0 | 0 | 0
27.6584 | 69.076 | 69.7776 | 73.4309 | 0 | 0 | 0
27.6625 | 69.1994 | 69.9634 | 73.3612 | 0 | 0 | 0
27.6667 | 69.3232 | 70.1528 | 73.2887 | 0 | 0 | 0
27.6709 | 70.308 | 71.3023 | 73.6572 | 0 | 0 | 0
27.675 | 71.3115 | 72.4703 | 74.0331 | 0 | 0 | 0
27.6792 | 71.4776 | 72.7033 | 73.9811 | 0 | 0 | 0
27.6834 | 71.6497 | 72.9413 | 73.9265 | 0 | 0 | 0
27.6875 | 72.6851 | 74.1104 | 74.2987 | 0 | 0 | 0
27.6917 | 73.739 | 75.2961 | 74.6834 | 0 | 0 | 0
27.6959 | 73.957 | 75.589 | 74.6523 | 0 | 0 | 0
27.7 | 74.1786 | 75.8908 | 74.6141 | 0 | 0 | 0
27.7042 | 75.2634 | 77.1346 | 75 | 0 | 0 | 0
27.7084 | 76.3718 | 78.398 | 75.402 | 0 | 0 | 0
27.7125 | 76.6423 | 78.7493 | 75.3895 | 0 | 0 | 0
27.7167 | 76.9169 | 79.1101 | 75.3714 | 0 | 0 | 0
27.7209 | 78.0596 | 80.4445 | 75.7816 | 0 | 0 | 0
27.725 | 79.2149 | 81.801 | 76.2005 | 0 | 0 | 0
27.7292 | 79.5404 | 82.2338 | 76.1922 | 0 | 0 | 0
27.7334 | 79.8835 | 82.6823 | 76.1884 | 0 | 0 | 0
27.7375 | 81.093 | 84.1098 | 76.6314 | 0 | 0 | 0
27.7417 | 82.3308 | 85.5682 | 77.0924 | 0 | 0 | 0
27.7459 | 82.7477 | 86.0907 | 77.1348 | 0 | 0 | 0
27.75 | 83.1632 | 86.6189 | 77.1616 | 0 | 0 | 0
27.7542 | 84.4356 | 88.0803 | 77.6086 | 0 | 0 | 0
27.7584 | 85.7345 | 89.5656 | 78.0704 | 0 | 0 | 0
27.7625 | 86.1985 | 90.1411 | 78.1167 | 0 | 0 | 0
27.7667 | 86.6931 | 90.7401 | 78.1865 | 0 | 0 | 0
27.7709 | 88.0703 | 92.2858 | 78.7102 | 0 | 0 | 0
27.775 | 89.4769 | 93.8543 | 79.2533 | 0 | 0 | 0
27.7792 | 90.0471 | 94.5223 | 79.3865 | 0 | 0 | 0
27.7834 | 90.6129 | 95.1903 | 79.4947 | 0 | 0 | 0
27.7875 | 92.0418 | 96.8107 | 80.009 | 0 | 0 | 0
27.7917 | 93.5089 | 98.4608 | 80.5513 | 0 | 0 | 0
27.7959 | 94.1493 | 99.2168 | 80.6902 | 0 | 0 | 0
27.8 | 94.8329 | 100.0061 | 80.8647 | 0 | 0 | 0
27.8042 | 96.3937 | 101.7921 | 81.5125 | 0 | 0 | 0
27.8084 | 97.9828 | 103.6092 | 82.1776 | 0 | 0 | 0
27.8125 | 98.7562 | 104.5008 | 82.4187 | 0 | 0 | 0
27.8167 | 99.5357 | 105.4072 | 82.659 | 0 | 0 | 0
27.8209 | 101.1824 | 107.2913 | 83.3426 | 0 | 0 | 0
27.825 | 102.8481 | 109.2075 | 84.0492 | 0 | 0 | 0
27.8292 | 103.6933 | 110.1875 | 84.3428 | 0 | 0 | 0
27.8334 | 104.5508 | 111.1872 | 84.6483 | 0 | 0 | 0
27.8375 | 106.2864 | 113.1159 | 85.3985 | 0 | 0 | 0
27.8417 | 108.064 | 115.0853 | 86.194 | 0 | 0 | 0
27.8459 | 109.0164 | 116.1591 | 86.6037 | 0 | 0 | 0
27.85 | 109.9904 | 117.2597 | 87.0378 | 0 | 0 | 0
27.8542 | 111.8595 | 119.3061 | 87.9236 | 0 | 0 | 0
27.8584 | 113.7446 | 121.3758 | 88.8318 | 0 | 0 | 0
27.8625 | 114.0461 | 121.6951 | 88.9483 | 0 | 0 | 0
27.8667 | 114.3359 | 122.0093 | 89.0532 | 0 | 0 | 0
27.8709 | 114.9717 | 122.712 | 89.318 | 0 | 0 | 0
27.875 | 115.6105 | 123.4156 | 89.5881 | 0 | 0 | 0
27.8792 | 115.1522 | 122.899 | 89.3031 | 0 | 0 | 0
27.8834 | 114.6742 | 122.368 | 89.0034 | 0 | 0 | 0
27.8875 | 114.9241 | 122.6542 | 89.0706 | 0 | 0 | 0
27.8917 | 115.18 | 122.9428 | 89.1471 | 0 | 0 | 0
27.8959 | 114.5388 | 122.2299 | 88.7665 | 0 | 0 | 0
27.9 | 113.8899 | 121.5063 | 88.3805 | 0 | 0 | 0
27.9042 | 114.0659 | 121.7038 | 88.4205 | 0 | 0 | 0
27.9084 | 114.223 | 121.8912 | 88.4485 | 0 | 0 | 0
27.9125 | 113.512 | 121.1219 | 88.0219 | 0 | 0 | 0
27.9167 | 112.7747 | 120.3302 | 87.5711 | 0 | 0 | 0
27.9209 | 112.8891 | 120.4569 | 87.5334 | 0 | 0 | 0
27.925 | 112.9882 | 120.5764 | 87.4899 | 0 | 0 | 0
27.9292 | 112.2411 | 119.7615 | 87.0137 | 0 | 0 | 0
27.9334 | 111.4713 | 118.9329 | 86.5222 | 0 | 0 | 0
27.9375 | 111.5671 | 119.0456 | 86.4468 | 0 | 0 | 0
27.9417 | 111.6825 | 119.1714 | 86.3936 | 0 | 0 | 0
27.9459 | 110.9738 | 118.3845 | 85.9399 | 0 | 0 | 0
27.95 | 110.2779 | 117.6065 | 85.4955 | 0 | 0 | 0
27.9542 | 110.4444 | 117.7817 | 85.4893 | 0 | 0 | 0
27.9584 | 110.6385 | 117.9781 | 85.51 | 0 | 0 | 0
27.9625 | 110.0058 | 117.2627 | 85.1244 | 0 | 0 | 0
27.9667 | 109.3726 | 116.5526 | 84.7421 | 0 | 0 | 0
27.9709 | 109.6001 | 116.7873 | 84.801 | 0 | 0 | 0
27.975 | 109.8319 | 117.0305 | 84.8724 | 0 | 0 | 0
27.9792 | 109.214 | 116.338 | 84.5142 | 0 | 0 | 0
27.9834 | 108.5872 | 115.6338 | 84.1433 | 0 | 0 | 0
27.9875 | 108.8051 | 115.8739 | 84.199 | 0 | 0 | 0
27.9917 | 109.013 | 116.1119 | 84.2517 | 0 | 0 | 0
27.9959 | 108.3741 | 115.3972 | 83.8712 | 0 | 0 | 0
28 | 107.7147 | 114.6694 | 83.4857 | 0 | 0 | 0
28.0042 | 107.8983 | 114.8686 | 83.519 | 0 | 0 | 0
28.0084 | 108.0793 | 115.0665 | 83.5542 | 0 | 0 | 0
28.0125 | 107.4151 | 114.3312 | 83.1682 | 0 | 0 | 0
28.0167 | 106.7403 | 113.5892 | 82.7727 | 0 | 0 | 0
28.0209 | 106.9175 | 113.7696 | 82.7893 | 0 | 0 | 0
28.025 | 107.1017 | 113.958 | 82.8226 | 0 | 0 | 0
28.0292 | 106.4587 | 113.2303 | 82.4594 | 0 | 0 | 0
28.0334 | 105.8088 | 112.4963 | 82.089 | 0 | 0 | 0
28.0375 | 105.9924 | 112.6945 | 82.1233 | 0 | 0 | 0
28.0417 | 106.199 | 112.9036 | 82.1743 | 0 | 0 | 0
28.0459 | 105.5862 | 112.2201 | 81.8311 | 0 | 0 | 0
28.05 | 104.9705 | 111.5317 | 81.4762 | 0 | 0 | 0
28.0542 | 105.1848 | 111.7515 | 81.5273 | 0 | 0 | 0
28.0584 | 105.4006 | 111.9755 | 81.585 | 0 | 0 | 0
28.0625 | 104.7856 | 111.2788 | 81.2275 | 0 | 0 | 0
28.0667 | 104.1705 | 110.5786 | 80.873 | 0 | 0 | 0
28.0709 | 104.3931 | 110.832 | 80.9483 | 0 | 0 | 0
28.075 | 104.6194 | 111.0884 | 81.0235 | 0 | 0 | 0
28.0792 | 104.0078 | 110.397 | 80.6789 | 0 | 0 | 0
28.0834 | 103.3894 | 109.6987 | 80.3308 | 0 | 0 | 0
28.0875 | 103.6107 | 109.9174 | 80.3916 | 0 | 0 | 0
28.0917 | 103.8361 | 110.143 | 80.4683 | 0 | 0 | 0
28.0959 | 103.215 | 109.449 | 80.1282 | 0 | 0 | 0
28.1 | 102.573 | 108.7461 | 79.771 | 0 | 0 | 0
28.1042 | 102.7958 | 108.9961 | 79.8507 | 0 | 0 | 0
28.1084 | 103.0312 | 109.2534 | 79.9425 | 0 | 0 | 0
28.1125 | 102.4129 | 108.5534 | 79.6028 | 0 | 0 | 0
28.1167 | 101.7888 | 107.8468 | 79.2615 | 0 | 0 | 0
28.1209 | 102.0193 | 108.0515 | 79.3494 | 0 | 0 | 0
28.125 | 102.251 | 108.2602 | 79.4508 | 0 | 0 | 0
28.1292 | 101.6124 | 107.544 | 79.1129 | 0 | 0 | 0
28.1334 | 100.9685 | 106.823 | 78.7681 | 0 | 0 | 0
28.1375 | 101.193 | 107.0825 | 78.8852 | 0 | 0 | 0
28.1417 | 101.4213 | 107.3468 | 79.0032 | 0 | 0 | 0
28.1459 | 100.7956 | 106.615 | 78.6693 | 0 | 0 | 0
28.15 | 100.1643 | 105.8757 | 78.335 | 0 | 0 | 0
28.1542 | 100.3889 | 106.0662 | 78.4279 | 0 | 0 | 0
28.1584 | 100.6147 | 106.2633 | 78.5361 | 0 | 0 | 0
28.1625 | 99.9835 | 105.5539 | 78.2307 | 0 | 0 | 0
28.1667 | 99.347 | 104.8375 | 77.9152 | 0 | 0 | 0
28.1709 | 99.5482 | 105.0601 | 78.0202 | 0 | 0 | 0
28.175 | 99.7579 | 105.2874 | 78.1335 | 0 | 0 | 0
28.1792 | 99.1419 | 104.5784 | 77.8381 | 0 | 0 | 0
28.1834 | 98.5145 | 103.8624 | 77.5375 | 0 | 0 | 0
28.1875 | 98.7242 | 104.0466 | 77.6372 | 0 | 0 | 0
28.1917 | 98.9397 | 104.2353 | 77.7475 | 0 | 0 | 0
28.1959 | 98.3151 | 103.5145 | 77.4465 | 0 | 0 | 0
28.2 | 97.6778 | 102.7862 | 77.1327 | 0 | 0 | 0
28.2042 | 97.879 | 102.9919 | 77.2356 | 0 | 0 | 0
28.2084 | 98.0857 | 103.2024 | 77.3436 | 0 | 0 | 0
28.2125 | 97.4496 | 102.4798 | 77.0282 | 0 | 0 | 0
28.2167 | 96.8018 | 101.7492 | 76.702 | 0 | 0 | 0
28.2209 | 97.0075 | 101.9634 | 76.812 | 0 | 0 | 0
28.225 | 97.2234 | 102.1821 | 76.9289 | 0 | 0 | 0
28.2292 | 96.5819 | 101.4271 | 76.5997 | 0 | 0 | 0
28.2334 | 95.9353 | 100.6647 | 76.2702 | 0 | 0 | 0
28.2375 | 96.149 | 100.8588 | 76.3845 | 0 | 0 | 0
28.2417 | 96.3643 | 101.0567 | 76.5058 | 0 | 0 | 0
28.2459 | 95.7095 | 100.3214 | 76.1927 | 0 | 0 | 0
28.25 | 95.0438 | 99.5783 | 75.8693 | 0 | 0 | 0
28.2542 | 95.2383 | 99.766 | 75.9811 | 0 | 0 | 0
28.2584 | 95.4383 | 99.9598 | 76.1035 | 0 | 0 | 0
28.2625 | 94.7912 | 99.2046 | 75.7984 | 0 | 0 | 0
28.2667 | 94.1394 | 98.4412 | 75.4841 | 0 | 0 | 0
28.2709 | 94.3278 | 98.6029 | 75.5855 | 0 | 0 | 0
28.275 | 94.519 | 98.7678 | 75.6973 | 0 | 0 | 0
28.2792 | 93.8637 | 98.01 | 75.3975 | 0 | 0 | 0
28.2834 | 93.2004 | 97.2445 | 75.0894 | 0 | 0 | 0
28.2875 | 93.3838 | 97.3999 | 75.1942 | 0 | 0 | 0
28.2917 | 93.5614 | 97.5582 | 75.3042 | 0 | 0 | 0
28.2959 | 92.8986 | 96.7813 | 74.9932 | 0 | 0 | 0
28.3 | 92.2288 | 95.9973 | 74.6767 | 0 | 0 | 0
28.3042 | 92.3932 | 96.1515 | 74.7894 | 0 | 0 | 0
28.3084 | 92.5645 | 96.3094 | 74.9066 | 0 | 0 | 0
28.3125 | 91.8928 | 95.519 | 74.5959 | 0 | 0 | 0
28.3167 | 91.2038 | 94.7202 | 74.2765 | 0 | 0 | 0
28.3209 | 91.3741 | 94.8484 | 74.3828 | 0 | 0 | 0
28.325 | 91.5501 | 94.9811 | 74.504 | 0 | 0 | 0
28.3292 | 90.8643 | 94.1771 | 74.1868 | 0 | 0 | 0
28.3334 | 90.1678 | 93.3641 | 73.8591 | 0 | 0 | 0
28.3375 | 90.3159 | 93.5138 | 73.9753 | 0 | 0 | 0
28.3417 | 90.4781 | 93.6668 | 74.0953 | 0 | 0 | 0
28.3459 | 89.7736 | 92.8657 | 73.781 | 0 | 0 | 0
28.35 | 89.0594 | 92.0542 | 73.4594 | 0 | 0 | 0
28.3542 | 89.1988 | 92.1596 | 73.5649 | 0 | 0 | 0
28.3584 | 89.336 | 92.2657 | 73.6796 | 0 | 0 | 0
28.3625 | 88.6277 | 91.4309 | 73.3645 | 0 | 0 | 0
28.3667 | 87.9099 | 90.5868 | 73.044 | 0 | 0 | 0
28.3709 | 88.0444 | 90.684 | 73.1489 | 0 | 0 | 0
28.375 | 88.1751 | 90.7831 | 73.259 | 0 | 0 | 0
28.3792 | 87.452 | 89.942 | 72.9484 | 0 | 0 | 0
28.3834 | 86.7139 | 89.0907 | 72.6293 | 0 | 0 | 0
28.3875 | 86.8235 | 89.1665 | 72.728 | 0 | 0 | 0
28.3917 | 86.9327 | 89.2441 | 72.8357 | 0 | 0 | 0
28.3959 | 86.187 | 88.3889 | 72.5219 | 0 | 0 | 0
28.4 | 85.4319 | 87.521 | 72.1975 | 0 | 0 | 0
28.4042 | 85.5272 | 87.571 | 72.2998 | 0 | 0 | 0
28.4084 | 85.6244 | 87.6219 | 72.4117 | 0 | 0 | 0
28.4125 | 84.8721 | 86.7297 | 72.0875 | 0 | 0 | 0
28.4167 | 84.1035 | 85.8286 | 71.7547 | 0 | 0 | 0
28.4209 | 84.1805 | 85.8737 | 71.864 | 0 | 0 | 0
28.425 | 84.2586 | 85.9182 | 71.9798 | 0 | 0 | 0
28.4292 | 83.4764 | 84.9978 | 71.6499 | 0 | 0 | 0
28.4334 | 82.6787 | 84.0658 | 71.3148 | 0 | 0 | 0
28.4375 | 82.7273 | 84.0871 | 71.4173 | 0 | 0 | 0
28.4417 | 82.7791 | 84.1088 | 71.525 | 0 | 0 | 0
28.4459 | 81.9793 | 83.1814 | 71.2033 | 0 | 0 | 0
28.45 | 81.1724 | 82.2401 | 70.8723 | 0 | 0 | 0
28.4542 | 81.2051 | 82.2209 | 70.9625 | 0 | 0 | 0
28.4584 | 81.2329 | 82.2011 | 71.0587 | 0 | 0 | 0
28.4625 | 80.4133 | 81.2478 | 70.7394 | 0 | 0 | 0
28.4667 | 79.5707 | 80.2789 | 70.4108 | 0 | 0 | 0
28.4709 | 79.5579 | 80.2143 | 70.4901 | 0 | 0 | 0
28.475 | 79.5596 | 80.146 | 70.5794 | 0 | 0 | 0
28.4792 | 78.6939 | 79.1553 | 70.2555 | 0 | 0 | 0
28.4834 | 77.8246 | 78.1499 | 69.9196 | 0 | 0 | 0
28.4875 | 77.8118 | 78.0661 | 69.9987 | 0 | 0 | 0
28.4917 | 77.7754 | 77.9781 | 70.0865 | 0 | 0 | 0
28.4959 | 76.8905 | 76.9469 | 69.7502 | 0 | 0 | 0
28.5 | 75.9897 | 75.9011 | 69.4012 | 0 | 0 | 0
28.5042 | 75.9196 | 75.7965 | 69.4848 | 0 | 0 | 0
28.5084 | 75.8567 | 75.6872 | 69.572 | 0 | 0 | 0
28.5125 | 74.9303 | 74.6042 | 69.219 | 0 | 0 | 0
28.5167 | 73.9842 | 73.5027 | 68.8591 | 0 | 0 | 0
28.5209 | 73.8806 | 73.3396 | 68.934 | 0 | 0 | 0
28.525 | 73.7764 | 73.173 | 69.0118 | 0 | 0 | 0
28.5292 | 72.8129 | 72.0474 | 68.651 | 0 | 0 | 0
28.5334 | 71.8325 | 70.904 | 68.283 | 0 | 0 | 0
28.5375 | 71.6908 | 70.6861 | 68.3388 | 0 | 0 | 0
28.5417 | 71.5436 | 70.4628 | 68.3989 | 0 | 0 | 0
28.5459 | 70.5342 | 69.3194 | 68.035 | 0 | 0 | 0
28.55 | 69.5056 | 68.1604 | 67.6577 | 0 | 0 | 0
28.5542 | 69.3132 | 67.9017 | 67.6962 | 0 | 0 | 0
28.5584 | 69.1186 | 67.6354 | 67.7427 | 0 | 0 | 0
28.5625 | 68.0604 | 66.4232 | 67.3654 | 0 | 0 | 0
28.5667 | 66.9793 | 65.192 | 66.973 | 0 | 0 | 0
28.5709 | 66.7375 | 64.8822 | 66.9965 | 0 | 0 | 0
28.575 | 66.4881 | 64.5639 | 67.0235 | 0 | 0 | 0
28.5792 | 65.3739 | 63.2713 | 66.6184 | 0 | 0 | 0
28.5834 | 64.2504 | 61.959 | 66.2073 | 0 | 0 | 0
28.5875 | 63.9573 | 61.5721 | 66.2283 | 0 | 0 | 0
28.5917 | 63.6528 | 61.1731 | 66.2487 | 0 | 0 | 0
28.5959 | 62.4852 | 59.7917 | 65.827 | 0 | 0 | 0
28.6 | 61.2851 | 58.3775 | 65.3818 | 0 | 0 | 0
28.6042 | 60.9037 | 57.8826 | 65.3479 | 0 | 0 | 0
28.6084 | 60.5218 | 57.379 | 65.3267 | 0 | 0 | 0
28.6125 | 59.2777 | 55.9454 | 64.8838 | 0 | 0 | 0
28.6167 | 58.0172 | 54.493 | 64.4384 | 0 | 0 | 0
28.6209 | 57.5982 | 53.9559 | 64.4191 | 0 | 0 | 0
28.625 | 57.1529 | 53.3966 | 64.3819 | 0 | 0 | 0
28.6292 | 55.827 | 51.8956 | 63.8962 | 0 | 0 | 0
28.6334 | 54.4615 | 50.3645 | 63.377 | 0 | 0 | 0
28.6375 | 53.9264 | 49.7374 | 63.2533 | 0 | 0 | 0
28.6417 | 53.3952 | 49.1103 | 63.1529 | 0 | 0 | 0
28.6459 | 52.0024 | 47.5341 | 62.6438 | 0 | 0 | 0
28.65 | 50.5871 | 45.9392 | 62.1263 | 0 | 0 | 0
28.6542 | 50.0035 | 45.2544 | 62.0337 | 0 | 0 | 0
28.6584 | 49.3789 | 44.5405 | 61.9085 | 0 | 0 | 0
28.6625 | 47.8825 | 42.8249 | 61.3105 | 0 | 0 | 0
28.6667 | 46.346 | 41.0736 | 60.6839 | 0 | 0 | 0
28.6709 | 45.6239 | 40.2398 | 60.4714 | 0 | 0 | 0
28.675 | 44.8887 | 39.39 | 60.2579 | 0 | 0 | 0
28.6792 | 43.2843 | 37.5564 | 59.6016 | 0 | 0 | 0
28.6834 | 41.6607 | 35.6921 | 58.9258 | 0 | 0 | 0
28.6875 | 40.8605 | 34.7456 | 58.6637 | 0 | 0 | 0
28.6917 | 40.0558 | 33.7828 | 58.3983 | 0 | 0 | 0
28.6959 | 38.3727 | 31.899 | 57.6977 | 0 | 0 | 0
28.7 | 36.6534 | 29.978 | 56.9587 | 0 | 0 | 0
28.7042 | 35.765 | 28.9611 | 56.6111 | 0 | 0 | 0
28.7084 | 34.8483 | 27.9128 | 56.2338 | 0 | 0 | 0
28.7125 | 32.7864 | 25.6373 | 55.2716 | 0 | 0 | 0
28.7167 | 30.6952 | 23.3267 | 54.2731 | 0 | 0 | 0
28.7209 | 29.9197 | 22.4848 | 53.9244 | 0 | 0 | 0
28.725 | 29.1471 | 21.6366 | 53.5771 | 0 | 0 | 0
28.7292 | 28.1002 | 20.4814 | 53.101 | 0 | 0 | 0
28.7334 | 27.0449 | 19.3185 | 52.6153 | 0 | 0 | 0
28.7375 | 27.2371 | 19.5449 | 52.7639 | 0 | 0 | 0
28.7417 | 27.4483 | 19.784 | 52.927 | 0 | 0 | 0
28.7459 | 27.0484 | 19.3351 | 52.7824 | 0 | 0 | 0
28.75 | 26.6462 | 18.8846 | 52.6315 | 0 | 0 | 0
28.7542 | 27.2124 | 19.5133 | 52.9771 | 0 | 0 | 0
28.7584 | 27.7793 | 20.1488 | 53.3221 | 0 | 0 | 0
28.7625 | 27.5547 | 19.904 | 53.255 | 0 | 0 | 0
28.7667 | 27.3405 | 19.6641 | 53.1916 | 0 | 0 | 0
28.7709 | 28.0143 | 20.3935 | 53.5832 | 0 | 0 | 0
28.775 | 28.7128 | 21.1446 | 53.9983 | 0 | 0 | 0
28.7792 | 28.5736 | 20.9889 | 54.0076 | 0 | 0 | 0
28.7834 | 28.4503 | 20.8429 | 54.0255 | 0 | 0 | 0
28.7875 | 29.1824 | 21.6428 | 54.4795 | 0 | 0 | 0
28.7917 | 29.9491 | 22.4641 | 54.959 | 0 | 0 | 0
28.7959 | 29.8606 | 22.3552 | 55.0344 | 0 | 0 | 0
28.8 | 29.7684 | 22.2432 | 55.0992 | 0 | 0 | 0
28.8042 | 30.5026 | 23.0516 | 55.5757 | 0 | 0 | 0
28.8084 | 31.2321 | 23.8572 | 56.0485 | 0 | 0 | 0
28.8125 | 31.0991 | 23.7126 | 56.0849 | 0 | 0 | 0
28.8167 | 30.9368 | 23.5476 | 56.0942 | 0 | 0 | 0
28.8209 | 31.6006 | 24.2925 | 56.5115 | 0 | 0 | 0
28.825 | 32.2567 | 25.0283 | 56.9207 | 0 | 0 | 0
28.8292 | 32.0443 | 24.8108 | 56.8814 | 0 | 0 | 0
28.8334 | 31.8221 | 24.5779 | 56.8227 | 0 | 0 | 0
28.8375 | 32.4416 | 25.2775 | 57.1863 | 0 | 0 | 0
28.8417 | 33.0633 | 25.9831 | 57.5551 | 0 | 0 | 0
28.8459 | 32.8387 | 25.7376 | 57.4938 | 0 | 0 | 0
28.85 | 32.6181 | 25.4918 | 57.4355 | 0 | 0 | 0
28.8542 | 33.243 | 26.1908 | 57.8065 | 0 | 0 | 0
28.8584 | 33.8888 | 26.9022 | 58.1842 | 0 | 0 | 0
28.8625 | 33.6918 | 26.6905 | 58.1458 | 0 | 0 | 0
28.8667 | 33.5009 | 26.482 | 58.1047 | 0 | 0 | 0
28.8709 | 34.1582 | 27.2065 | 58.4833 | 0 | 0 | 0
28.875 | 34.8304 | 27.9415 | 58.8761 | 0 | 0 | 0
28.8792 | 34.6577 | 27.7595 | 58.8646 | 0 | 0 | 0
28.8834 | 34.4807 | 27.571 | 58.8386 | 0 | 0 | 0
28.8875 | 35.127 | 28.3038 | 59.2093 | 0 | 0 | 0
28.8917 | 35.7864 | 29.0442 | 59.5881 | 0 | 0 | 0
28.8959 | 35.6137 | 28.862 | 59.5628 | 0 | 0 | 0
28.9 | 35.4215 | 28.6699 | 59.5197 | 0 | 0 | 0
28.9042 | 36.0479 | 29.3656 | 59.8714 | 0 | 0 | 0
28.9084 | 36.6712 | 30.0644 | 60.2312 | 0 | 0 | 0
28.9125 | 36.4605 | 29.8439 | 60.1781 | 0 | 0 | 0
28.9167 | 36.2471 | 29.6191 | 60.1221 | 0 | 0 | 0
28.9209 | 36.8659 | 30.3263 | 60.487 | 0 | 0 | 0
28.925 | 37.4851 | 31.0367 | 60.8478 | 0 | 0 | 0
28.9292 | 37.2647 | 30.7884 | 60.7792 | 0 | 0 | 0
28.9334 | 37.0384 | 30.5357 | 60.7082 | 0 | 0 | 0
28.9375 | 37.6501 | 31.2169 | 61.0501 | 0 | 0 | 0
28.9417 | 38.2679 | 31.9059 | 61.4001 | 0 | 0 | 0
28.9459 | 38.0432 | 31.6826 | 61.3399 | 0 | 0 | 0
28.95 | 37.8096 | 31.4521 | 61.2607 | 0 | 0 | 0
28.9542 | 38.4299 | 32.1547 | 61.6072 | 0 | 0 | 0
28.9584 | 39.0721 | 32.866 | 61.9686 | 0 | 0 | 0
28.9625 | 38.8499 | 32.6167 | 61.8912 | 0 | 0 | 0
28.9667 | 38.6203 | 32.3608 | 61.806 | 0 | 0 | 0
28.9709 | 39.2411 | 33.0456 | 62.1491 | 0 | 0 | 0
28.975 | 39.8656 | 33.7361 | 62.4958 | 0 | 0 | 0
28.9792 | 39.629 | 33.5206 | 62.4096 | 0 | 0 | 0
28.9834 | 39.3907 | 33.3014 | 62.3087 | 0 | 0 | 0
28.9875 | 40.025 | 34.032 | 62.6569 | 0 | 0 | 0
28.9917 | 40.6653 | 34.7676 | 63.0074 | 0 | 0 | 0
28.9959 | 40.4435 | 34.5074 | 62.895 | 0 | 0 | 0
29 | 40.218 | 34.2417 | 62.7824 | 0 | 0 | 0
29.0042 | 40.8443 | 34.95 | 63.1098 | 0 | 0 | 0
29.0084 | 41.4755 | 35.666 | 63.4425 | 0 | 0 | 0
29.0125 | 41.2492 | 35.4748 | 63.3569 | 0 | 0 | 0
29.0167 | 41.0214 | 35.2772 | 63.2544 | 0 | 0 | 0
29.0209 | 41.6439 | 35.9968 | 63.5663 | 0 | 0 | 0
29.025 | 42.2742 | 36.7228 | 63.8854 | 0 | 0 | 0
29.0292 | 42.075 | 36.5033 | 63.7857 | 0 | 0 | 0
29.0334 | 41.866 | 36.2791 | 63.6786 | 0 | 0 | 0
29.0375 | 42.4852 | 36.9761 | 63.974 | 0 | 0 | 0
29.0417 | 43.1146 | 37.6799 | 64.2756 | 0 | 0 | 0
29.0459 | 42.9029 | 37.4874 | 64.1741 | 0 | 0 | 0
29.05 | 42.6846 | 37.2903 | 64.0596 | 0 | 0 | 0
29.0542 | 43.3055 | 38.0151 | 64.3611 | 0 | 0 | 0
29.0584 | 43.9387 | 38.7475 | 64.6727 | 0 | 0 | 0
29.0625 | 43.7322 | 38.5422 | 64.5651 | 0 | 0 | 0
29.0667 | 43.5204 | 38.3321 | 64.4522 | 0 | 0 | 0
29.0709 | 44.156 | 39.0573 | 64.7684 | 0 | 0 | 0
29.075 | 44.8049 | 39.7904 | 65.0959 | 0 | 0 | 0
29.0792 | 44.597 | 39.5661 | 64.9815 | 0 | 0 | 0
29.0834 | 44.3818 | 39.3373 | 64.864 | 0 | 0 | 0
29.0875 | 45.0249 | 40.0818 | 65.193 | 0 | 0 | 0
29.0917 | 45.6713 | 40.8336 | 65.5238 | 0 | 0 | 0
29.0959 | 45.4536 | 40.6422 | 65.4148 | 0 | 0 | 0
29.1 | 45.2316 | 40.447 | 65.2959 | 0 | 0 | 0
29.1042 | 45.8784 | 41.1807 | 65.6099 | 0 | 0 | 0
29.1084 | 46.5365 | 41.923 | 65.9345 | 0 | 0 | 0
29.1125 | 46.3417 | 41.7278 | 65.8256 | 0 | 0 | 0
29.1167 | 46.1436 | 41.5267 | 65.7066 | 0 | 0 | 0
29.1209 | 46.7884 | 42.2704 | 66.0092 | 0 | 0 | 0
29.125 | 47.4376 | 43.0214 | 66.321 | 0 | 0 | 0
29.1292 | 47.2456 | 42.8547 | 66.2206 | 0 | 0 | 0
29.1334 | 47.0495 | 42.6846 | 66.11 | 0 | 0 | 0
29.1375 | 47.7016 | 43.4383 | 66.4112 | 0 | 0 | 0
29.1417 | 48.3585 | 44.1995 | 66.719 | 0 | 0 | 0
29.1459 | 48.1714 | 44.036 | 66.611 | 0 | 0 | 0
29.15 | 47.9892 | 43.8698 | 66.4981 | 0 | 0 | 0
29.1542 | 48.6442 | 44.6432 | 66.8106 | 0 | 0 | 0
29.1584 | 49.3102 | 45.4241 | 67.1284 | 0 | 0 | 0
29.1625 | 49.1399 | 45.2639 | 67.0163 | 0 | 0 | 0
29.1667 | 48.9608 | 45.0998 | 66.8986 | 0 | 0 | 0
29.1709 | 49.6322 | 45.8791 | 67.2074 | 0 | 0 | 0
29.175 | 50.3199 | 46.667 | 67.5279 | 0 | 0 | 0
29.1792 | 50.1446 | 46.5303 | 67.4188 | 0 | 0 | 0
29.1834 | 49.9655 | 46.3889 | 67.2951 | 0 | 0 | 0
29.1875 | 50.642 | 47.1968 | 67.6146 | 0 | 0 | 0
29.1917 | 51.3325 | 48.0133 | 67.9411 | 0 | 0 | 0
29.1959 | 51.1749 | 47.8655 | 67.8266 | 0 | 0 | 0
29.2 | 51.0047 | 47.7139 | 67.7082 | 0 | 0 | 0
29.2042 | 51.7027 | 48.5005 | 68.0195 | 0 | 0 | 0
29.2084 | 52.4056 | 49.2964 | 68.3399 | 0 | 0 | 0
29.2125 | 52.2626 | 49.1747 | 68.233 | 0 | 0 | 0
29.2167 | 52.1202 | 49.0521 | 68.1183 | 0 | 0 | 0
29.2209 | 52.8255 | 49.8783 | 68.4327 | 0 | 0 | 0
29.225 | 53.539 | 50.7141 | 68.7516 | 0 | 0 | 0
29.2292 | 53.3983 | 50.6116 | 68.6479 | 0 | 0 | 0
29.2334 | 53.2593 | 50.5071 | 68.5378 | 0 | 0 | 0
29.2375 | 53.9717 | 51.3388 | 68.8467 | 0 | 0 | 0
29.2417 | 54.6995 | 52.1807 | 69.1649 | 0 | 0 | 0
29.2459 | 54.5786 | 52.0967 | 69.0646 | 0 | 0 | 0
29.25 | 54.4601 | 52.0101 | 68.9548 | 0 | 0 | 0
29.2542 | 55.1969 | 52.8535 | 69.2693 | 0 | 0 | 0
29.2584 | 55.9446 | 53.7091 | 69.5943 | 0 | 0 | 0
29.2625 | 55.8439 | 53.6425 | 69.4887 | 0 | 0 | 0
29.2667 | 55.7395 | 53.576 | 69.3742 | 0 | 0 | 0
29.2709 | 56.4835 | 54.4607 | 69.6997 | 0 | 0 | 0
29.275 | 57.2431 | 55.3539 | 70.0329 | 0 | 0 | 0
29.2792 | 57.1531 | 55.2965 | 69.922 | 0 | 0 | 0
29.2834 | 57.0621 | 55.2387 | 69.8055 | 0 | 0 | 0
29.2875 | 57.8302 | 56.1466 | 70.1327 | 0 | 0 | 0
29.2917 | 58.6144 | 57.0661 | 70.4649 | 0 | 0 | 0
29.2959 | 58.555 | 57.0378 | 70.3641 | 0 | 0 | 0
29.3 | 58.4953 | 57.0085 | 70.2567 | 0 | 0 | 0
29.3042 | 59.2859 | 57.9196 | 70.5749 | 0 | 0 | 0
29.3084 | 60.0818 | 58.844 | 70.9021 | 0 | 0 | 0
29.3125 | 60.0392 | 58.8487 | 70.8116 | 0 | 0 | 0
29.3167 | 59.9955 | 58.8533 | 70.7149 | 0 | 0 | 0
29.3209 | 60.7963 | 59.7862 | 71.0304 | 0 | 0 | 0
29.325 | 61.6245 | 60.7333 | 71.3565 | 0 | 0 | 0
29.3292 | 61.6154 | 60.7781 | 71.2744 | 0 | 0 | 0
29.3334 | 61.5997 | 60.8265 | 71.1818 | 0 | 0 | 0
29.3375 | 62.4577 | 61.8037 | 71.5046 | 0 | 0 | 0
29.3417 | 63.3092 | 62.7954 | 71.839 | 0 | 0 | 0
29.3459 | 63.3127 | 62.8607 | 71.7553 | 0 | 0 | 0
29.35 | 63.3324 | 62.9302 | 71.6626 | 0 | 0 | 0
29.3542 | 64.1947 | 63.9476 | 71.9988 | 0 | 0 | 0
29.3584 | 65.0807 | 64.9796 | 72.3459 | 0 | 0 | 0
29.3625 | 65.1291 | 65.0619 | 72.2567 | 0 | 0 | 0
29.3667 | 65.1715 | 65.1475 | 72.1652 | 0 | 0 | 0
29.3709 | 66.0792 | 66.203 | 72.5134 | 0 | 0 | 0
29.375 | 67.0042 | 67.2769 | 72.8687 | 0 | 0 | 0
29.3792 | 67.0888 | 67.4161 | 72.7896 | 0 | 0 | 0
29.3834 | 67.1741 | 67.5589 | 72.7075 | 0 | 0 | 0
29.3875 | 68.1182 | 68.6576 | 73.0605 | 0 | 0 | 0
29.3917 | 69.0775 | 69.7736 | 73.4212 | 0 | 0 | 0
29.3959 | 69.197 | 69.976 | 73.3617 | 0 | 0 | 0
29.4 | 69.3207 | 70.1843 | 73.296 | 0 | 0 | 0
29.4042 | 70.3054 | 71.3083 | 73.6529 | 0 | 0 | 0
29.4084 | 71.3098 | 72.4473 | 74.0237 | 0 | 0 | 0
29.4125 | 71.4773 | 72.676 | 73.9784 | 0 | 0 | 0
29.4167 | 71.6458 | 72.9109 | 73.9247 | 0 | 0 | 0
29.4209 | 72.6787 | 74.0953 | 74.2946 | 0 | 0 | 0
29.425 | 73.7324 | 75.298 | 74.6781 | 0 | 0 | 0
29.4292 | 73.9466 | 75.5712 | 74.6428 | 0 | 0 | 0
29.4334 | 74.1722 | 75.8522 | 74.6066 | 0 | 0 | 0
29.4375 | 75.2595 | 77.106 | 75.0068 | 0 | 0 | 0
29.4417 | 76.3562 | 78.3782 | 75.4126 | 0 | 0 | 0
29.4459 | 76.622 | 78.7219 | 75.3844 | 0 | 0 | 0
29.45 | 76.8915 | 79.0727 | 75.3508 | 0 | 0 | 0
29.4542 | 78.02 | 80.4029 | 75.7518 | 0 | 0 | 0
29.4584 | 79.182 | 81.7653 | 76.1786 | 0 | 0 | 0
29.4625 | 79.5242 | 82.2247 | 76.1985 | 0 | 0 | 0
29.4667 | 79.8726 | 82.6974 | 76.2135 | 0 | 0 | 0
29.4709 | 81.0904 | 84.1041 | 76.6564 | 0 | 0 | 0
29.475 | 82.318 | 85.5266 | 77.0944 | 0 | 0 | 0
29.4792 | 82.7003 | 86.0314 | 77.0994 | 0 | 0 | 0
29.4834 | 83.0989 | 86.5535 | 77.1095 | 0 | 0 | 0
29.4875 | 84.3731 | 88.0127 | 77.5555 | 0 | 0 | 0
29.4917 | 85.6937 | 89.5077 | 78.0446 | 0 | 0 | 0
29.4959 | 86.1884 | 90.0947 | 78.1471 | 0 | 0 | 0
29.5 | 86.6872 | 90.6875 | 78.2379 | 0 | 0 | 0
29.5042 | 88.0496 | 92.23 | 78.7502 | 0 | 0 | 0
29.5084 | 89.4221 | 93.7832 | 79.2562 | 0 | 0 | 0
29.5125 | 89.9602 | 94.4092 | 79.3201 | 0 | 0 | 0
29.5167 | 90.5293 | 95.056 | 79.405 | 0 | 0 | 0
29.5209 | 91.9633 | 96.7009 | 79.9534 | 0 | 0 | 0
29.525 | 93.4434 | 98.3831 | 80.537 | 0 | 0 | 0
29.5292 | 94.1077 | 99.1526 | 80.7133 | 0 | 0 | 0
29.5334 | 94.7939 | 99.9401 | 80.8959 | 0 | 0 | 0
29.5375 | 96.3518 | 101.7131 | 81.5235 | 0 | 0 | 0
29.5417 | 97.9347 | 103.5173 | 82.1715 | 0 | 0 | 0
29.5459 | 98.6921 | 104.4252 | 82.4091 | 0 | 0 | 0
29.55 | 99.4502 | 105.3474 | 82.644 | 0 | 0 | 0
29.5542 | 101.0881 | 107.1928 | 83.3078 | 0 | 0 | 0
29.5584 | 102.753 | 109.0697 | 83.999 | 0 | 0 | 0
29.5625 | 103.4985 | 109.9413 | 84.2469 | 0 | 0 | 0
29.5667 | 104.2715 | 110.8428 | 84.5215 | 0 | 0 | 0
29.5709 | 106.3205 | 113.1243 | 85.4496 | 0 | 0 | 0
29.575 | 108.4088 | 115.4489 | 86.4232 | 0 | 0 | 0
29.5792 | 109.5162 | 116.6634 | 86.9222 | 0 | 0 | 0
29.5834 | 110.6309 | 117.896 | 87.4316 | 0 | 0 | 0
29.5875 | 112.1098 | 119.53 | 88.1233 | 0 | 0 | 0
29.5917 | 113.6059 | 121.182 | 88.833 | 0 | 0 | 0
29.5959 | 113.7732 | 121.3505 | 88.8668 | 0 | 0 | 0
29.6 | 113.9266 | 121.5117 | 88.8899 | 0 | 0 | 0
29.6042 | 114.5713 | 122.2266 | 89.1611 | 0 | 0 | 0
29.6084 | 115.2138 | 122.9429 | 89.4348 | 0 | 0 | 0
29.6125 | 114.788 | 122.4715 | 89.1573 | 0 | 0 | 0
29.6167 | 114.3641 | 121.9951 | 88.8825 | 0 | 0 | 0
29.6209 | 114.6716 | 122.3263 | 88.9877 | 0 | 0 | 0
29.625 | 114.9776 | 122.658 | 89.0979 | 0 | 0 | 0
29.6292 | 114.3603 | 121.9875 | 88.7446 | 0 | 0 | 0
29.6334 | 113.7231 | 121.2989 | 88.3723 | 0 | 0 | 0
29.6375 | 113.9008 | 121.4982 | 88.3966 | 0 | 0 | 0
29.6417 | 114.0677 | 121.6889 | 88.4147 | 0 | 0 | 0
29.6459 | 113.3658 | 120.9197 | 87.994 | 0 | 0 | 0
29.65 | 112.6246 | 120.1253 | 87.5423 | 0 | 0 | 0
29.6542 | 112.7243 | 120.2479 | 87.4856 | 0 | 0 | 0
29.6584 | 112.8131 | 120.3641 | 87.4281 | 0 | 0 | 0
29.6625 | 112.0683 | 119.549 | 86.945 | 0 | 0 | 0
29.6667 | 111.3147 | 118.7277 | 86.4563 | 0 | 0 | 0
29.6709 | 111.4211 | 118.8495 | 86.398 | 0 | 0 | 0
29.675 | 111.5513 | 118.9865 | 86.3623 | 0 | 0 | 0
29.6792 | 110.8525 | 118.2102 | 85.9127 | 0 | 0 | 0
29.6834 | 110.1661 | 117.4428 | 85.4722 | 0 | 0 | 0
29.6875 | 110.3523 | 117.6351 | 85.4828 | 0 | 0 | 0
29.6917 | 110.5532 | 117.8478 | 85.5177 | 0 | 0 | 0
29.6959 | 109.9211 | 117.1309 | 85.1372 | 0 | 0 | 0
29.7 | 109.2931 | 116.4146 | 84.7607 | 0 | 0 | 0
29.7042 | 109.5156 | 116.6544 | 84.8189 | 0 | 0 | 0
29.7084 | 109.7423 | 116.8988 | 84.8777 | 0 | 0 | 0
29.7125 | 109.1262 | 116.2096 | 84.5134 | 0 | 0 | 0
29.7167 | 108.4926 | 115.5106 | 84.1416 | 0 | 0 | 0
29.7209 | 108.7036 | 115.7343 | 84.1848 | 0 | 0 | 0
29.725 | 108.9076 | 115.9551 | 84.2331 | 0 | 0 | 0
29.7292 | 108.2634 | 115.245 | 83.8651 | 0 | 0 | 0
29.7334 | 107.6005 | 114.5212 | 83.4798 | 0 | 0 | 0
29.7375 | 107.7742 | 114.7111 | 83.4924 | 0 | 0 | 0
29.7417 | 107.9504 | 114.9055 | 83.5162 | 0 | 0 | 0
29.7459 | 107.3047 | 114.1758 | 83.1413 | 0 | 0 | 0
29.75 | 106.6402 | 113.4366 | 82.7562 | 0 | 0 | 0
29.7542 | 106.8068 | 113.6078 | 82.7738 | 0 | 0 | 0
29.7584 | 106.9856 | 113.7869 | 82.8085 | 0 | 0 | 0
29.7625 | 106.3448 | 113.0751 | 82.4451 | 0 | 0 | 0
29.7667 | 105.7102 | 112.3614 | 82.0783 | 0 | 0 | 0
29.7709 | 105.9138 | 112.5807 | 82.1318 | 0 | 0 | 0
29.775 | 106.1223 | 112.8047 | 82.1859 | 0 | 0 | 0
29.7792 | 105.4982 | 112.0882 | 81.8162 | 0 | 0 | 0
29.7834 | 104.8732 | 111.3686 | 81.4498 | 0 | 0 | 0
29.7875 | 105.0897 | 111.6054 | 81.5091 | 0 | 0 | 0
29.7917 | 105.3139 | 111.8482 | 81.5747 | 0 | 0 | 0
29.7959 | 104.6997 | 111.1718 | 81.2326 | 0 | 0 | 0
29.8 | 104.0789 | 110.4872 | 80.878 | 0 | 0 | 0
29.8042 | 104.3058 | 110.7195 | 80.9398 | 0 | 0 | 0
29.8084 | 104.5468 | 110.9593 | 81.0213 | 0 | 0 | 0
29.8125 | 103.9283 | 110.2514 | 80.6696 | 0 | 0 | 0
29.8167 | 103.2901 | 109.535 | 80.3071 | 0 | 0 | 0
29.8209 | 103.5134 | 109.7769 | 80.3817 | 0 | 0 | 0
29.825 | 103.7386 | 110.0244 | 80.4616 | 0 | 0 | 0
29.8292 | 103.1136 | 109.3488 | 80.1147 | 0 | 0 | 0
29.8334 | 102.4849 | 108.668 | 79.7611 | 0 | 0 | 0
29.8375 | 102.7249 | 108.9021 | 79.8478 | 0 | 0 | 0
29.8417 | 102.9673 | 109.1398 | 79.9476 | 0 | 0 | 0
29.8459 | 102.3392 | 108.401 | 79.5909 | 0 | 0 | 0
29.85 | 101.7048 | 107.6564 | 79.2362 | 0 | 0 | 0
29.8542 | 101.9262 | 107.9067 | 79.3388 | 0 | 0 | 0
29.8584 | 102.1508 | 108.1631 | 79.4442 | 0 | 0 | 0
29.8625 | 101.5232 | 107.4748 | 79.1225 | 0 | 0 | 0
29.8667 | 100.8911 | 106.7787 | 78.7908 | 0 | 0 | 0
29.8709 | 101.116 | 106.9807 | 78.8732 | 0 | 0 | 0
29.875 | 101.3434 | 107.1886 | 78.9715 | 0 | 0 | 0
29.8792 | 100.7296 | 106.4636 | 78.6539 | 0 | 0 | 0
29.8834 | 100.1057 | 105.7325 | 78.3319 | 0 | 0 | 0
29.8875 | 100.3069 | 105.9429 | 78.4242 | 0 | 0 | 0
29.8917 | 100.518 | 106.1583 | 78.5245 | 0 | 0 | 0
29.8959 | 99.8955 | 105.4676 | 78.226 | 0 | 0 | 0
29.9 | 99.2639 | 104.7701 | 77.9198 | 0 | 0 | 0
29.9042 | 99.4753 | 104.9743 | 78.0223 | 0 | 0 | 0
29.9084 | 99.6943 | 105.1834 | 78.1386 | 0 | 0 | 0
29.9125 | 99.0753 | 104.4586 | 77.8355 | 0 | 0 | 0
29.9167 | 98.4447 | 103.7262 | 77.5251 | 0 | 0 | 0
29.9209 | 98.6569 | 103.9319 | 77.637 | 0 | 0 | 0
29.925 | 98.875 | 104.1425 | 77.7556 | 0 | 0 | 0
29.9292 | 98.2411 | 103.4115 | 77.4387 | 0 | 0 | 0
29.9334 | 97.5934 | 102.6727 | 77.1116 | 0 | 0 | 0
29.9375 | 97.8046 | 102.9017 | 77.23 | 0 | 0 | 0
29.9417 | 98.0196 | 103.1351 | 77.3488 | 0 | 0 | 0
29.9459 | 97.3745 | 102.4035 | 77.023 | 0 | 0 | 0
29.95 | 96.726 | 101.6648 | 76.6922 | 0 | 0 | 0
29.9542 | 96.9445 | 101.8571 | 76.7972 | 0 | 0 | 0
29.9584 | 97.1698 | 102.0539 | 76.9141 | 0 | 0 | 0
29.9625 | 96.5312 | 101.3196 | 76.5989 | 0 | 0 | 0
29.9667 | 95.8824 | 100.5762 | 76.2736 | 0 | 0 | 0
29.9709 | 96.0795 | 100.7747 | 76.3783 | 0 | 0 | 0
29.975 | 96.2778 | 100.9787 | 76.4928 | 0 | 0 | 0
29.9792 | 95.6351 | 100.246 | 76.1917 | 0 | 0 | 0
29.9834 | 94.9868 | 99.5065 | 75.8813 | 0 | 0 | 0
29.9875 | 95.1822 | 99.6806 | 75.9817 | 0 | 0 | 0
29.9917 | 95.3813 | 99.8582 | 76.0915 | 0 | 0 | 0
29.9959 | 94.7322 | 99.1085 | 75.7878 | 0 | 0 | 0
1
2
3

## ESD Exit Transient (Ns = 0.79)
Transient conditions immediately downstream of ESD
| Pressure (m H2O std) |  |  | Velocity (m/s)
Time (s) | MC | 4QBEP | 4QOP | MC | 4QBEP | 4QOP | Event Times
0 | 88.425 | 88.8968 | 88.425 | 1.1422 | 1.2183 | 1.1422 | 10 | -10
0.0041667 | 88.4262 | 88.8982 | 88.4262 | 1.1422 | 1.2184 | 1.1422 | 10 | 200
0.0083333 | 88.4262 | 88.8982 | 88.4262 | 1.1422 | 1.2184 | 1.1422
0.0125 | 88.1521 | 88.6212 | 88.1532 | 1.1444 | 1.2206 | 1.1444 | 20 | -10
0.016667 | 87.8933 | 88.3585 | 87.8942 | 1.1465 | 1.2228 | 1.1465 | 20 | 200
0.020833 | 87.7031 | 88.178 | 87.6889 | 1.1476 | 1.224 | 1.1475
0.025 | 87.5398 | 88.001 | 87.4889 | 1.1489 | 1.2252 | 1.1485 | 27 | -10
0.029167 | 87.604 | 88.055 | 87.4915 | 1.1523 | 1.2286 | 1.1512 | 27 | 200
0.033333 | 87.679 | 88.103 | 87.4827 | 1.1557 | 1.2318 | 1.1538
0.0375 | 87.5784 | 87.9745 | 87.3073 | 1.159 | 1.2348 | 1.1562
0.041667 | 87.4853 | 87.8536 | 87.1418 | 1.1622 | 1.2377 | 1.1585 | Atmosphere
0.045833 | 87.5339 | 87.8815 | 87.1058 | 1.1644 | 1.2397 | 1.1599 | 0 | 10.3326
0.05 | 87.5842 | 87.9011 | 87.0626 | 1.1667 | 1.2417 | 1.1614 | 30 | 10.3326
0.054167 | 87.6565 | 87.9346 | 87.037 | 1.17 | 1.2448 | 1.1638
0.058333 | 87.7209 | 87.9664 | 87.0056 | 1.1732 | 1.2477 | 1.1661
0.0625 | 87.6601 | 87.8788 | 86.8766 | 1.1754 | 1.2497 | 1.1675
0.066667 | 87.6025 | 87.7987 | 86.7644 | 1.1776 | 1.2516 | 1.169
0.070833 | 87.6644 | 87.8396 | 86.7544 | 1.1796 | 1.2535 | 1.1705
0.075 | 87.724 | 87.8729 | 86.7339 | 1.1817 | 1.2554 | 1.1719
0.079167 | 87.7269 | 87.848 | 86.6699 | 1.1842 | 1.2578 | 1.1737
0.083333 | 87.7284 | 87.8279 | 86.6114 | 1.1867 | 1.26 | 1.1754
0.0875 | 87.6964 | 87.7802 | 86.5325 | 1.1884 | 1.2615 | 1.1765
0.091667 | 87.666 | 87.7356 | 86.463 | 1.1901 | 1.2631 | 1.1777
0.095833 | 87.7125 | 87.7615 | 86.4481 | 1.1921 | 1.2649 | 1.1791
0.1 | 87.7535 | 87.7822 | 86.4238 | 1.194 | 1.2667 | 1.1805
0.10417 | 87.738 | 87.7461 | 86.3591 | 1.196 | 1.2685 | 1.1818
0.10833 | 87.722 | 87.7153 | 86.3031 | 1.1979 | 1.2703 | 1.1831
0.1125 | 87.7178 | 87.6987 | 86.258 | 1.1995 | 1.2717 | 1.1841
0.11667 | 87.7145 | 87.6813 | 86.2148 | 1.201 | 1.2731 | 1.1851
0.12083 | 87.7402 | 87.6892 | 86.1901 | 1.2028 | 1.2747 | 1.1863
0.125 | 87.7634 | 87.6951 | 86.1608 | 1.2045 | 1.2763 | 1.1874
0.12917 | 87.7493 | 87.6665 | 86.1098 | 1.2061 | 1.2777 | 1.1885
0.13333 | 87.7366 | 87.6417 | 86.0658 | 1.2077 | 1.2791 | 1.1895
0.1375 | 87.7437 | 87.637 | 86.0357 | 1.2091 | 1.2804 | 1.1904
0.14167 | 87.7503 | 87.6307 | 86.0045 | 1.2105 | 1.2816 | 1.1913
0.14583 | 87.7624 | 87.6271 | 85.9759 | 1.212 | 1.283 | 1.1922
0.15 | 87.7713 | 87.6236 | 85.9467 | 1.2135 | 1.2843 | 1.1932
0.15417 | 87.7646 | 87.6053 | 85.9095 | 1.2148 | 1.2855 | 1.194
0.15833 | 87.7576 | 87.5887 | 85.8764 | 1.2161 | 1.2867 | 1.1948
0.1625 | 87.766 | 87.586 | 85.8522 | 1.2174 | 1.2878 | 1.1956
0.16667 | 87.7724 | 87.5822 | 85.8268 | 1.2186 | 1.2889 | 1.1964
0.17083 | 87.7782 | 87.5746 | 85.7999 | 1.2199 | 1.2901 | 1.1971
0.175 | 87.781 | 87.5678 | 85.774 | 1.2211 | 1.2912 | 1.1979
0.17917 | 87.7799 | 87.5565 | 85.7466 | 1.2223 | 1.2922 | 1.1986
0.18333 | 87.7776 | 87.546 | 85.7212 | 1.2234 | 1.2932 | 1.1993
0.1875 | 87.7833 | 87.5425 | 85.7 | 1.2245 | 1.2942 | 1.1999
0.19167 | 87.7891 | 87.5385 | 85.6783 | 1.2256 | 1.2951 | 1.2006
0.19583 | 87.7907 | 87.531 | 85.6555 | 1.2266 | 1.2961 | 1.2012
0.2 | 87.7933 | 87.524 | 85.6337 | 1.2277 | 1.297 | 1.2018
0.20417 | 87.7931 | 87.5167 | 85.6125 | 1.2287 | 1.2979 | 1.2024
0.20833 | 87.794 | 87.5096 | 85.5922 | 1.2296 | 1.2987 | 1.203
0.2125 | 87.7964 | 87.5054 | 85.5736 | 1.2306 | 1.2996 | 1.2035
0.21667 | 87.8005 | 87.5011 | 85.5552 | 1.2315 | 1.3004 | 1.2041
0.22083 | 87.801 | 87.4947 | 85.5363 | 1.2324 | 1.3012 | 1.2046
0.225 | 87.8027 | 87.4887 | 85.5183 | 1.2333 | 1.302 | 1.2051
0.22917 | 87.8046 | 87.4833 | 85.5011 | 1.2341 | 1.3027 | 1.2056
0.23333 | 87.805 | 87.478 | 85.4844 | 1.235 | 1.3034 | 1.206
0.2375 | 87.8078 | 87.4737 | 85.4685 | 1.2358 | 1.3042 | 1.2065
0.24167 | 87.8104 | 87.4695 | 85.4529 | 1.2366 | 1.3049 | 1.207
0.24583 | 87.8107 | 87.4643 | 85.4374 | 1.2374 | 1.3055 | 1.2074
0.25 | 87.813 | 87.4594 | 85.4224 | 1.2381 | 1.3062 | 1.2078
0.25417 | 87.8134 | 87.455 | 85.4081 | 1.2389 | 1.3068 | 1.2082
0.25833 | 87.8146 | 87.4507 | 85.3941 | 1.2396 | 1.3075 | 1.2086
0.2625 | 87.8168 | 87.4467 | 85.3806 | 1.2403 | 1.3081 | 1.209
0.26667 | 87.8177 | 87.4428 | 85.3675 | 1.241 | 1.3087 | 1.2094
0.27083 | 87.8194 | 87.4385 | 85.3545 | 1.2416 | 1.3093 | 1.2097
0.275 | 87.8194 | 87.4345 | 85.342 | 1.2423 | 1.3098 | 1.2101
0.27917 | 87.8204 | 87.4307 | 85.33 | 1.2429 | 1.3104 | 1.2104
0.28333 | 87.8222 | 87.4271 | 85.3182 | 1.2435 | 1.3109 | 1.2108
0.2875 | 87.8225 | 87.4235 | 85.3068 | 1.2441 | 1.3115 | 1.2111
0.29167 | 87.8244 | 87.42 | 85.2956 | 1.2447 | 1.312 | 1.2114
0.29583 | 87.8256 | 87.4165 | 85.2848 | 1.2453 | 1.3125 | 1.2117
0.3 | 87.8252 | 87.413 | 85.2742 | 1.2459 | 1.313 | 1.212
0.30417 | 87.827 | 87.4097 | 85.264 | 1.2464 | 1.3134 | 1.2123
0.30833 | 87.8283 | 87.4066 | 85.254 | 1.2469 | 1.3139 | 1.2126
0.3125 | 87.8278 | 87.4034 | 85.2443 | 1.2475 | 1.3144 | 1.2129
0.31667 | 87.8297 | 87.4004 | 85.2349 | 1.248 | 1.3148 | 1.2132
0.32083 | 87.8309 | 87.3974 | 85.2257 | 1.2485 | 1.3152 | 1.2134
0.325 | 87.8301 | 87.3944 | 85.2167 | 1.249 | 1.3156 | 1.2137
0.32917 | 87.8317 | 87.3916 | 85.208 | 1.2494 | 1.3161 | 1.2139
0.33333 | 87.833 | 87.3888 | 85.1995 | 1.2499 | 1.3165 | 1.2142
0.3375 | 87.8321 | 87.386 | 85.1912 | 1.2504 | 1.3169 | 1.2144
0.34167 | 87.8336 | 87.3833 | 85.1831 | 1.2508 | 1.3172 | 1.2146
0.34583 | 87.8348 | 87.3807 | 85.1753 | 1.2512 | 1.3176 | 1.2148
0.35 | 87.8338 | 87.3781 | 85.1676 | 1.2516 | 1.318 | 1.2151
0.35417 | 87.8365 | 87.3757 | 85.1601 | 1.2521 | 1.3183 | 1.2153
0.35833 | 87.8367 | 87.3732 | 85.1528 | 1.2525 | 1.3187 | 1.2155
0.3625 | 87.8371 | 87.3708 | 85.1457 | 1.2529 | 1.319 | 1.2157
0.36667 | 87.8373 | 87.3685 | 85.1388 | 1.2533 | 1.3193 | 1.2159
0.37083 | 87.8375 | 87.3662 | 85.1321 | 1.2536 | 1.3197 | 1.2161
0.375 | 87.8381 | 87.3639 | 85.1255 | 1.254 | 1.32 | 1.2163
0.37917 | 87.8392 | 87.3617 | 85.119 | 1.2544 | 1.3203 | 1.2164
0.38333 | 87.8394 | 87.3596 | 85.1127 | 1.2547 | 1.3206 | 1.2166
0.3875 | 87.84 | 87.3574 | 85.1066 | 1.2551 | 1.3209 | 1.2168
0.39167 | 87.8388 | 87.3553 | 85.1006 | 1.2554 | 1.3212 | 1.2169
0.39583 | 87.8402 | 87.3533 | 85.0948 | 1.2557 | 1.3215 | 1.2171
0.4 | 87.8404 | 87.3513 | 85.0891 | 1.256 | 1.3217 | 1.2173
0.40417 | 87.841 | 87.3494 | 85.0835 | 1.2564 | 1.322 | 1.2174
0.40833 | 87.8408 | 87.3475 | 85.0781 | 1.2567 | 1.3223 | 1.2176
0.4125 | 87.8418 | 87.3456 | 85.0728 | 1.257 | 1.3225 | 1.2177
0.41667 | 87.8413 | 87.3438 | 85.0676 | 1.2573 | 1.3228 | 1.2179
0.42083 | 87.8419 | 87.342 | 85.0625 | 1.2576 | 1.323 | 1.218
0.425 | 87.8431 | 87.3402 | 85.0575 | 1.2578 | 1.3233 | 1.2182
0.42917 | 87.8418 | 87.3385 | 85.0527 | 1.2581 | 1.3235 | 1.2183
0.43333 | 87.8422 | 87.3368 | 85.0481 | 1.2584 | 1.3237 | 1.2184
0.4375 | 87.843 | 87.3351 | 85.0434 | 1.2586 | 1.324 | 1.2186
0.44167 | 87.8431 | 87.3335 | 85.0389 | 1.2589 | 1.3242 | 1.2187
0.44583 | 87.8427 | 87.3319 | 85.0345 | 1.2592 | 1.3244 | 1.2188
0.45 | 87.8447 | 87.3303 | 85.0301 | 1.2594 | 1.3246 | 1.2189
0.45417 | 87.8439 | 87.3288 | 85.0258 | 1.2596 | 1.3248 | 1.219
0.45833 | 87.8437 | 87.3272 | 85.0217 | 1.2599 | 1.325 | 1.2192
0.4625 | 87.845 | 87.3257 | 85.0177 | 1.2601 | 1.3252 | 1.2193
0.46667 | 87.8437 | 87.3243 | 85.0137 | 1.2603 | 1.3254 | 1.2194
0.47083 | 87.8436 | 87.3229 | 85.0098 | 1.2606 | 1.3256 | 1.2195
0.475 | 87.8443 | 87.3214 | 85.006 | 1.2608 | 1.3258 | 1.2196
0.47917 | 87.8444 | 87.3201 | 85.0022 | 1.261 | 1.326 | 1.2197
0.48333 | 87.8452 | 87.3187 | 84.9986 | 1.2612 | 1.3262 | 1.2198
0.4875 | 87.8461 | 87.3174 | 84.995 | 1.2614 | 1.3263 | 1.2199
0.49167 | 87.8452 | 87.3161 | 84.9915 | 1.2616 | 1.3265 | 1.22
0.49583 | 87.8449 | 87.3148 | 84.9881 | 1.2618 | 1.3267 | 1.2201
0.5 | 87.845 | 87.3135 | 84.9847 | 1.262 | 1.3268 | 1.2202
0.50417 | 87.8452 | 87.3123 | 84.9815 | 1.2622 | 1.327 | 1.2203
0.50833 | 87.8463 | 87.311 | 84.9782 | 1.2624 | 1.3272 | 1.2204
0.5125 | 87.8457 | 87.3098 | 84.9751 | 1.2626 | 1.3273 | 1.2205
0.51667 | 87.8453 | 87.3086 | 84.972 | 1.2628 | 1.3275 | 1.2205
0.52083 | 87.8452 | 87.3075 | 84.9689 | 1.2629 | 1.3276 | 1.2206
0.525 | 87.8452 | 87.3064 | 84.966 | 1.2631 | 1.3278 | 1.2207
0.52917 | 87.8461 | 87.3053 | 84.9631 | 1.2633 | 1.3279 | 1.2208
0.53333 | 87.8469 | 87.3041 | 84.9602 | 1.2635 | 1.328 | 1.2209
0.5375 | 87.8458 | 87.3031 | 84.9574 | 1.2636 | 1.3282 | 1.2209
0.54167 | 87.8468 | 87.302 | 84.9547 | 1.2638 | 1.3283 | 1.221
0.54583 | 87.8461 | 87.301 | 84.952 | 1.2639 | 1.3285 | 1.2211
0.55 | 87.8458 | 87.2999 | 84.9493 | 1.2641 | 1.3286 | 1.2212
0.55417 | 87.8467 | 87.2989 | 84.9467 | 1.2642 | 1.3287 | 1.2212
0.55833 | 87.8467 | 87.2979 | 84.9442 | 1.2644 | 1.3288 | 1.2213
0.5625 | 87.8456 | 87.2969 | 84.9417 | 1.2645 | 1.329 | 1.2214
0.56667 | 87.8471 | 87.296 | 84.9392 | 1.2647 | 1.3291 | 1.2214
0.57083 | 87.8463 | 87.295 | 84.9368 | 1.2648 | 1.3292 | 1.2215
0.575 | 87.8457 | 87.2941 | 84.9345 | 1.265 | 1.3293 | 1.2216
0.57917 | 87.8464 | 87.2932 | 84.9321 | 1.2651 | 1.3294 | 1.2216
0.58333 | 87.8463 | 87.2923 | 84.9298 | 1.2652 | 1.3295 | 1.2217
0.5875 | 87.845 | 87.2914 | 84.9276 | 1.2653 | 1.3297 | 1.2218
0.59167 | 87.8463 | 87.2905 | 84.9254 | 1.2655 | 1.3298 | 1.2218
0.59583 | 87.8455 | 87.2896 | 84.9232 | 1.2656 | 1.3299 | 1.2219
0.6 | 87.8463 | 87.2888 | 84.9211 | 1.2657 | 1.33 | 1.2219
0.60417 | 87.8463 | 87.2879 | 84.9191 | 1.2658 | 1.3301 | 1.222
0.60833 | 87.8472 | 87.2871 | 84.917 | 1.266 | 1.3302 | 1.222
0.6125 | 87.8456 | 87.2863 | 84.915 | 1.2661 | 1.3303 | 1.2221
0.61667 | 87.847 | 87.2855 | 84.913 | 1.2662 | 1.3304 | 1.2222
0.62083 | 87.8458 | 87.2847 | 84.9111 | 1.2663 | 1.3305 | 1.2222
0.625 | 87.8458 | 87.284 | 84.9092 | 1.2664 | 1.3306 | 1.2223
0.62917 | 87.8459 | 87.2832 | 84.9073 | 1.2665 | 1.3307 | 1.2223
0.63333 | 87.8462 | 87.2825 | 84.9055 | 1.2666 | 1.3307 | 1.2224
0.6375 | 87.8459 | 87.2817 | 84.9036 | 1.2667 | 1.3308 | 1.2224
0.64167 | 87.847 | 87.281 | 84.9019 | 1.2669 | 1.3309 | 1.2225
0.64583 | 87.8467 | 87.2803 | 84.9001 | 1.267 | 1.331 | 1.2225
0.65 | 87.846 | 87.2796 | 84.8984 | 1.2671 | 1.3311 | 1.2226
0.65417 | 87.8462 | 87.2789 | 84.8967 | 1.2672 | 1.3312 | 1.2226
0.65833 | 87.8461 | 87.2782 | 84.895 | 1.2673 | 1.3313 | 1.2226
0.6625 | 87.8464 | 87.2775 | 84.8934 | 1.2674 | 1.3313 | 1.2227
0.66667 | 87.847 | 87.2768 | 84.8918 | 1.2675 | 1.3314 | 1.2227
0.67083 | 87.8458 | 87.2762 | 84.8902 | 1.2675 | 1.3315 | 1.2228
0.675 | 87.8466 | 87.2755 | 84.8886 | 1.2676 | 1.3316 | 1.2228
0.67917 | 87.8458 | 87.2749 | 84.8871 | 1.2677 | 1.3317 | 1.2229
0.68333 | 87.8465 | 87.2743 | 84.8856 | 1.2678 | 1.3317 | 1.2229
0.6875 | 87.8466 | 87.2737 | 84.8841 | 1.2679 | 1.3318 | 1.2229
0.69167 | 87.8459 | 87.2731 | 84.8827 | 1.268 | 1.3319 | 1.223
0.69583 | 87.846 | 87.2724 | 84.8812 | 1.2681 | 1.3319 | 1.223
0.7 | 87.8457 | 87.2719 | 84.8798 | 1.2681 | 1.332 | 1.2231
0.70417 | 87.8459 | 87.2713 | 84.8784 | 1.2682 | 1.3321 | 1.2231
0.70833 | 87.8464 | 87.2707 | 84.877 | 1.2683 | 1.3321 | 1.2231
0.7125 | 87.8465 | 87.2701 | 84.8757 | 1.2684 | 1.3322 | 1.2232
0.71667 | 87.8453 | 87.2696 | 84.8744 | 1.2685 | 1.3323 | 1.2232
0.72083 | 87.8459 | 87.269 | 84.873 | 1.2685 | 1.3323 | 1.2232
0.725 | 87.8451 | 87.2685 | 84.8717 | 1.2686 | 1.3324 | 1.2233
0.72917 | 87.8457 | 87.2679 | 84.8705 | 1.2687 | 1.3325 | 1.2233
0.73333 | 87.8457 | 87.2674 | 84.8692 | 1.2688 | 1.3325 | 1.2233
0.7375 | 87.8464 | 87.2669 | 84.868 | 1.2688 | 1.3326 | 1.2234
0.74167 | 87.8447 | 87.2663 | 84.8668 | 1.2689 | 1.3327 | 1.2234
0.74583 | 87.8457 | 87.2658 | 84.8656 | 1.269 | 1.3327 | 1.2234
0.75 | 87.8444 | 87.2653 | 84.8644 | 1.269 | 1.3328 | 1.2235
0.75417 | 87.8454 | 87.2648 | 84.8632 | 1.2691 | 1.3328 | 1.2235
0.75833 | 87.8449 | 87.2643 | 84.8621 | 1.2692 | 1.3329 | 1.2235
0.7625 | 87.846 | 87.2639 | 84.861 | 1.2692 | 1.3329 | 1.2236
0.76667 | 87.8452 | 87.2634 | 84.8598 | 1.2693 | 1.333 | 1.2236
0.77083 | 87.8448 | 87.2629 | 84.8587 | 1.2694 | 1.333 | 1.2236
0.775 | 87.8443 | 87.2625 | 84.8577 | 1.2694 | 1.3331 | 1.2236
0.77917 | 87.8445 | 87.262 | 84.8566 | 1.2695 | 1.3332 | 1.2237
0.78333 | 87.844 | 87.2616 | 84.8555 | 1.2695 | 1.3332 | 1.2237
0.7875 | 87.8449 | 87.2611 | 84.8545 | 1.2696 | 1.3333 | 1.2237
0.79167 | 87.8446 | 87.2607 | 84.8535 | 1.2697 | 1.3333 | 1.2238
0.79583 | 87.8436 | 87.2602 | 84.8525 | 1.2697 | 1.3334 | 1.2238
0.8 | 87.8435 | 87.2598 | 84.8515 | 1.2698 | 1.3334 | 1.2238
0.80417 | 87.8445 | 87.2594 | 84.8505 | 1.2698 | 1.3334 | 1.2238
0.80833 | 87.8442 | 87.259 | 84.8495 | 1.2699 | 1.3335 | 1.2239
0.8125 | 87.8456 | 87.2586 | 84.8486 | 1.27 | 1.3335 | 1.2239
0.81667 | 87.8453 | 87.2581 | 84.8476 | 1.27 | 1.3336 | 1.2239
0.82083 | 87.8443 | 87.2577 | 84.8467 | 1.2701 | 1.3336 | 1.2239
0.825 | 87.8444 | 87.2573 | 84.8458 | 1.2701 | 1.3337 | 1.224
0.82917 | 87.8441 | 87.257 | 84.8449 | 1.2702 | 1.3337 | 1.224
0.83333 | 87.8443 | 87.2566 | 84.844 | 1.2702 | 1.3338 | 1.224
0.8375 | 87.8447 | 87.2562 | 84.8431 | 1.2703 | 1.3338 | 1.224
0.84167 | 87.8449 | 87.2558 | 84.8423 | 1.2703 | 1.3338 | 1.2241
0.84583 | 87.8436 | 87.2554 | 84.8414 | 1.2704 | 1.3339 | 1.2241
0.85 | 87.844 | 87.255 | 84.8406 | 1.2704 | 1.3339 | 1.2241
0.85417 | 87.5815 | 86.9891 | 84.5764 | 1.2726 | 1.3361 | 1.2263
0.85833 | 87.3336 | 86.7364 | 84.3256 | 1.2747 | 1.3382 | 1.2283
0.8625 | 87.262 | 86.6536 | 84.2177 | 1.2752 | 1.3387 | 1.2286
0.86667 | 87.1903 | 86.5723 | 84.1123 | 1.2758 | 1.3393 | 1.2289
0.87083 | 87.3275 | 86.6939 | 84.1896 | 1.2788 | 1.3422 | 1.2313
0.875 | 87.4567 | 86.8111 | 84.2623 | 1.2817 | 1.3449 | 1.2336
0.87917 | 87.3523 | 86.6906 | 84.1343 | 1.2835 | 1.3467 | 1.2348
0.88333 | 87.2446 | 86.5764 | 84.0154 | 1.2854 | 1.3485 | 1.2359
0.8875 | 87.1318 | 86.4518 | 83.9022 | 1.2881 | 1.351 | 1.2378
0.89167 | 87.003 | 86.3293 | 83.7947 | 1.2909 | 1.3535 | 1.2395
0.89583 | 86.9049 | 86.2343 | 83.6888 | 1.2942 | 1.3565 | 1.2415
0.9 | 86.818 | 86.1493 | 83.5904 | 1.2975 | 1.3595 | 1.2434
0.90417 | 86.7874 | 86.1184 | 83.5368 | 1.3011 | 1.3627 | 1.2452
0.90833 | 86.7701 | 86.0908 | 83.4839 | 1.3048 | 1.3659 | 1.247
0.9125 | 86.7029 | 86.0117 | 83.3866 | 1.3091 | 1.3696 | 1.2494
0.91667 | 86.6339 | 85.9337 | 83.2937 | 1.3134 | 1.3733 | 1.2515
0.92083 | 86.6084 | 85.8986 | 83.2229 | 1.3172 | 1.3764 | 1.2532
0.925 | 86.5924 | 85.8675 | 83.1533 | 1.3208 | 1.3794 | 1.2548
0.92917 | 86.6374 | 85.8907 | 83.1313 | 1.325 | 1.383 | 1.2568
0.93333 | 86.6804 | 85.9132 | 83.1049 | 1.3292 | 1.3865 | 1.2587
0.9375 | 86.6367 | 85.8505 | 83.0133 | 1.3332 | 1.3898 | 1.2605
0.94167 | 86.591 | 85.7897 | 82.9304 | 1.3371 | 1.393 | 1.2622
0.94583 | 86.6077 | 85.7976 | 82.8939 | 1.3405 | 1.3959 | 1.2636
0.95 | 86.6314 | 85.8036 | 82.8542 | 1.3438 | 1.3987 | 1.265
0.95417 | 86.6578 | 85.8159 | 82.8202 | 1.3477 | 1.402 | 1.2668
0.95833 | 86.683 | 85.8284 | 82.7863 | 1.3514 | 1.4052 | 1.2684
0.9625 | 86.6474 | 85.7836 | 82.7139 | 1.3547 | 1.4079 | 1.2698
0.96667 | 86.6116 | 85.7421 | 82.6493 | 1.3579 | 1.4107 | 1.2711
0.97083 | 86.6421 | 85.7633 | 82.628 | 1.361 | 1.4133 | 1.2725
0.975 | 86.6708 | 85.7811 | 82.6016 | 1.364 | 1.4159 | 1.2737
0.97917 | 86.6753 | 85.7745 | 82.5588 | 1.3673 | 1.4187 | 1.2752
0.98333 | 86.6786 | 85.7698 | 82.5197 | 1.3705 | 1.4215 | 1.2765
0.9875 | 86.6587 | 85.747 | 82.471 | 1.3733 | 1.4238 | 1.2776
0.99167 | 86.6428 | 85.7256 | 82.4259 | 1.376 | 1.4261 | 1.2787
0.99583 | 86.6672 | 85.7433 | 82.4062 | 1.3788 | 1.4286 | 1.2799
1 | 86.6919 | 85.7582 | 82.3825 | 1.3815 | 1.4309 | 1.2811
1.0042 | 86.6843 | 85.7447 | 82.3415 | 1.3842 | 1.4333 | 1.2822
1.0083 | 86.6797 | 85.7337 | 82.3052 | 1.3869 | 1.4355 | 1.2833
1.0125 | 86.6742 | 85.7259 | 82.2727 | 1.3893 | 1.4376 | 1.2842
1.0167 | 86.6707 | 85.7179 | 82.2408 | 1.3917 | 1.4396 | 1.2852
1.0208 | 86.6864 | 85.7268 | 82.2189 | 1.3941 | 1.4417 | 1.2862
1.025 | 86.7014 | 85.7343 | 82.1955 | 1.3965 | 1.4438 | 1.2872
1.0292 | 86.6933 | 85.7223 | 82.1617 | 1.3988 | 1.4458 | 1.2881
1.0333 | 86.6871 | 85.7121 | 82.1314 | 1.4011 | 1.4477 | 1.289
1.0375 | 86.6879 | 85.7111 | 82.1076 | 1.4032 | 1.4495 | 1.2898
1.0417 | 86.6904 | 85.7094 | 82.0831 | 1.4053 | 1.4513 | 1.2907
1.0458 | 86.6974 | 85.7117 | 82.061 | 1.4074 | 1.4531 | 1.2915
1.05 | 86.7056 | 85.7137 | 82.039 | 1.4095 | 1.4549 | 1.2923
1.0542 | 86.7008 | 85.7056 | 82.0126 | 1.4114 | 1.4566 | 1.2931
1.0583 | 86.6959 | 85.6986 | 81.9883 | 1.4134 | 1.4582 | 1.2939
1.0625 | 86.6985 | 85.6991 | 81.9686 | 1.4152 | 1.4598 | 1.2946
1.0667 | 86.702 | 85.699 | 81.9484 | 1.417 | 1.4614 | 1.2953
1.0708 | 86.7048 | 85.6981 | 81.9281 | 1.4188 | 1.4629 | 1.296
1.075 | 86.7083 | 85.6973 | 81.9084 | 1.4206 | 1.4644 | 1.2967
1.0792 | 86.7066 | 85.6925 | 81.8876 | 1.4223 | 1.4659 | 1.2973
1.0833 | 86.7044 | 85.6882 | 81.8679 | 1.424 | 1.4673 | 1.298
1.0875 | 86.7064 | 85.6883 | 81.8508 | 1.4256 | 1.4687 | 1.2986
1.0917 | 86.7102 | 85.6881 | 81.8335 | 1.4272 | 1.47 | 1.2992
1.0958 | 86.71 | 85.6861 | 81.8158 | 1.4288 | 1.4714 | 1.2998
1.1 | 86.7121 | 85.6843 | 81.7987 | 1.4303 | 1.4727 | 1.3004
1.1042 | 86.7109 | 85.6815 | 81.7818 | 1.4318 | 1.4739 | 1.3009
1.1083 | 86.7093 | 85.6788 | 81.7655 | 1.4332 | 1.4752 | 1.3015
1.1125 | 86.7052 | 85.6728 | 81.7465 | 1.4347 | 1.4764 | 1.3021
1.1167 | 86.7014 | 85.6668 | 81.7277 | 1.4361 | 1.4776 | 1.3026
1.1208 | 86.6955 | 85.6596 | 81.7083 | 1.4375 | 1.4788 | 1.3031
1.125 | 86.6919 | 85.6525 | 81.6897 | 1.4389 | 1.48 | 1.3037
1.1292 | 86.691 | 85.6507 | 81.6746 | 1.4403 | 1.4812 | 1.3042
1.1333 | 86.6907 | 85.6488 | 81.66 | 1.4416 | 1.4823 | 1.3047
1.1375 | 86.6898 | 85.6459 | 81.6446 | 1.4429 | 1.4835 | 1.3052
1.1417 | 86.6885 | 85.643 | 81.6294 | 1.4442 | 1.4846 | 1.3057
1.1458 | 86.6865 | 85.6395 | 81.6143 | 1.4455 | 1.4857 | 1.3062
1.15 | 86.6852 | 85.6362 | 81.5997 | 1.4468 | 1.4867 | 1.3067
1.1542 | 86.6849 | 85.6347 | 81.5864 | 1.448 | 1.4878 | 1.3071
1.1583 | 86.6858 | 85.6333 | 81.5734 | 1.4492 | 1.4888 | 1.3076
1.1625 | 86.6845 | 85.6314 | 81.5603 | 1.4504 | 1.4898 | 1.308
1.1667 | 86.6852 | 85.6296 | 81.5475 | 1.4515 | 1.4908 | 1.3085
1.1708 | 86.6834 | 85.6274 | 81.5349 | 1.4526 | 1.4918 | 1.3089
1.175 | 86.6818 | 85.6253 | 81.5226 | 1.4538 | 1.4927 | 1.3093
1.1792 | 86.6829 | 85.6239 | 81.5109 | 1.4548 | 1.4937 | 1.3097
1.1833 | 86.6842 | 85.6226 | 81.4995 | 1.4559 | 1.4946 | 1.3101
1.1875 | 86.6824 | 85.6211 | 81.4882 | 1.4569 | 1.4955 | 1.3105
1.1917 | 86.6834 | 85.6196 | 81.4771 | 1.458 | 1.4963 | 1.3108
1.1958 | 86.6821 | 85.6179 | 81.4663 | 1.4589 | 1.4972 | 1.3112
1.2 | 86.6802 | 85.6164 | 81.4557 | 1.4599 | 1.498 | 1.3116
1.2042 | 86.6815 | 85.6151 | 81.4454 | 1.4609 | 1.4988 | 1.3119
1.2083 | 86.6831 | 85.6138 | 81.4354 | 1.4618 | 1.4996 | 1.3123
1.2125 | 86.6801 | 85.6126 | 81.4258 | 1.4627 | 1.5004 | 1.3126
1.2167 | 86.6821 | 85.6115 | 81.4163 | 1.4636 | 1.5012 | 1.3129
1.2208 | 86.6809 | 85.6104 | 81.4071 | 1.4645 | 1.5019 | 1.3132
1.225 | 86.6793 | 85.6093 | 81.398 | 1.4654 | 1.5026 | 1.3135
1.2292 | 86.6814 | 85.608 | 81.3891 | 1.4662 | 1.5034 | 1.3138
1.2333 | 86.6802 | 85.6068 | 81.3803 | 1.467 | 1.504 | 1.3141
1.2375 | 86.6789 | 85.6056 | 81.3718 | 1.4678 | 1.5047 | 1.3144
1.2417 | 86.6796 | 85.6045 | 81.3634 | 1.4686 | 1.5054 | 1.3147
1.2458 | 86.679 | 85.6033 | 81.3553 | 1.4694 | 1.5061 | 1.315
1.25 | 86.6793 | 85.6022 | 81.3473 | 1.4701 | 1.5067 | 1.3153
1.2542 | 86.679 | 85.601 | 81.3394 | 1.4709 | 1.5073 | 1.3155
1.2583 | 86.6779 | 85.5998 | 81.3317 | 1.4716 | 1.508 | 1.3158
1.2625 | 86.6762 | 85.5987 | 81.3242 | 1.4723 | 1.5086 | 1.3161
1.2667 | 86.6769 | 85.5975 | 81.3168 | 1.473 | 1.5091 | 1.3163
1.2708 | 86.6762 | 85.5965 | 81.3096 | 1.4737 | 1.5097 | 1.3165
1.275 | 86.6763 | 85.5953 | 81.3026 | 1.4743 | 1.5103 | 1.3168
1.2792 | 86.6757 | 85.5942 | 81.2956 | 1.475 | 1.5109 | 1.317
1.2833 | 86.6745 | 85.5932 | 81.2888 | 1.4756 | 1.5114 | 1.3173
1.2875 | 86.6752 | 85.5921 | 81.2821 | 1.4763 | 1.5119 | 1.3175
1.2917 | 86.674 | 85.591 | 81.2756 | 1.4769 | 1.5125 | 1.3177
1.2958 | 86.6745 | 85.59 | 81.2692 | 1.4775 | 1.513 | 1.3179
1.3 | 86.6741 | 85.5889 | 81.263 | 1.4781 | 1.5135 | 1.3181
1.3042 | 86.6721 | 85.5879 | 81.2568 | 1.4787 | 1.514 | 1.3183
1.3083 | 86.6726 | 85.5869 | 81.2508 | 1.4793 | 1.5145 | 1.3185
1.3125 | 86.6733 | 85.5868 | 81.2456 | 1.4798 | 1.5149 | 1.3187
1.3167 | 86.6732 | 85.5868 | 81.2404 | 1.4803 | 1.5154 | 1.3189
1.3208 | 86.6734 | 85.5867 | 81.2354 | 1.4809 | 1.5158 | 1.3191
1.325 | 86.6748 | 85.5866 | 81.2304 | 1.4814 | 1.5163 | 1.3193
1.3292 | 86.6726 | 85.5857 | 81.2251 | 1.4819 | 1.5167 | 1.3195
1.3333 | 86.6728 | 85.5847 | 81.2199 | 1.4824 | 1.5171 | 1.3196
1.3375 | 86.6733 | 85.584 | 81.2149 | 1.4829 | 1.5176 | 1.3198
1.3417 | 86.6722 | 85.5834 | 81.2101 | 1.4833 | 1.518 | 1.32
1.3458 | 86.6704 | 85.5828 | 81.2054 | 1.4838 | 1.5183 | 1.3201
1.35 | 86.6726 | 85.5821 | 81.2007 | 1.4843 | 1.5187 | 1.3203
1.3542 | 86.6708 | 85.5812 | 81.196 | 1.4847 | 1.5191 | 1.3205
1.3583 | 86.6714 | 85.5803 | 81.1913 | 1.4852 | 1.5195 | 1.3206
1.3625 | 86.6727 | 85.5795 | 81.1868 | 1.4856 | 1.5199 | 1.3208
1.3667 | 86.6693 | 85.5788 | 81.1824 | 1.486 | 1.5202 | 1.3209
1.3708 | 86.6691 | 85.5804 | 81.1781 | 1.4864 | 1.5205 | 1.3211
1.375 | 86.6689 | 85.5796 | 81.1739 | 1.4868 | 1.5209 | 1.3212
1.3792 | 86.669 | 85.5788 | 81.1697 | 1.4872 | 1.5212 | 1.3213
1.3833 | 86.6684 | 85.578 | 81.1655 | 1.4876 | 1.5216 | 1.3215
1.3875 | 86.6695 | 85.5749 | 81.1614 | 1.488 | 1.5219 | 1.3216
1.3917 | 86.6652 | 85.5741 | 81.1574 | 1.4884 | 1.5222 | 1.3217
1.3958 | 86.6655 | 85.5742 | 81.1535 | 1.4888 | 1.5225 | 1.3219
1.4 | 86.665 | 85.5734 | 81.1497 | 1.4891 | 1.5228 | 1.322
1.4042 | 86.6641 | 85.5726 | 81.1459 | 1.4895 | 1.5231 | 1.3221
1.4083 | 86.6687 | 85.5718 | 81.1421 | 1.4898 | 1.5234 | 1.3222
1.4125 | 86.6666 | 85.5697 | 81.138 | 1.4902 | 1.5237 | 1.3224
1.4167 | 86.6639 | 85.5683 | 81.1339 | 1.4905 | 1.524 | 1.3225
1.4208 | 86.6642 | 85.5672 | 81.1299 | 1.4909 | 1.5243 | 1.3226
1.425 | 86.6586 | 85.5658 | 81.1259 | 1.4912 | 1.5246 | 1.3227
1.4292 | 86.6601 | 85.5651 | 81.1224 | 1.4915 | 1.5249 | 1.3229
1.4333 | 86.6615 | 85.5644 | 81.1189 | 1.4919 | 1.5252 | 1.323
1.4375 | 86.6596 | 85.5632 | 81.1153 | 1.4922 | 1.5254 | 1.3231
1.4417 | 86.6594 | 85.5622 | 81.1118 | 1.4925 | 1.5257 | 1.3232
1.4458 | 86.6588 | 85.5615 | 81.1083 | 1.4928 | 1.526 | 1.3233
1.45 | 86.6564 | 85.5606 | 81.1049 | 1.4931 | 1.5262 | 1.3234
1.4542 | 86.6581 | 85.5599 | 81.1016 | 1.4934 | 1.5265 | 1.3235
1.4583 | 86.657 | 85.5592 | 81.0984 | 1.4937 | 1.5268 | 1.3236
1.4625 | 86.6557 | 85.5583 | 81.0952 | 1.494 | 1.527 | 1.3238
1.4667 | 86.655 | 85.5576 | 81.092 | 1.4943 | 1.5273 | 1.3239
1.4708 | 86.6549 | 85.557 | 81.0889 | 1.4946 | 1.5275 | 1.324
1.475 | 86.6524 | 85.5562 | 81.0859 | 1.4949 | 1.5278 | 1.3241
1.4792 | 86.6534 | 85.5556 | 81.0829 | 1.4952 | 1.528 | 1.3242
1.4833 | 86.6525 | 85.5549 | 81.082 | 1.4955 | 1.5282 | 1.3242
1.4875 | 86.6503 | 85.5542 | 81.0791 | 1.4957 | 1.5285 | 1.3243
1.4917 | 86.6519 | 85.5536 | 81.0766 | 1.496 | 1.5287 | 1.3244
1.4958 | 86.6499 | 85.553 | 81.0736 | 1.4962 | 1.5289 | 1.3245
1.5 | 86.6498 | 85.5523 | 81.0693 | 1.4965 | 1.5291 | 1.3246
1.5042 | 86.6489 | 85.5517 | 81.0664 | 1.4967 | 1.5294 | 1.3247
1.5083 | 86.6502 | 85.5511 | 81.0645 | 1.497 | 1.5296 | 1.3248
1.5125 | 86.6468 | 85.5501 | 81.0616 | 1.4972 | 1.5298 | 1.3249
1.5167 | 86.6477 | 85.5492 | 81.0588 | 1.4975 | 1.53 | 1.325
1.5208 | 86.6465 | 85.5483 | 81.056 | 1.4977 | 1.5302 | 1.325
1.525 | 86.6439 | 85.5474 | 81.0528 | 1.498 | 1.5304 | 1.3251
1.5292 | 86.6454 | 85.5468 | 81.0502 | 1.4982 | 1.5306 | 1.3252
1.5333 | 86.6438 | 85.5463 | 81.048 | 1.4985 | 1.5308 | 1.3253
1.5375 | 86.6447 | 85.5456 | 81.0454 | 1.4987 | 1.531 | 1.3254
1.5417 | 86.6438 | 85.5449 | 81.0429 | 1.4989 | 1.5312 | 1.3255
1.5458 | 86.6444 | 85.5443 | 81.0405 | 1.4992 | 1.5314 | 1.3255
1.55 | 86.6424 | 85.5436 | 81.0379 | 1.4994 | 1.5316 | 1.3256
1.5542 | 86.6428 | 85.5431 | 81.0355 | 1.4996 | 1.5318 | 1.3257
1.5583 | 86.6423 | 85.5425 | 81.0333 | 1.4998 | 1.5319 | 1.3258
1.5625 | 86.6429 | 85.542 | 81.031 | 1.5 | 1.5321 | 1.3259
1.5667 | 86.6406 | 85.5414 | 81.0287 | 1.5002 | 1.5323 | 1.3259
1.5708 | 86.6417 | 85.5409 | 81.0264 | 1.5004 | 1.5325 | 1.326
1.575 | 86.6401 | 85.5403 | 81.0241 | 1.5006 | 1.5327 | 1.3261
1.5792 | 86.6392 | 85.5398 | 81.022 | 1.5008 | 1.5328 | 1.3261
1.5833 | 86.6407 | 85.5393 | 81.0199 | 1.501 | 1.533 | 1.3262
1.5875 | 86.6395 | 85.5388 | 81.0177 | 1.5012 | 1.5332 | 1.3263
1.5917 | 86.6376 | 85.5383 | 81.0156 | 1.5014 | 1.5333 | 1.3264
1.5958 | 86.6381 | 85.5378 | 81.0136 | 1.5016 | 1.5335 | 1.3264
1.6 | 86.6373 | 85.5372 | 81.0115 | 1.5018 | 1.5336 | 1.3265
1.6042 | 86.6371 | 85.5368 | 81.0095 | 1.502 | 1.5338 | 1.3266
1.6083 | 86.6386 | 85.5363 | 81.0076 | 1.5021 | 1.534 | 1.3266
1.6125 | 86.6385 | 85.5361 | 81.0058 | 1.5023 | 1.5341 | 1.3267
1.6167 | 86.6372 | 85.5358 | 81.004 | 1.5025 | 1.5343 | 1.3267
1.6208 | 86.6373 | 85.5355 | 81.0022 | 1.5027 | 1.5344 | 1.3268
1.625 | 86.636 | 85.5353 | 81.0005 | 1.5028 | 1.5345 | 1.3269
1.6292 | 86.6376 | 85.5348 | 80.9987 | 1.503 | 1.5347 | 1.3269
1.6333 | 86.6373 | 85.5343 | 80.9969 | 1.5031 | 1.5348 | 1.327
1.6375 | 86.6378 | 85.534 | 80.9952 | 1.5033 | 1.535 | 1.327
1.6417 | 86.6375 | 85.5336 | 80.9935 | 1.5035 | 1.5351 | 1.3271
1.6458 | 86.6354 | 85.5332 | 80.9918 | 1.5036 | 1.5352 | 1.3272
1.65 | 86.6351 | 85.5329 | 80.9902 | 1.5038 | 1.5354 | 1.3272
1.6542 | 86.6354 | 85.5325 | 80.9885 | 1.5039 | 1.5355 | 1.3273
1.6583 | 86.635 | 85.532 | 80.9868 | 1.5041 | 1.5356 | 1.3273
1.6625 | 86.6341 | 85.5316 | 80.9852 | 1.5042 | 1.5357 | 1.3274
1.6667 | 86.6342 | 85.5312 | 80.9837 | 1.5044 | 1.5359 | 1.3274
1.6708 | 86.6313 | 85.5308 | 80.9821 | 1.5045 | 1.536 | 1.3275
1.675 | 86.6313 | 85.5304 | 80.9805 | 1.5046 | 1.5361 | 1.3275
1.6792 | 86.6329 | 85.53 | 80.979 | 1.5048 | 1.5362 | 1.3276
1.6833 | 86.6327 | 85.5296 | 80.9774 | 1.5049 | 1.5363 | 1.3276
1.6875 | 86.6338 | 85.5296 | 80.9763 | 1.5051 | 1.5364 | 1.3277
1.6917 | 86.634 | 85.5296 | 80.9751 | 1.5052 | 1.5366 | 1.3277
1.6958 | 86.6392 | 85.5364 | 80.9796 | 1.5053 | 1.5366 | 1.3277
1.7 | 86.645 | 85.5429 | 80.9839 | 1.5053 | 1.5367 | 1.3277
1.7042 | 86.7393 | 85.6352 | 81.0741 | 1.5047 | 1.536 | 1.327
1.7083 | 86.8257 | 85.7231 | 81.1596 | 1.5041 | 1.5354 | 1.3264
1.7125 | 86.9238 | 85.752 | 81.1979 | 1.5045 | 1.5352 | 1.3262
1.7167 | 86.9528 | 85.7805 | 81.231 | 1.5043 | 1.535 | 1.326
1.7208 | 86.9609 | 85.7548 | 81.2417 | 1.5039 | 1.5339 | 1.325
1.725 | 86.9306 | 85.7302 | 81.2489 | 1.503 | 1.5328 | 1.3239
1.7292 | 86.7339 | 85.5713 | 81.139 | 1.5042 | 1.5338 | 1.3247
1.7333 | 86.5725 | 85.4187 | 81.0371 | 1.5051 | 1.5347 | 1.3254
1.7375 | 86.5051 | 85.3991 | 81.0177 | 1.5041 | 1.5339 | 1.3245
1.7417 | 86.4883 | 85.381 | 81.0023 | 1.5035 | 1.5332 | 1.3236
1.7458 | 86.6005 | 85.518 | 81.1224 | 1.5042 | 1.5343 | 1.3241
1.75 | 86.7349 | 85.6495 | 81.2365 | 1.5053 | 1.5352 | 1.3246
1.7542 | 86.6514 | 85.5117 | 81.1488 | 1.5063 | 1.5358 | 1.3247
1.7583 | 86.5337 | 85.3766 | 81.0608 | 1.5072 | 1.5363 | 1.3246
1.7625 | 86.393 | 85.3013 | 81.0334 | 1.5076 | 1.5368 | 1.3245
1.7667 | 86.3127 | 85.2237 | 81.0098 | 1.5087 | 1.5373 | 1.3244
1.7708 | 86.2123 | 85.2093 | 81.0082 | 1.5099 | 1.539 | 1.3249
1.775 | 86.1734 | 85.1989 | 81.0154 | 1.5119 | 1.5406 | 1.3255
1.7792 | 86.1313 | 85.1337 | 80.985 | 1.5138 | 1.5421 | 1.3257
1.7833 | 86.062 | 85.0706 | 80.9522 | 1.5158 | 1.5436 | 1.3259
1.7875 | 85.9683 | 85.0085 | 80.9228 | 1.5185 | 1.5457 | 1.3265
1.7917 | 85.8931 | 84.9433 | 80.8951 | 1.5212 | 1.5478 | 1.327
1.7958 | 85.8324 | 84.9188 | 80.8715 | 1.5237 | 1.5498 | 1.3274
1.8 | 85.7988 | 84.8995 | 80.8538 | 1.5264 | 1.5518 | 1.3278
1.8042 | 85.8196 | 84.9047 | 80.8621 | 1.5293 | 1.5541 | 1.3282
1.8083 | 85.827 | 84.9108 | 80.8649 | 1.5324 | 1.5564 | 1.3287
1.8125 | 85.7653 | 84.8506 | 80.8247 | 1.5355 | 1.5589 | 1.3294
1.8167 | 85.7085 | 84.7904 | 80.7878 | 1.5387 | 1.5613 | 1.3299
1.8208 | 85.6912 | 84.7872 | 80.7765 | 1.5413 | 1.5634 | 1.3302
1.825 | 85.6919 | 84.7845 | 80.7664 | 1.544 | 1.5654 | 1.3305
1.8292 | 85.7194 | 84.803 | 80.7725 | 1.5471 | 1.568 | 1.3311
1.8333 | 85.7437 | 84.8214 | 80.7757 | 1.5503 | 1.5705 | 1.3317
1.8375 | 85.6944 | 84.7705 | 80.7365 | 1.5532 | 1.5728 | 1.3321
1.8417 | 85.6449 | 84.7221 | 80.7011 | 1.556 | 1.575 | 1.3325
1.8458 | 85.6584 | 84.7379 | 80.7021 | 1.5585 | 1.577 | 1.3329
1.85 | 85.6737 | 84.7515 | 80.7011 | 1.561 | 1.5791 | 1.3332
1.8542 | 85.6886 | 84.7577 | 80.6945 | 1.5639 | 1.5815 | 1.3337
1.8583 | 85.6974 | 84.765 | 80.6882 | 1.5668 | 1.5838 | 1.3343
1.8625 | 85.6637 | 84.7317 | 80.6603 | 1.5692 | 1.5858 | 1.3346
1.8667 | 85.6295 | 84.7002 | 80.6345 | 1.5716 | 1.5877 | 1.3349
1.8708 | 85.6491 | 84.7206 | 80.6375 | 1.574 | 1.5897 | 1.3353
1.875 | 85.6713 | 84.7382 | 80.6382 | 1.5764 | 1.5916 | 1.3356
1.8792 | 85.6689 | 84.7331 | 80.6242 | 1.5789 | 1.5937 | 1.3361
1.8833 | 85.6674 | 84.7302 | 80.6123 | 1.5813 | 1.5957 | 1.3365
1.8875 | 85.6476 | 84.7138 | 80.5958 | 1.5834 | 1.5975 | 1.3368
1.8917 | 85.6304 | 84.6978 | 80.5794 | 1.5855 | 1.5992 | 1.3371
1.8958 | 85.6452 | 84.7132 | 80.5788 | 1.5877 | 1.601 | 1.3375
1.9 | 85.6624 | 84.7265 | 80.5768 | 1.5898 | 1.6028 | 1.3378
1.9042 | 85.6539 | 84.7175 | 80.5622 | 1.5919 | 1.6045 | 1.3382
1.9083 | 85.6462 | 84.7105 | 80.5495 | 1.594 | 1.6063 | 1.3385
1.9125 | 85.6394 | 84.7057 | 80.5404 | 1.5959 | 1.6078 | 1.3388
1.9167 | 85.6329 | 84.7006 | 80.5305 | 1.5977 | 1.6094 | 1.339
1.9208 | 85.6442 | 84.7098 | 80.5266 | 1.5996 | 1.611 | 1.3394
1.925 | 85.6529 | 84.7179 | 80.5225 | 1.6015 | 1.6125 | 1.3397
1.9292 | 85.6467 | 84.71 | 80.5104 | 1.6033 | 1.614 | 1.34
1.9333 | 85.6377 | 84.7035 | 80.4996 | 1.6051 | 1.6155 | 1.3403
1.9375 | 85.6363 | 84.7032 | 80.4931 | 1.6067 | 1.6169 | 1.3405
1.9417 | 85.6352 | 84.7022 | 80.4858 | 1.6084 | 1.6183 | 1.3408
1.9458 | 85.6385 | 84.7057 | 80.4797 | 1.61 | 1.6197 | 1.3411
1.95 | 85.6422 | 84.709 | 80.474 | 1.6117 | 1.621 | 1.3413
1.9542 | 85.6288 | 84.6983 | 80.4608 | 1.6132 | 1.6224 | 1.3416
1.9583 | 85.6184 | 84.6885 | 80.4484 | 1.6148 | 1.6237 | 1.3419
1.9625 | 85.6139 | 84.6859 | 80.4397 | 1.6163 | 1.625 | 1.3421
1.9667 | 85.6111 | 84.6828 | 80.4309 | 1.6178 | 1.6262 | 1.3424
1.9708 | 85.6141 | 84.6852 | 80.4248 | 1.6193 | 1.6275 | 1.3427
1.975 | 85.6155 | 84.6876 | 80.4193 | 1.6208 | 1.6288 | 1.3429
1.9792 | 85.6091 | 84.6827 | 80.4107 | 1.6222 | 1.63 | 1.3432
1.9833 | 85.6024 | 84.6782 | 80.4021 | 1.6236 | 1.6312 | 1.3435
1.9875 | 85.5967 | 84.6736 | 80.3932 | 1.625 | 1.6323 | 1.3437
1.9917 | 85.5922 | 84.6687 | 80.3842 | 1.6264 | 1.6335 | 1.344
1.9958 | 85.5854 | 84.6646 | 80.3751 | 1.6277 | 1.6347 | 1.3442
2 | 85.5822 | 84.6609 | 80.3668 | 1.6291 | 1.6358 | 1.3445
2.0042 | 85.5787 | 84.6586 | 80.3597 | 1.6304 | 1.637 | 1.3447
2.0083 | 85.574 | 84.6565 | 80.3528 | 1.6317 | 1.6381 | 1.345
2.0125 | 85.5717 | 84.6529 | 80.3448 | 1.633 | 1.6392 | 1.3453
2.0167 | 85.5652 | 84.6492 | 80.3365 | 1.6343 | 1.6403 | 1.3455
2.0208 | 85.56 | 84.6454 | 80.3282 | 1.6355 | 1.6414 | 1.3458
2.025 | 85.555 | 84.6417 | 80.3204 | 1.6368 | 1.6424 | 1.346
2.0292 | 85.5542 | 84.6407 | 80.3139 | 1.638 | 1.6435 | 1.3462
2.0333 | 85.5526 | 84.6396 | 80.3076 | 1.6392 | 1.6445 | 1.3465
2.0375 | 85.5494 | 84.6377 | 80.3007 | 1.6404 | 1.6456 | 1.3467
2.0417 | 85.5462 | 84.6358 | 80.2938 | 1.6416 | 1.6466 | 1.347
2.0458 | 85.5402 | 84.6335 | 80.2869 | 1.6427 | 1.6476 | 1.3472
2.05 | 85.5377 | 84.6314 | 80.2802 | 1.6439 | 1.6485 | 1.3474
2.0542 | 85.5376 | 84.6309 | 80.2743 | 1.6449 | 1.6495 | 1.3476
2.0583 | 85.537 | 84.6304 | 80.2687 | 1.646 | 1.6504 | 1.3478
2.0625 | 85.5347 | 84.6294 | 80.2627 | 1.6471 | 1.6513 | 1.3481
2.0667 | 85.5333 | 84.6284 | 80.2567 | 1.6482 | 1.6522 | 1.3483
2.0708 | 85.5294 | 84.6268 | 80.2508 | 1.6492 | 1.6531 | 1.3485
2.075 | 85.5262 | 84.6254 | 80.2449 | 1.6502 | 1.654 | 1.3487
2.0792 | 85.5251 | 84.6248 | 80.2394 | 1.6512 | 1.6549 | 1.3489
2.0833 | 85.5242 | 84.6242 | 80.2341 | 1.6521 | 1.6557 | 1.3491
2.0875 | 85.5216 | 84.6235 | 80.2288 | 1.6531 | 1.6565 | 1.3493
2.0917 | 85.5227 | 84.6228 | 80.2235 | 1.654 | 1.6573 | 1.3494
2.0958 | 85.5198 | 84.6219 | 80.2184 | 1.6549 | 1.6581 | 1.3496
2.1 | 85.5172 | 84.6211 | 80.2133 | 1.6559 | 1.6589 | 1.3498
2.1042 | 85.5162 | 84.6204 | 80.2083 | 1.6567 | 1.6597 | 1.35
2.1083 | 85.5129 | 84.6197 | 80.2034 | 1.6576 | 1.6604 | 1.3502
2.1125 | 85.5119 | 84.6192 | 80.1987 | 1.6584 | 1.6612 | 1.3503
2.1167 | 85.5126 | 84.6187 | 80.1941 | 1.6593 | 1.6619 | 1.3505
2.1208 | 85.5118 | 84.6181 | 80.1896 | 1.6601 | 1.6626 | 1.3507
2.125 | 85.5099 | 84.6175 | 80.1851 | 1.6609 | 1.6633 | 1.3508
2.1292 | 85.509 | 84.6168 | 80.1806 | 1.6617 | 1.664 | 1.351
2.1333 | 85.5048 | 84.6161 | 80.1762 | 1.6624 | 1.6646 | 1.3511
2.1375 | 85.5036 | 84.6165 | 80.1719 | 1.6632 | 1.6653 | 1.3513
2.1417 | 85.5025 | 84.6183 | 80.1676 | 1.6639 | 1.666 | 1.3514
2.1458 | 85.5015 | 84.6208 | 80.1635 | 1.6646 | 1.6666 | 1.3516
2.15 | 85.4998 | 84.6241 | 80.1594 | 1.6653 | 1.6673 | 1.3517
2.1542 | 85.4975 | 84.628 | 80.1559 | 1.666 | 1.6679 | 1.3519
2.1583 | 85.498 | 84.6312 | 80.1525 | 1.6667 | 1.6686 | 1.352
2.1625 | 85.4984 | 84.6345 | 80.1491 | 1.6674 | 1.6692 | 1.3522
2.1667 | 85.4953 | 84.6381 | 80.1457 | 1.668 | 1.6698 | 1.3523
2.1708 | 85.4964 | 84.641 | 80.1418 | 1.6687 | 1.6704 | 1.3524
2.175 | 85.4928 | 84.6442 | 80.138 | 1.6693 | 1.6711 | 1.3525
2.1792 | 85.4897 | 84.6478 | 80.1345 | 1.6699 | 1.6716 | 1.3527
2.1833 | 85.492 | 84.651 | 80.1311 | 1.6705 | 1.6722 | 1.3528
2.1875 | 85.4919 | 84.655 | 80.1281 | 1.6711 | 1.6728 | 1.3529
2.1917 | 85.491 | 84.659 | 80.1252 | 1.6717 | 1.6734 | 1.353
2.1958 | 85.4911 | 84.6627 | 80.1222 | 1.6722 | 1.6739 | 1.3531
2.2 | 85.4888 | 84.6664 | 80.1192 | 1.6728 | 1.6745 | 1.3533
2.2042 | 85.4876 | 84.6695 | 80.1159 | 1.6733 | 1.675 | 1.3534
2.2083 | 85.4855 | 84.6723 | 80.1128 | 1.6739 | 1.6755 | 1.3535
2.2125 | 85.4886 | 84.6784 | 80.1102 | 1.6744 | 1.676 | 1.3536
2.2167 | 85.4856 | 84.6822 | 80.1077 | 1.6749 | 1.6765 | 1.3537
2.2208 | 85.4846 | 84.6852 | 80.1053 | 1.6754 | 1.677 | 1.3538
2.225 | 85.4858 | 84.6885 | 80.1028 | 1.6759 | 1.6775 | 1.3539
2.2292 | 85.4822 | 84.6889 | 80.0999 | 1.6763 | 1.6779 | 1.354
2.2333 | 85.4833 | 84.6912 | 80.0971 | 1.6768 | 1.6784 | 1.3541
2.2375 | 85.4831 | 84.6955 | 80.0946 | 1.6773 | 1.6788 | 1.3542
2.2417 | 85.4804 | 84.6983 | 80.0921 | 1.6777 | 1.6793 | 1.3542
2.2458 | 85.4794 | 84.7026 | 80.0896 | 1.6782 | 1.6797 | 1.3543
2.25 | 85.4829 | 84.7052 | 80.0872 | 1.6786 | 1.6801 | 1.3544
2.2542 | 85.4789 | 84.7061 | 80.0842 | 1.679 | 1.6805 | 1.3545
2.2583 | 85.4785 | 84.7073 | 80.0813 | 1.6794 | 1.6809 | 1.3546
2.2625 | 85.4779 | 84.7078 | 80.0785 | 1.6798 | 1.6813 | 1.3547
2.2667 | 85.4703 | 84.7095 | 80.0759 | 1.6802 | 1.6817 | 1.3548
2.2708 | 85.4698 | 84.7132 | 80.0736 | 1.6806 | 1.6821 | 1.3549
2.275 | 85.4718 | 84.7155 | 80.0714 | 1.681 | 1.6825 | 1.3549
2.2792 | 85.4672 | 84.717 | 80.0689 | 1.6814 | 1.6829 | 1.355
2.2833 | 85.4718 | 84.7186 | 80.0665 | 1.6818 | 1.6833 | 1.3551
2.2875 | 85.4699 | 84.7187 | 80.0638 | 1.6822 | 1.6836 | 1.3552
2.2917 | 85.4637 | 84.7199 | 80.0612 | 1.6825 | 1.684 | 1.3553
2.2958 | 85.4647 | 84.722 | 80.0587 | 1.6829 | 1.6844 | 1.3554
2.3 | 85.4606 | 84.7234 | 80.0563 | 1.6833 | 1.6847 | 1.3554
2.3042 | 85.4589 | 84.725 | 80.054 | 1.6836 | 1.6851 | 1.3555
2.3083 | 85.4633 | 84.7266 | 80.0518 | 1.684 | 1.6854 | 1.3556
2.3125 | 85.4601 | 84.7274 | 80.0495 | 1.6844 | 1.6858 | 1.3557
2.3167 | 85.457 | 84.7286 | 80.0471 | 1.6847 | 1.6861 | 1.3557
2.3208 | 85.4568 | 84.7303 | 80.0448 | 1.6851 | 1.6865 | 1.3558
2.325 | 85.4524 | 84.7317 | 80.0446 | 1.6854 | 1.6868 | 1.3559
2.3292 | 85.4536 | 84.7332 | 80.0425 | 1.6857 | 1.6871 | 1.356
2.3333 | 85.4535 | 84.7348 | 80.0401 | 1.686 | 1.6874 | 1.356
2.3375 | 85.4523 | 84.7359 | 80.0378 | 1.6864 | 1.6878 | 1.3561
2.3417 | 85.4498 | 84.7372 | 80.0341 | 1.6867 | 1.6881 | 1.3562
2.3458 | 85.4508 | 84.7387 | 80.0319 | 1.687 | 1.6884 | 1.3562
2.35 | 85.4465 | 84.74 | 80.0308 | 1.6873 | 1.6887 | 1.3563
2.3542 | 85.4497 | 84.741 | 80.0288 | 1.6876 | 1.689 | 1.3564
2.3583 | 85.4468 | 84.7422 | 80.0277 | 1.688 | 1.6893 | 1.3564
2.3625 | 85.4458 | 84.7431 | 80.0258 | 1.6882 | 1.6896 | 1.3565
2.3667 | 85.4437 | 84.7441 | 80.0234 | 1.6886 | 1.6899 | 1.3566
2.3708 | 85.4425 | 84.7456 | 80.0213 | 1.6888 | 1.6902 | 1.3567
2.375 | 85.4411 | 84.747 | 80.0187 | 1.6891 | 1.6905 | 1.3567
2.3792 | 85.4409 | 84.7482 | 80.0167 | 1.6894 | 1.6908 | 1.3568
2.3833 | 85.4424 | 84.7493 | 80.0156 | 1.6897 | 1.691 | 1.3568
2.3875 | 85.4391 | 84.7501 | 80.0138 | 1.69 | 1.6913 | 1.3569
2.3917 | 85.4393 | 84.751 | 80.0117 | 1.6903 | 1.6916 | 1.357
2.3958 | 85.4358 | 84.752 | 80.0097 | 1.6905 | 1.6919 | 1.357
2.4 | 85.4332 | 84.7529 | 80.0073 | 1.6908 | 1.6921 | 1.3571
2.4042 | 85.4313 | 84.754 | 80.0054 | 1.6911 | 1.6924 | 1.3572
2.4083 | 85.4337 | 84.7552 | 80.0041 | 1.6913 | 1.6927 | 1.3572
2.4125 | 85.4308 | 84.7558 | 80.0022 | 1.6916 | 1.6929 | 1.3573
2.4167 | 85.4319 | 84.7564 | 80.0002 | 1.6919 | 1.6932 | 1.3573
2.4208 | 85.429 | 84.757 | 79.9982 | 1.6922 | 1.6934 | 1.3574
2.425 | 85.4261 | 84.7576 | 79.996 | 1.6924 | 1.6937 | 1.3575
2.4292 | 85.424 | 84.7586 | 79.9942 | 1.6927 | 1.6939 | 1.3575
2.4333 | 85.425 | 84.7597 | 79.9928 | 1.6929 | 1.6942 | 1.3576
2.4375 | 85.4242 | 84.7605 | 79.9911 | 1.6931 | 1.6944 | 1.3576
2.4417 | 85.4241 | 84.7614 | 79.9893 | 1.6934 | 1.6947 | 1.3577
2.4458 | 85.4244 | 84.7622 | 79.9875 | 1.6937 | 1.6949 | 1.3578
2.45 | 85.4232 | 84.763 | 79.9857 | 1.6939 | 1.6951 | 1.3578
2.4542 | 85.4205 | 84.7641 | 79.9842 | 1.6941 | 1.6954 | 1.3579
2.4583 | 85.4223 | 84.7653 | 79.9828 | 1.6943 | 1.6956 | 1.3579
2.4625 | 85.4197 | 84.7663 | 79.9814 | 1.6946 | 1.6958 | 1.358
2.4667 | 85.4187 | 84.7673 | 79.9798 | 1.6948 | 1.6961 | 1.358
2.4708 | 85.4178 | 84.768 | 79.9782 | 1.695 | 1.6963 | 1.3581
2.475 | 85.4171 | 84.7688 | 79.9766 | 1.6952 | 1.6965 | 1.3581
2.4792 | 85.4154 | 84.7697 | 79.9751 | 1.6955 | 1.6967 | 1.3582
2.4833 | 85.4179 | 84.7706 | 79.9737 | 1.6957 | 1.6969 | 1.3582
2.4875 | 85.4154 | 84.7717 | 79.9723 | 1.6959 | 1.6971 | 1.3583
2.4917 | 85.4148 | 84.7726 | 79.971 | 1.6961 | 1.6973 | 1.3583
2.4958 | 85.4136 | 84.7735 | 79.9696 | 1.6963 | 1.6975 | 1.3584
2.5 | 85.4126 | 84.7744 | 79.9682 | 1.6965 | 1.6977 | 1.3584
2.5042 | 85.4142 | 84.7752 | 79.9668 | 1.6967 | 1.6979 | 1.3585
2.5083 | 85.4138 | 84.7759 | 79.9655 | 1.6969 | 1.6981 | 1.3585
2.5125 | 85.4142 | 84.7766 | 79.964 | 1.6971 | 1.6983 | 1.3586
2.5167 | 85.4116 | 84.7773 | 79.9627 | 1.6973 | 1.6985 | 1.3586
2.5208 | 85.4121 | 84.7778 | 79.9613 | 1.6975 | 1.6987 | 1.3587
2.525 | 85.4092 | 84.7785 | 79.9599 | 1.6976 | 1.6988 | 1.3587
2.5292 | 85.4115 | 84.7792 | 79.9586 | 1.6978 | 1.699 | 1.3588
2.5333 | 85.4097 | 84.7798 | 79.9573 | 1.698 | 1.6992 | 1.3588
2.5375 | 85.4051 | 84.7775 | 79.9534 | 1.6982 | 1.6994 | 1.3589
2.5417 | 85.4008 | 84.7753 | 79.9497 | 1.6984 | 1.6996 | 1.3589
2.5458 | 85.3945 | 84.7716 | 79.9443 | 1.6986 | 1.6998 | 1.359
2.55 | 85.3893 | 84.7682 | 79.9392 | 1.6988 | 1.7 | 1.3591
2.5542 | 85.3626 | 84.7403 | 79.9081 | 1.6993 | 1.7005 | 1.3594
2.5583 | 85.3378 | 84.7138 | 79.8786 | 1.6997 | 1.7009 | 1.3597
2.5625 | 85.3279 | 84.7064 | 79.8632 | 1.7 | 1.7012 | 1.3598
2.5667 | 85.3217 | 84.7002 | 79.8502 | 1.7003 | 1.7015 | 1.36
2.5708 | 85.2758 | 84.7144 | 79.8372 | 1.7012 | 1.702 | 1.3605
2.575 | 85.2885 | 84.7292 | 79.83 | 1.7017 | 1.7026 | 1.3609
2.5792 | 85.3603 | 84.8536 | 79.9156 | 1.7014 | 1.7019 | 1.3603
2.5833 | 85.4783 | 84.972 | 80.0006 | 1.7007 | 1.7013 | 1.3597
2.5875 | 85.5637 | 85.0004 | 80.0202 | 1.7013 | 1.7015 | 1.3601
2.5917 | 85.666 | 85.0237 | 80.038 | 1.7021 | 1.7017 | 1.3605
2.5958 | 85.6731 | 84.9636 | 80.0134 | 1.7012 | 1.7006 | 1.3596
2.6 | 85.661 | 84.9025 | 79.984 | 1.7009 | 1.6994 | 1.3588
2.6042 | 85.613 | 84.8396 | 79.9553 | 1.7013 | 1.7 | 1.3594
2.6083 | 85.5223 | 84.7825 | 79.9267 | 1.702 | 1.7004 | 1.36
2.6125 | 85.4864 | 84.7964 | 79.9149 | 1.7014 | 1.6996 | 1.3594
2.6167 | 85.4398 | 84.8148 | 79.914 | 1.7004 | 1.6989 | 1.3588
2.6208 | 85.5791 | 84.929 | 80.0073 | 1.6999 | 1.6989 | 1.3589
2.625 | 85.6677 | 85.0365 | 80.094 | 1.6998 | 1.699 | 1.359
2.6292 | 85.7031 | 84.9108 | 80.0299 | 1.7 | 1.6992 | 1.3591
2.6333 | 85.6313 | 84.7835 | 79.9533 | 1.7005 | 1.6993 | 1.3592
2.6375 | 85.5567 | 84.7408 | 79.9431 | 1.7004 | 1.6987 | 1.3587
2.6417 | 85.4726 | 84.7005 | 79.9404 | 1.7 | 1.6983 | 1.3583
2.6458 | 85.4033 | 84.7358 | 79.9758 | 1.7001 | 1.6991 | 1.3586
2.65 | 85.3652 | 84.7768 | 80.0188 | 1.7005 | 1.6999 | 1.3589
2.6542 | 85.3172 | 84.6788 | 79.9807 | 1.701 | 1.7006 | 1.3589
2.6583 | 85.2127 | 84.5792 | 79.9304 | 1.7016 | 1.7013 | 1.3588
2.6625 | 85.132 | 84.5314 | 79.9222 | 1.7028 | 1.7022 | 1.3589
2.6667 | 85.0675 | 84.4835 | 79.9175 | 1.704 | 1.7031 | 1.359
2.6708 | 84.9962 | 84.4811 | 79.9136 | 1.7053 | 1.7045 | 1.3592
2.675 | 84.9528 | 84.4897 | 79.9196 | 1.707 | 1.706 | 1.3594
2.6792 | 84.9513 | 84.4663 | 79.9204 | 1.7087 | 1.7075 | 1.3595
2.6833 | 84.9187 | 84.4421 | 79.9112 | 1.7105 | 1.709 | 1.3596
2.6875 | 84.852 | 84.395 | 79.8927 | 1.7128 | 1.7109 | 1.3599
2.6917 | 84.7952 | 84.3471 | 79.8758 | 1.715 | 1.7127 | 1.3602
2.6958 | 84.7526 | 84.3474 | 79.8674 | 1.7169 | 1.7144 | 1.3602
2.7 | 84.7352 | 84.3548 | 79.8658 | 1.7189 | 1.716 | 1.3603
2.7042 | 84.7585 | 84.3718 | 79.8782 | 1.7212 | 1.7181 | 1.3605
2.7083 | 84.7678 | 84.3883 | 79.8846 | 1.7236 | 1.7202 | 1.3608
2.7125 | 84.7102 | 84.3446 | 79.8593 | 1.726 | 1.7222 | 1.361
2.7167 | 84.6558 | 84.3008 | 79.8349 | 1.7284 | 1.7242 | 1.3612
2.7208 | 84.6477 | 84.3172 | 79.835 | 1.7304 | 1.726 | 1.3613
2.725 | 84.6503 | 84.3358 | 79.8388 | 1.7324 | 1.7277 | 1.3614
2.7292 | 84.6718 | 84.3569 | 79.8457 | 1.7348 | 1.7299 | 1.3616
2.7333 | 84.6841 | 84.3784 | 79.8509 | 1.7373 | 1.7321 | 1.3619
2.7375 | 84.638 | 84.3453 | 79.8295 | 1.7394 | 1.734 | 1.3621
2.7417 | 84.5929 | 84.3123 | 79.8091 | 1.7415 | 1.7359 | 1.3623
2.7458 | 84.6041 | 84.3383 | 79.8161 | 1.7435 | 1.7376 | 1.3624
2.75 | 84.6181 | 84.3637 | 79.8235 | 1.7454 | 1.7394 | 1.3625
2.7542 | 84.6266 | 84.3759 | 79.8233 | 1.7477 | 1.7414 | 1.3628
2.7583 | 84.6315 | 84.3896 | 79.8228 | 1.7499 | 1.7434 | 1.363
2.7625 | 84.5996 | 84.3714 | 79.8092 | 1.7517 | 1.7451 | 1.3632
2.7667 | 84.5718 | 84.3526 | 79.7963 | 1.7536 | 1.7468 | 1.3633
2.7708 | 84.583 | 84.3776 | 79.8031 | 1.7554 | 1.7485 | 1.3635
2.775 | 84.601 | 84.4013 | 79.8092 | 1.7572 | 1.7501 | 1.3636
2.7792 | 84.5947 | 84.4044 | 79.8042 | 1.7591 | 1.7519 | 1.3638
2.7833 | 84.5936 | 84.4093 | 79.7998 | 1.761 | 1.7536 | 1.364
2.7875 | 84.5752 | 84.4033 | 79.7931 | 1.7627 | 1.7551 | 1.3641
2.7917 | 84.5606 | 84.3963 | 79.7865 | 1.7643 | 1.7566 | 1.3643
2.7958 | 84.5717 | 84.4159 | 79.7905 | 1.7659 | 1.7581 | 1.3644
2.8 | 84.5824 | 84.4346 | 79.7941 | 1.7676 | 1.7596 | 1.3646
2.8042 | 84.577 | 84.4355 | 79.7896 | 1.7692 | 1.7611 | 1.3647
2.8083 | 84.5714 | 84.4377 | 79.7857 | 1.7708 | 1.7626 | 1.3649
2.8125 | 84.5672 | 84.4394 | 79.7836 | 1.7722 | 1.7639 | 1.365
2.8167 | 84.5598 | 84.4399 | 79.781 | 1.7736 | 1.7652 | 1.3651
2.8208 | 84.5658 | 84.452 | 79.7822 | 1.7751 | 1.7666 | 1.3652
2.825 | 84.5696 | 84.4636 | 79.783 | 1.7765 | 1.7679 | 1.3654
2.8292 | 84.5578 | 84.4586 | 79.7766 | 1.7779 | 1.7692 | 1.3655
2.8333 | 84.5473 | 84.4545 | 79.7704 | 1.7793 | 1.7705 | 1.3656
2.8375 | 84.5446 | 84.4567 | 79.7682 | 1.7806 | 1.7717 | 1.3657
2.8417 | 84.5406 | 84.4582 | 79.7659 | 1.7818 | 1.7728 | 1.3658
2.8458 | 84.5441 | 84.4683 | 79.7668 | 1.7831 | 1.774 | 1.366
2.85 | 84.5475 | 84.4782 | 79.7679 | 1.7844 | 1.7752 | 1.3661
2.8542 | 84.5386 | 84.4746 | 79.7634 | 1.7856 | 1.7764 | 1.3662
2.8583 | 84.5291 | 84.4713 | 79.7587 | 1.7868 | 1.7775 | 1.3664
2.8625 | 84.5244 | 84.4707 | 79.7558 | 1.788 | 1.7786 | 1.3665
2.8667 | 84.5189 | 84.4694 | 79.7525 | 1.7892 | 1.7797 | 1.3666
2.8708 | 84.5149 | 84.4724 | 79.7505 | 1.7904 | 1.7808 | 1.3667
2.875 | 84.5148 | 84.4756 | 79.749 | 1.7915 | 1.7819 | 1.3668
2.8792 | 84.5071 | 84.4748 | 79.7464 | 1.7926 | 1.7829 | 1.367
2.8833 | 84.502 | 84.4741 | 79.7439 | 1.7938 | 1.784 | 1.3671
2.8875 | 84.4968 | 84.473 | 79.7411 | 1.7949 | 1.785 | 1.3672
2.8917 | 84.4881 | 84.4716 | 79.7379 | 1.7959 | 1.786 | 1.3673
2.8958 | 84.4857 | 84.4717 | 79.7352 | 1.7971 | 1.787 | 1.3675
2.9 | 84.4793 | 84.4719 | 79.7327 | 1.7981 | 1.788 | 1.3676
2.9042 | 84.4775 | 84.4726 | 79.7308 | 1.7992 | 1.789 | 1.3677
2.9083 | 84.4736 | 84.4733 | 79.729 | 1.8002 | 1.79 | 1.3678
2.9125 | 84.4685 | 84.4731 | 79.7266 | 1.8012 | 1.791 | 1.368
2.9167 | 84.4645 | 84.4727 | 79.724 | 1.8023 | 1.7919 | 1.3681
2.9208 | 84.4586 | 84.4726 | 79.7215 | 1.8032 | 1.7929 | 1.3682
2.925 | 84.4535 | 84.4727 | 79.7192 | 1.8042 | 1.7938 | 1.3683
2.9292 | 84.454 | 84.474 | 79.7175 | 1.8052 | 1.7947 | 1.3684
2.9333 | 84.4497 | 84.4754 | 79.7161 | 1.8062 | 1.7956 | 1.3686
2.9375 | 84.4479 | 84.4759 | 79.7141 | 1.8071 | 1.7965 | 1.3687
2.9417 | 84.4451 | 84.4762 | 79.712 | 1.808 | 1.7974 | 1.3688
2.9458 | 84.4383 | 84.4763 | 79.7098 | 1.8089 | 1.7982 | 1.3689
2.95 | 84.4354 | 84.4765 | 79.7076 | 1.8098 | 1.7991 | 1.369
2.9542 | 84.4333 | 84.4778 | 79.7062 | 1.8107 | 1.7999 | 1.3691
2.9583 | 84.4331 | 84.4791 | 79.7047 | 1.8116 | 1.8007 | 1.3692
2.9625 | 84.4292 | 84.4801 | 79.703 | 1.8124 | 1.8015 | 1.3693
2.9667 | 84.4301 | 84.4808 | 79.7013 | 1.8132 | 1.8023 | 1.3694
2.9708 | 84.4246 | 84.4812 | 79.6995 | 1.814 | 1.8031 | 1.3695
2.975 | 84.4213 | 84.4815 | 79.6978 | 1.8149 | 1.8038 | 1.3696
2.9792 | 84.4202 | 84.4824 | 79.6962 | 1.8156 | 1.8045 | 1.3697
2.9833 | 84.4177 | 84.4833 | 79.6947 | 1.8164 | 1.8053 | 1.3698
2.9875 | 84.4144 | 84.4841 | 79.6932 | 1.8172 | 1.806 | 1.3699
2.9917 | 84.4165 | 84.4849 | 79.6917 | 1.8179 | 1.8067 | 1.37
2.9958 | 84.4131 | 84.4845 | 79.6902 | 1.8186 | 1.8074 | 1.3701
3 | 84.4105 | 84.4829 | 79.6887 | 1.8193 | 1.8081 | 1.3702
3.0042 | 84.4103 | 84.4802 | 79.6869 | 1.8201 | 1.8088 | 1.3703
3.0083 | 84.4047 | 84.4763 | 79.6853 | 1.8207 | 1.8094 | 1.3704
3.0125 | 84.4033 | 84.4733 | 79.6838 | 1.8214 | 1.8101 | 1.3705
3.0167 | 84.4018 | 84.4716 | 79.6822 | 1.822 | 1.8108 | 1.3706
3.0208 | 84.4008 | 84.4703 | 79.6808 | 1.8227 | 1.8115 | 1.3706
3.025 | 84.3973 | 84.4695 | 79.6794 | 1.8233 | 1.8122 | 1.3707
3.0292 | 84.396 | 84.4685 | 79.6783 | 1.824 | 1.8128 | 1.3708
3.0333 | 84.3941 | 84.4669 | 79.6773 | 1.8246 | 1.8135 | 1.3709
3.0375 | 84.3941 | 84.4653 | 79.6761 | 1.8252 | 1.8141 | 1.371
3.0417 | 84.3913 | 84.4646 | 79.6748 | 1.8258 | 1.8148 | 1.371
3.0458 | 84.3915 | 84.4634 | 79.6732 | 1.8264 | 1.8154 | 1.3711
3.05 | 84.3856 | 84.4626 | 79.6717 | 1.8269 | 1.8161 | 1.3712
3.0542 | 84.3834 | 84.4629 | 79.6708 | 1.8275 | 1.8167 | 1.3713
3.0583 | 84.3848 | 84.4628 | 79.67 | 1.828 | 1.8173 | 1.3713
3.0625 | 84.385 | 84.4624 | 79.6692 | 1.8286 | 1.8179 | 1.3714
3.0667 | 84.3843 | 84.463 | 79.6685 | 1.8291 | 1.8185 | 1.3715
3.0708 | 84.3825 | 84.4631 | 79.6674 | 1.8296 | 1.8191 | 1.3715
3.075 | 84.3811 | 84.4631 | 79.6661 | 1.8301 | 1.8197 | 1.3716
3.0792 | 84.3776 | 84.4639 | 79.665 | 1.8306 | 1.8202 | 1.3717
3.0833 | 84.3787 | 84.4639 | 79.664 | 1.8311 | 1.8208 | 1.3717
3.0875 | 84.3814 | 84.4661 | 79.6632 | 1.8315 | 1.8213 | 1.3718
3.0917 | 84.3776 | 84.4672 | 79.6626 | 1.832 | 1.8218 | 1.3719
3.0958 | 84.3767 | 84.4667 | 79.6619 | 1.8325 | 1.8224 | 1.3719
3.1 | 84.3761 | 84.4673 | 79.661 | 1.8329 | 1.8229 | 1.372
3.1042 | 84.3693 | 84.4658 | 79.6601 | 1.8333 | 1.8234 | 1.372
3.1083 | 84.374 | 84.4657 | 79.6592 | 1.8337 | 1.8238 | 1.3721
3.1125 | 84.3739 | 84.4684 | 79.6585 | 1.8341 | 1.8243 | 1.3721
3.1167 | 84.3708 | 84.4693 | 79.6578 | 1.8345 | 1.8248 | 1.3722
3.1208 | 84.3715 | 84.4701 | 79.657 | 1.8349 | 1.8252 | 1.3722
3.125 | 84.3707 | 84.4704 | 79.6562 | 1.8353 | 1.8257 | 1.3723
3.1292 | 84.3664 | 84.4686 | 79.655 | 1.8357 | 1.8261 | 1.3723
3.1333 | 84.3676 | 84.4677 | 79.6538 | 1.8361 | 1.8266 | 1.3724
3.1375 | 84.3677 | 84.4673 | 79.6529 | 1.8364 | 1.827 | 1.3724
3.1417 | 84.3607 | 84.4673 | 79.6521 | 1.8368 | 1.8274 | 1.3725
3.1458 | 84.3598 | 84.4689 | 79.6515 | 1.8371 | 1.8278 | 1.3725
3.15 | 84.363 | 84.4693 | 79.6509 | 1.8375 | 1.8282 | 1.3726
3.1542 | 84.3567 | 84.468 | 79.6499 | 1.8378 | 1.8286 | 1.3726
3.1583 | 84.362 | 84.4672 | 79.6489 | 1.8382 | 1.829 | 1.3727
3.1625 | 84.3615 | 84.4657 | 79.6479 | 1.8385 | 1.8294 | 1.3727
3.1667 | 84.352 | 84.4649 | 79.6469 | 1.8388 | 1.8297 | 1.3728
3.1708 | 84.3525 | 84.4654 | 79.6461 | 1.8392 | 1.8301 | 1.3728
3.175 | 84.3516 | 84.4651 | 79.6447 | 1.8394 | 1.8305 | 1.3729
3.1792 | 84.3461 | 84.4643 | 79.6439 | 1.8398 | 1.8309 | 1.3729
3.1833 | 84.3542 | 84.4638 | 79.6432 | 1.8401 | 1.8312 | 1.373
3.1875 | 84.3509 | 84.4623 | 79.6423 | 1.8404 | 1.8316 | 1.373
3.1917 | 84.3447 | 84.4614 | 79.6417 | 1.8407 | 1.8319 | 1.3731
3.1958 | 84.3443 | 84.4614 | 79.641 | 1.841 | 1.8323 | 1.3731
3.2 | 84.3422 | 84.4609 | 79.6412 | 1.8413 | 1.8326 | 1.3731
3.2042 | 84.3407 | 84.4606 | 79.6406 | 1.8416 | 1.833 | 1.3732
3.2083 | 84.3451 | 84.4602 | 79.6393 | 1.8419 | 1.8333 | 1.3732
3.2125 | 84.3425 | 84.4592 | 79.6384 | 1.8422 | 1.8336 | 1.3733
3.2167 | 84.3376 | 84.4586 | 79.6366 | 1.8425 | 1.834 | 1.3733
3.2208 | 84.337 | 84.4585 | 79.6357 | 1.8428 | 1.8343 | 1.3733
3.225 | 84.3336 | 84.4579 | 79.6363 | 1.843 | 1.8346 | 1.3734
3.2292 | 84.3354 | 84.4573 | 79.6358 | 1.8433 | 1.8349 | 1.3734
3.2333 | 84.3357 | 84.4567 | 79.6352 | 1.8436 | 1.8352 | 1.3735
3.2375 | 84.3349 | 84.4558 | 79.6345 | 1.8438 | 1.8355 | 1.3735
3.2417 | 84.3296 | 84.4552 | 79.6333 | 1.8441 | 1.8358 | 1.3735
3.2458 | 84.3299 | 84.4551 | 79.6324 | 1.8444 | 1.8361 | 1.3736
3.25 | 84.3254 | 84.4548 | 79.6317 | 1.8446 | 1.8364 | 1.3736
3.2542 | 84.3278 | 84.4539 | 79.6309 | 1.8449 | 1.8367 | 1.3737
3.2583 | 84.3279 | 84.4531 | 79.6306 | 1.8451 | 1.837 | 1.3737
3.2625 | 84.3264 | 84.452 | 79.6298 | 1.8453 | 1.8373 | 1.3737
3.2667 | 84.3245 | 84.4511 | 79.6287 | 1.8456 | 1.8376 | 1.3738
3.2708 | 84.322 | 84.4507 | 79.6279 | 1.8458 | 1.8379 | 1.3738
3.275 | 84.318 | 84.4503 | 79.6269 | 1.8461 | 1.8381 | 1.3738
3.2792 | 84.318 | 84.4497 | 79.6261 | 1.8463 | 1.8384 | 1.3739
3.2833 | 84.3183 | 84.4491 | 79.6259 | 1.8466 | 1.8387 | 1.3739
3.2875 | 84.3173 | 84.4481 | 79.6252 | 1.8468 | 1.8389 | 1.374
3.2917 | 84.3175 | 84.4471 | 79.6242 | 1.847 | 1.8392 | 1.374
3.2958 | 84.3147 | 84.4463 | 79.6233 | 1.8473 | 1.8395 | 1.374
3.3 | 84.3094 | 84.4455 | 79.6223 | 1.8475 | 1.8397 | 1.3741
3.3042 | 84.3095 | 84.445 | 79.6215 | 1.8477 | 1.84 | 1.3741
3.3083 | 84.308 | 84.4445 | 79.6211 | 1.8479 | 1.8403 | 1.3741
3.3125 | 84.3097 | 84.4437 | 79.6205 | 1.8482 | 1.8405 | 1.3742
3.3167 | 84.3097 | 84.4428 | 79.6196 | 1.8484 | 1.8408 | 1.3742
3.3208 | 84.3093 | 84.4422 | 79.6189 | 1.8486 | 1.841 | 1.3743
3.325 | 84.3054 | 84.4416 | 79.618 | 1.8489 | 1.8413 | 1.3743
3.3292 | 84.3054 | 84.4413 | 79.6174 | 1.8491 | 1.8415 | 1.3743
3.3333 | 84.3034 | 84.4411 | 79.617 | 1.8493 | 1.8418 | 1.3744
3.3375 | 84.3037 | 84.4406 | 79.6165 | 1.8495 | 1.842 | 1.3744
3.3417 | 84.3025 | 84.44 | 79.6157 | 1.8497 | 1.8422 | 1.3744
3.3458 | 84.2999 | 84.4394 | 79.615 | 1.8499 | 1.8425 | 1.3745
3.35 | 84.2992 | 84.4387 | 79.6142 | 1.8501 | 1.8427 | 1.3745
3.3542 | 84.2965 | 84.4383 | 79.6135 | 1.8503 | 1.8429 | 1.3745
3.3583 | 84.2976 | 84.4379 | 79.613 | 1.8505 | 1.8431 | 1.3746
3.3625 | 84.295 | 84.4374 | 79.6124 | 1.8507 | 1.8434 | 1.3746
3.3667 | 84.2958 | 84.437 | 79.6117 | 1.8509 | 1.8436 | 1.3747
3.3708 | 84.2926 | 84.4367 | 79.6112 | 1.8511 | 1.8438 | 1.3747
3.375 | 84.2947 | 84.4365 | 79.6106 | 1.8513 | 1.844 | 1.3747
3.3792 | 84.293 | 84.4362 | 79.6101 | 1.8515 | 1.8442 | 1.3748
3.3833 | 84.2947 | 84.4359 | 79.6096 | 1.8517 | 1.8444 | 1.3748
3.3875 | 84.293 | 84.4355 | 79.6091 | 1.8519 | 1.8446 | 1.3748
3.3917 | 84.292 | 84.435 | 79.6085 | 1.852 | 1.8448 | 1.3748
3.3958 | 84.292 | 84.4348 | 79.6081 | 1.8522 | 1.845 | 1.3749
3.4 | 84.2918 | 84.4347 | 79.6077 | 1.8523 | 1.8452 | 1.3749
3.4042 | 84.3001 | 84.4428 | 79.6162 | 1.8524 | 1.8453 | 1.3749
3.4083 | 84.3081 | 84.4503 | 79.6241 | 1.8525 | 1.8455 | 1.3748
3.4125 | 84.3053 | 84.4465 | 79.6232 | 1.8527 | 1.8457 | 1.3749
3.4167 | 84.299 | 84.4429 | 79.6221 | 1.8529 | 1.8459 | 1.3749
3.4208 | 84.3088 | 84.4336 | 79.6242 | 1.8528 | 1.846 | 1.3748
3.425 | 84.2977 | 84.4236 | 79.6231 | 1.853 | 1.8461 | 1.3747
3.4292 | 84.2525 | 84.3598 | 79.5756 | 1.8535 | 1.8469 | 1.3752
3.4333 | 84.1938 | 84.2975 | 79.5277 | 1.8542 | 1.8476 | 1.3756
3.4375 | 84.1601 | 84.2801 | 79.5139 | 1.8543 | 1.8479 | 1.3755
3.4417 | 84.1445 | 84.2634 | 79.502 | 1.8546 | 1.8482 | 1.3755
3.4458 | 84.1015 | 84.2897 | 79.497 | 1.8558 | 1.8492 | 1.3763
3.45 | 84.0664 | 84.3192 | 79.4962 | 1.8572 | 1.8502 | 1.377
3.4542 | 84.1259 | 84.4315 | 79.5577 | 1.857 | 1.8496 | 1.3764
3.4583 | 84.1698 | 84.5429 | 79.6189 | 1.857 | 1.8491 | 1.3758
3.4625 | 84.2445 | 84.5618 | 79.6306 | 1.8578 | 1.8497 | 1.3765
3.4667 | 84.3259 | 84.5764 | 79.6375 | 1.8587 | 1.8503 | 1.3771
3.4708 | 84.3051 | 84.4975 | 79.5872 | 1.8587 | 1.8495 | 1.3765
3.475 | 84.3205 | 84.4176 | 79.5338 | 1.8583 | 1.8488 | 1.376
3.4792 | 84.2856 | 84.437 | 79.5532 | 1.8586 | 1.8491 | 1.3764
3.4833 | 84.3072 | 84.458 | 79.5733 | 1.859 | 1.8494 | 1.3768
3.4875 | 84.2508 | 84.4888 | 79.5597 | 1.8589 | 1.849 | 1.3767
3.4917 | 84.2448 | 84.5258 | 79.5582 | 1.8587 | 1.8486 | 1.3765
3.4958 | 84.3259 | 84.5974 | 79.6104 | 1.8584 | 1.8481 | 1.3764
3.5 | 84.4289 | 84.6626 | 79.6559 | 1.8579 | 1.8477 | 1.3762
3.5042 | 84.5339 | 84.5853 | 79.6211 | 1.8581 | 1.8478 | 1.3765
3.5083 | 84.5658 | 84.5022 | 79.5741 | 1.8581 | 1.8478 | 1.3768
3.5125 | 84.578 | 84.4891 | 79.5616 | 1.8581 | 1.8469 | 1.3764
3.5167 | 84.5704 | 84.4809 | 79.5624 | 1.8573 | 1.8461 | 1.3759
3.5208 | 84.5373 | 84.5392 | 79.611 | 1.8569 | 1.8463 | 1.376
3.525 | 84.5433 | 84.5962 | 79.6609 | 1.8567 | 1.8466 | 1.3763
3.5292 | 84.5366 | 84.4861 | 79.6196 | 1.8566 | 1.8467 | 1.3763
3.5333 | 84.4668 | 84.369 | 79.5643 | 1.8565 | 1.8469 | 1.3763
3.5375 | 84.4182 | 84.3332 | 79.5618 | 1.8568 | 1.847 | 1.3761
3.5417 | 84.3595 | 84.2975 | 79.5671 | 1.8568 | 1.847 | 1.3759
3.5458 | 84.2626 | 84.3124 | 79.5825 | 1.8569 | 1.8479 | 1.3761
3.55 | 84.19 | 84.3341 | 79.6049 | 1.8572 | 1.8489 | 1.3763
3.5542 | 84.161 | 84.2676 | 79.5915 | 1.8575 | 1.8497 | 1.3763
3.5583 | 84.0975 | 84.1966 | 79.5666 | 1.8579 | 1.8506 | 1.3763
3.5625 | 84.0521 | 84.1504 | 79.5612 | 1.8591 | 1.8517 | 1.3764
3.5667 | 84.013 | 84.1016 | 79.5584 | 1.8602 | 1.8527 | 1.3764
3.5708 | 83.9448 | 84.0977 | 79.5568 | 1.8612 | 1.854 | 1.3765
3.575 | 83.9096 | 84.1021 | 79.5633 | 1.8624 | 1.8554 | 1.3766
3.5792 | 83.9159 | 84.0848 | 79.5707 | 1.8637 | 1.8568 | 1.3766
3.5833 | 83.9029 | 84.0649 | 79.5693 | 1.8651 | 1.8583 | 1.3767
3.5875 | 83.8506 | 84.0137 | 79.5547 | 1.8668 | 1.86 | 1.3769
3.5917 | 83.8035 | 83.9604 | 79.5396 | 1.8685 | 1.8615 | 1.377
3.5958 | 83.7732 | 83.9613 | 79.5378 | 1.8698 | 1.863 | 1.377
3.6 | 83.7621 | 83.9676 | 79.5417 | 1.8713 | 1.8645 | 1.377
3.6042 | 83.7812 | 83.9723 | 79.5511 | 1.8731 | 1.8663 | 1.3772
3.6083 | 83.7887 | 83.9757 | 79.5562 | 1.8749 | 1.8681 | 1.3774
3.6125 | 83.7375 | 83.9276 | 79.5374 | 1.8766 | 1.8698 | 1.3775
3.6167 | 83.6911 | 83.8789 | 79.5192 | 1.8784 | 1.8715 | 1.3776
3.6208 | 83.6883 | 83.8902 | 79.5236 | 1.8798 | 1.873 | 1.3776
3.625 | 83.6926 | 83.9034 | 79.5302 | 1.8813 | 1.8745 | 1.3777
3.6292 | 83.7098 | 83.9099 | 79.5351 | 1.8831 | 1.8764 | 1.3779
3.6333 | 83.7176 | 83.9164 | 79.538 | 1.8849 | 1.8782 | 1.3781
3.6375 | 83.6789 | 83.8794 | 79.5226 | 1.8865 | 1.8798 | 1.3781
3.6417 | 83.6398 | 83.8424 | 79.508 | 1.8881 | 1.8813 | 1.3782
3.6458 | 83.6476 | 83.858 | 79.5148 | 1.8894 | 1.8828 | 1.3783
3.65 | 83.6596 | 83.8732 | 79.5217 | 1.8909 | 1.8843 | 1.3784
3.6542 | 83.6607 | 83.8727 | 79.5204 | 1.8926 | 1.886 | 1.3785
3.6583 | 83.6648 | 83.8731 | 79.5189 | 1.8942 | 1.8876 | 1.3787
3.6625 | 83.6367 | 83.8491 | 79.5091 | 1.8956 | 1.889 | 1.3788
3.6667 | 83.6131 | 83.8251 | 79.4998 | 1.897 | 1.8904 | 1.3788
3.6708 | 83.6216 | 83.84 | 79.5055 | 1.8983 | 1.8918 | 1.3789
3.675 | 83.6353 | 83.8537 | 79.5109 | 1.8997 | 1.8932 | 1.379
3.6792 | 83.6321 | 83.8511 | 79.5087 | 1.9011 | 1.8946 | 1.3791
3.6833 | 83.6328 | 83.8499 | 79.5068 | 1.9025 | 1.896 | 1.3793
3.6875 | 83.6187 | 83.838 | 79.5029 | 1.9037 | 1.8973 | 1.3793
3.6917 | 83.6074 | 83.8258 | 79.4987 | 1.9049 | 1.8985 | 1.3794
3.6958 | 83.6109 | 83.8347 | 79.5016 | 1.9061 | 1.8997 | 1.3795
3.7 | 83.6188 | 83.8425 | 79.5041 | 1.9073 | 1.9009 | 1.3796
3.7042 | 83.6108 | 83.8341 | 79.4995 | 1.9085 | 1.9022 | 1.3797
3.7083 | 83.6032 | 83.8268 | 79.4952 | 1.9097 | 1.9034 | 1.3798
3.7125 | 83.5991 | 83.8209 | 79.4933 | 1.9108 | 1.9044 | 1.3798
3.7167 | 83.5924 | 83.8147 | 79.4913 | 1.9118 | 1.9055 | 1.3799
3.7208 | 83.5986 | 83.8223 | 79.4938 | 1.9129 | 1.9066 | 1.38
3.725 | 83.6045 | 83.8292 | 79.4964 | 1.914 | 1.9077 | 1.38
3.7292 | 83.5946 | 83.8197 | 79.4921 | 1.915 | 1.9087 | 1.3801
3.7333 | 83.5849 | 83.811 | 79.4878 | 1.9161 | 1.9098 | 1.3802
3.7375 | 83.5797 | 83.8053 | 79.486 | 1.917 | 1.9107 | 1.3803
3.7417 | 83.5738 | 83.7991 | 79.484 | 1.9179 | 1.9117 | 1.3803
3.7458 | 83.576 | 83.8012 | 79.4842 | 1.9189 | 1.9127 | 1.3804
3.75 | 83.5795 | 83.8029 | 79.4849 | 1.9199 | 1.9136 | 1.3805
3.7542 | 83.5694 | 83.7955 | 79.4822 | 1.9208 | 1.9146 | 1.3806
3.7583 | 83.5636 | 83.7886 | 79.4796 | 1.9217 | 1.9155 | 1.3806
3.7625 | 83.5569 | 83.7827 | 79.4777 | 1.9226 | 1.9164 | 1.3807
3.7667 | 83.5489 | 83.7763 | 79.4756 | 1.9235 | 1.9173 | 1.3808
3.7708 | 83.55 | 83.7741 | 79.4744 | 1.9244 | 1.9182 | 1.3809
3.775 | 83.5454 | 83.7718 | 79.4735 | 1.9252 | 1.9191 | 1.3809
3.7792 | 83.5422 | 83.7666 | 79.4719 | 1.9261 | 1.9199 | 1.381
3.7833 | 83.5375 | 83.7617 | 79.4703 | 1.927 | 1.9208 | 1.3811
3.7875 | 83.5315 | 83.7564 | 79.4686 | 1.9278 | 1.9216 | 1.3812
3.7917 | 83.5276 | 83.751 | 79.4667 | 1.9286 | 1.9225 | 1.3812
3.7958 | 83.5238 | 83.7475 | 79.4651 | 1.9295 | 1.9233 | 1.3813
3.8 | 83.5182 | 83.7439 | 79.4638 | 1.9303 | 1.9241 | 1.3814
3.8042 | 83.5177 | 83.7404 | 79.4627 | 1.931 | 1.9249 | 1.3815
3.8083 | 83.5129 | 83.737 | 79.4616 | 1.9318 | 1.9257 | 1.3815
3.8125 | 83.5093 | 83.7328 | 79.4602 | 1.9326 | 1.9265 | 1.3816
3.8167 | 83.5051 | 83.7285 | 79.4585 | 1.9334 | 1.9272 | 1.3817
3.8208 | 83.5017 | 83.7248 | 79.457 | 1.9341 | 1.928 | 1.3818
3.825 | 83.4966 | 83.7212 | 79.4556 | 1.9349 | 1.9287 | 1.3818
3.8292 | 83.495 | 83.7185 | 79.4547 | 1.9356 | 1.9295 | 1.3819
3.8333 | 83.4955 | 83.716 | 79.4538 | 1.9363 | 1.9302 | 1.382
3.8375 | 83.4878 | 83.7128 | 79.4526 | 1.937 | 1.9309 | 1.382
3.8417 | 83.4879 | 83.7096 | 79.4514 | 1.9377 | 1.9316 | 1.3821
3.8458 | 83.4828 | 83.7066 | 79.45 | 1.9384 | 1.9323 | 1.3822
3.85 | 83.4779 | 83.704 | 79.4487 | 1.9391 | 1.9329 | 1.3822
3.8542 | 83.4775 | 83.7027 | 79.4478 | 1.9397 | 1.9336 | 1.3823
3.8583 | 83.4771 | 83.7017 | 79.447 | 1.9404 | 1.9342 | 1.3824
3.8625 | 83.47 | 83.7003 | 79.446 | 1.941 | 1.9348 | 1.3824
3.8667 | 83.4738 | 83.6985 | 79.445 | 1.9416 | 1.9354 | 1.3825
3.8708 | 83.47 | 83.6957 | 79.4439 | 1.9422 | 1.936 | 1.3826
3.875 | 83.4677 | 83.6917 | 79.4428 | 1.9428 | 1.9366 | 1.3826
3.8792 | 83.4679 | 83.6872 | 79.4416 | 1.9435 | 1.9372 | 1.3827
3.8833 | 83.4633 | 83.682 | 79.4405 | 1.944 | 1.9377 | 1.3827
3.8875 | 83.4586 | 83.6774 | 79.4394 | 1.9446 | 1.9383 | 1.3828
3.8917 | 83.4597 | 83.6736 | 79.4383 | 1.9451 | 1.9389 | 1.3828
3.8958 | 83.457 | 83.67 | 79.4374 | 1.9457 | 1.9394 | 1.3829
3.9 | 83.4538 | 83.6664 | 79.4365 | 1.9462 | 1.94 | 1.383
3.9042 | 83.454 | 83.6621 | 79.4356 | 1.9468 | 1.9406 | 1.383
3.9083 | 83.4505 | 83.6572 | 79.4347 | 1.9472 | 1.9411 | 1.3831
3.9125 | 83.4494 | 83.6526 | 79.4337 | 1.9478 | 1.9417 | 1.3831
3.9167 | 83.4492 | 83.6486 | 79.4327 | 1.9483 | 1.9422 | 1.3832
3.9208 | 83.4458 | 83.6445 | 79.4315 | 1.9488 | 1.9427 | 1.3832
3.925 | 83.4411 | 83.6408 | 79.4304 | 1.9493 | 1.9433 | 1.3833
3.9292 | 83.4402 | 83.6377 | 79.4298 | 1.9497 | 1.9438 | 1.3833
3.9333 | 83.438 | 83.6343 | 79.4293 | 1.9502 | 1.9443 | 1.3834
3.9375 | 83.4396 | 83.63 | 79.4286 | 1.9507 | 1.9449 | 1.3834
3.9417 | 83.4381 | 83.6273 | 79.4279 | 1.9511 | 1.9454 | 1.3835
3.9458 | 83.435 | 83.6246 | 79.4269 | 1.9516 | 1.9459 | 1.3835
3.95 | 83.4318 | 83.6216 | 79.4258 | 1.952 | 1.9464 | 1.3836
3.9542 | 83.4312 | 83.6201 | 79.425 | 1.9524 | 1.9469 | 1.3836
3.9583 | 83.429 | 83.6172 | 79.4243 | 1.9528 | 1.9474 | 1.3837
3.9625 | 83.4334 | 83.6154 | 79.4237 | 1.9532 | 1.9478 | 1.3837
3.9667 | 83.43 | 83.6137 | 79.4232 | 1.9536 | 1.9483 | 1.3838
3.9708 | 83.4263 | 83.6106 | 79.4225 | 1.954 | 1.9488 | 1.3838
3.975 | 83.4253 | 83.6086 | 79.4218 | 1.9544 | 1.9492 | 1.3838
3.9792 | 83.4199 | 83.6058 | 79.4212 | 1.9547 | 1.9496 | 1.3839
3.9833 | 83.4249 | 83.6037 | 79.4206 | 1.9551 | 1.9501 | 1.3839
3.9875 | 83.4273 | 83.6043 | 79.4201 | 1.9555 | 1.9505 | 1.384
3.9917 | 83.4233 | 83.6032 | 79.4197 | 1.9558 | 1.9509 | 1.384
3.9958 | 83.4252 | 83.6012 | 79.419 | 1.9562 | 1.9513 | 1.384
4 | 83.421 | 83.5994 | 79.4183 | 1.9565 | 1.9517 | 1.3841
4.0042 | 83.4185 | 83.5959 | 79.4175 | 1.9568 | 1.9521 | 1.3841
4.0083 | 83.4194 | 83.5934 | 79.4166 | 1.9571 | 1.9524 | 1.3842
4.0125 | 83.4202 | 83.5927 | 79.4161 | 1.9574 | 1.9528 | 1.3842
4.0167 | 83.414 | 83.5913 | 79.4156 | 1.9577 | 1.9532 | 1.3842
4.0208 | 83.4126 | 83.5907 | 79.4152 | 1.958 | 1.9535 | 1.3843
4.025 | 83.4157 | 83.5895 | 79.415 | 1.9583 | 1.9539 | 1.3843
4.0292 | 83.4111 | 83.5862 | 79.4142 | 1.9586 | 1.9542 | 1.3843
4.0333 | 83.4141 | 83.5839 | 79.4133 | 1.9589 | 1.9545 | 1.3844
4.0375 | 83.4154 | 83.5816 | 79.4126 | 1.9592 | 1.9549 | 1.3844
4.0417 | 83.4056 | 83.5797 | 79.4119 | 1.9595 | 1.9552 | 1.3844
4.0458 | 83.4051 | 83.5789 | 79.4114 | 1.9597 | 1.9555 | 1.3845
4.05 | 83.4071 | 83.5774 | 79.4101 | 1.96 | 1.9558 | 1.3845
4.0542 | 83.4001 | 83.5748 | 79.4095 | 1.9602 | 1.9561 | 1.3845
4.0583 | 83.4081 | 83.5727 | 79.4091 | 1.9605 | 1.9564 | 1.3846
4.0625 | 83.4049 | 83.5699 | 79.4085 | 1.9608 | 1.9567 | 1.3846
4.0667 | 83.3987 | 83.5679 | 79.4084 | 1.9611 | 1.957 | 1.3846
4.0708 | 83.3969 | 83.5668 | 79.4079 | 1.9613 | 1.9573 | 1.3847
4.075 | 83.3977 | 83.565 | 79.4075 | 1.9615 | 1.9576 | 1.3847
4.0792 | 83.393 | 83.5631 | 79.4071 | 1.9618 | 1.9579 | 1.3847
4.0833 | 83.399 | 83.5614 | 79.4061 | 1.962 | 1.9582 | 1.3847
4.0875 | 83.3983 | 83.559 | 79.4054 | 1.9623 | 1.9585 | 1.3848
4.0917 | 83.3913 | 83.5571 | 79.4042 | 1.9625 | 1.9588 | 1.3848
4.0958 | 83.3922 | 83.5558 | 79.4036 | 1.9628 | 1.959 | 1.3848
4.1 | 83.3889 | 83.554 | 79.4043 | 1.963 | 1.9593 | 1.3849
4.1042 | 83.3875 | 83.5523 | 79.4041 | 1.9632 | 1.9596 | 1.3849
4.1083 | 83.3912 | 83.5506 | 79.4033 | 1.9634 | 1.9598 | 1.3849
4.1125 | 83.3889 | 83.5486 | 79.4028 | 1.9637 | 1.9601 | 1.3849
4.1167 | 83.3864 | 83.5469 | 79.4018 | 1.9639 | 1.9603 | 1.385
4.1208 | 83.3859 | 83.5457 | 79.4012 | 1.9641 | 1.9606 | 1.385
4.125 | 83.3811 | 83.5442 | 79.4012 | 1.9643 | 1.9608 | 1.385
4.1292 | 83.3844 | 83.5423 | 79.4007 | 1.9645 | 1.9611 | 1.3851
4.1333 | 83.3837 | 83.5404 | 79.4003 | 1.9647 | 1.9613 | 1.3851
4.1375 | 83.3837 | 83.5383 | 79.3999 | 1.9649 | 1.9616 | 1.3851
4.1417 | 83.3809 | 83.5366 | 79.3989 | 1.9651 | 1.9618 | 1.3851
4.1458 | 83.3794 | 83.5354 | 79.3984 | 1.9653 | 1.962 | 1.3852
4.15 | 83.3755 | 83.534 | 79.3979 | 1.9655 | 1.9622 | 1.3852
4.1542 | 83.3763 | 83.5324 | 79.3974 | 1.9657 | 1.9625 | 1.3852
4.1583 | 83.3798 | 83.5308 | 79.3973 | 1.9659 | 1.9627 | 1.3852
4.1625 | 83.3754 | 83.5287 | 79.3969 | 1.9661 | 1.9629 | 1.3853
4.1667 | 83.3767 | 83.5268 | 79.396 | 1.9663 | 1.9631 | 1.3853
4.1708 | 83.3703 | 83.5253 | 79.3955 | 1.9665 | 1.9634 | 1.3853
4.175 | 83.3649 | 83.5237 | 79.3947 | 1.9667 | 1.9636 | 1.3853
4.1792 | 83.3652 | 83.5221 | 79.3942 | 1.9668 | 1.9638 | 1.3854
4.1833 | 83.3652 | 83.5205 | 79.3941 | 1.967 | 1.964 | 1.3854
4.1875 | 83.3667 | 83.5187 | 79.3936 | 1.9672 | 1.9642 | 1.3854
4.1917 | 83.3703 | 83.5168 | 79.3929 | 1.9674 | 1.9644 | 1.3854
4.1958 | 83.3657 | 83.5153 | 79.3924 | 1.9676 | 1.9646 | 1.3855
4.2 | 83.3634 | 83.5137 | 79.3917 | 1.9678 | 1.9648 | 1.3855
4.2042 | 83.3621 | 83.5126 | 79.3913 | 1.9679 | 1.965 | 1.3855
4.2083 | 83.3611 | 83.5114 | 79.3912 | 1.9681 | 1.9652 | 1.3855
4.2125 | 83.3616 | 83.5098 | 79.3908 | 1.9683 | 1.9654 | 1.3856
4.2167 | 83.3619 | 83.5082 | 79.3902 | 1.9684 | 1.9656 | 1.3856
4.2208 | 83.359 | 83.5067 | 79.3897 | 1.9686 | 1.9658 | 1.3856
4.225 | 83.3563 | 83.5051 | 79.389 | 1.9688 | 1.966 | 1.3856
4.2292 | 83.3564 | 83.5039 | 79.3885 | 1.9689 | 1.9662 | 1.3857
4.2333 | 83.3535 | 83.5027 | 79.3883 | 1.9691 | 1.9664 | 1.3857
4.2375 | 83.3537 | 83.5004 | 79.3871 | 1.9693 | 1.9666 | 1.3857
4.2417 | 83.3516 | 83.4981 | 79.3858 | 1.9695 | 1.9668 | 1.3857
4.2458 | 83.3481 | 83.4959 | 79.3845 | 1.9696 | 1.967 | 1.3858
4.25 | 83.3487 | 83.4936 | 79.3831 | 1.9698 | 1.9671 | 1.3858
4.2542 | 83.3438 | 83.4892 | 79.379 | 1.97 | 1.9674 | 1.3859
4.2583 | 83.3407 | 83.4849 | 79.3754 | 1.9702 | 1.9676 | 1.3859
4.2625 | 83.3413 | 83.4839 | 79.3743 | 1.9704 | 1.9677 | 1.386
4.2667 | 83.3395 | 83.4827 | 79.3732 | 1.9705 | 1.9679 | 1.386
4.2708 | 83.3372 | 83.4841 | 79.371 | 1.9708 | 1.9681 | 1.3861
4.275 | 83.3399 | 83.4856 | 79.3699 | 1.9709 | 1.9683 | 1.3862
4.2792 | 83.3596 | 83.5111 | 79.391 | 1.9709 | 1.9683 | 1.386
4.2833 | 83.3863 | 83.5356 | 79.4118 | 1.9708 | 1.9682 | 1.3859
4.2875 | 83.3926 | 83.5353 | 79.4137 | 1.971 | 1.9684 | 1.386
4.2917 | 83.403 | 83.536 | 79.415 | 1.9712 | 1.9686 | 1.3861
4.2958 | 83.4286 | 83.5205 | 79.4208 | 1.9709 | 1.9685 | 1.3857
4.3 | 83.4381 | 83.5047 | 79.423 | 1.9707 | 1.9684 | 1.3854
4.3042 | 83.4081 | 83.4197 | 79.3709 | 1.9715 | 1.9692 | 1.386
4.3083 | 83.3526 | 83.3358 | 79.3185 | 1.9722 | 1.9701 | 1.3865
4.3125 | 83.2743 | 83.3144 | 79.3065 | 1.972 | 1.9702 | 1.3862
4.3167 | 83.2427 | 83.2916 | 79.2972 | 1.972 | 1.9703 | 1.3859
4.3208 | 83.1946 | 83.3329 | 79.308 | 1.9727 | 1.9715 | 1.3867
4.325 | 83.1582 | 83.373 | 79.3222 | 1.9741 | 1.9725 | 1.3875
4.3292 | 83.193 | 83.4387 | 79.3507 | 1.9741 | 1.9721 | 1.3869
4.3333 | 83.2036 | 83.5045 | 79.3789 | 1.9742 | 1.9718 | 1.3864
4.3375 | 83.2577 | 83.5042 | 79.3904 | 1.9748 | 1.9725 | 1.387
4.3417 | 83.313 | 83.5023 | 79.3952 | 1.9759 | 1.9732 | 1.3875
4.3458 | 83.3021 | 83.4204 | 79.3378 | 1.9759 | 1.973 | 1.3873
4.35 | 83.2398 | 83.3413 | 79.2809 | 1.9762 | 1.9728 | 1.387
4.3542 | 83.2311 | 83.4061 | 79.3196 | 1.9766 | 1.973 | 1.3872
4.3583 | 83.2304 | 83.4696 | 79.3621 | 1.9769 | 1.9731 | 1.3873
4.3625 | 83.1644 | 83.4993 | 79.3535 | 1.9776 | 1.9733 | 1.3875
4.3667 | 83.1655 | 83.533 | 79.3493 | 1.9782 | 1.9734 | 1.3877
4.3708 | 83.1856 | 83.5536 | 79.3626 | 1.9785 | 1.9729 | 1.3874
4.375 | 83.2342 | 83.574 | 79.3704 | 1.9784 | 1.9724 | 1.3871
4.3792 | 83.3264 | 83.5589 | 79.3648 | 1.9787 | 1.9725 | 1.3875
4.3833 | 83.3778 | 83.5416 | 79.3539 | 1.9789 | 1.9725 | 1.3878
4.3875 | 83.4073 | 83.5534 | 79.3399 | 1.9791 | 1.9718 | 1.3875
4.3917 | 83.4538 | 83.5697 | 79.3362 | 1.9789 | 1.9711 | 1.3872
4.3958 | 83.4695 | 83.6279 | 79.3789 | 1.9788 | 1.9708 | 1.3872
4.4 | 83.5468 | 83.6826 | 79.4191 | 1.9787 | 1.9706 | 1.3873
4.4042 | 83.6116 | 83.597 | 79.3847 | 1.9784 | 1.9705 | 1.3874
4.4083 | 83.6168 | 83.5096 | 79.3402 | 1.978 | 1.9705 | 1.3876
4.4125 | 83.6405 | 83.4988 | 79.3365 | 1.9778 | 1.9699 | 1.3873
4.4167 | 83.6477 | 83.488 | 79.3419 | 1.9772 | 1.9694 | 1.387
4.4208 | 83.5837 | 83.5249 | 79.3694 | 1.977 | 1.9698 | 1.3872
4.425 | 83.5513 | 83.5612 | 79.3996 | 1.9768 | 1.9701 | 1.3874
4.4292 | 83.5488 | 83.4767 | 79.3749 | 1.9765 | 1.9703 | 1.3874
4.4333 | 83.4981 | 83.3921 | 79.3399 | 1.9763 | 1.9706 | 1.3873
4.4375 | 83.4818 | 83.364 | 79.3398 | 1.9767 | 1.9709 | 1.3873
4.4417 | 83.4437 | 83.3321 | 79.3451 | 1.9768 | 1.9711 | 1.3872
4.4458 | 83.3599 | 83.3426 | 79.3527 | 1.9769 | 1.9719 | 1.3873
4.45 | 83.2948 | 83.3548 | 79.3665 | 1.9771 | 1.9726 | 1.3874
4.4542 | 83.2488 | 83.3085 | 79.363 | 1.977 | 1.9734 | 1.3874
4.4583 | 83.2216 | 83.2623 | 79.3499 | 1.9774 | 1.9742 | 1.3874
4.4625 | 83.167 | 83.2203 | 79.3437 | 1.978 | 1.9751 | 1.3875
4.4667 | 83.1309 | 83.1749 | 79.3386 | 1.9789 | 1.976 | 1.3875
4.4708 | 83.0966 | 83.1766 | 79.3383 | 1.9795 | 1.977 | 1.3875
4.475 | 83.0638 | 83.1795 | 79.3443 | 1.9803 | 1.9779 | 1.3876
4.4792 | 83.0645 | 83.165 | 79.3507 | 1.9812 | 1.9791 | 1.3876
4.4833 | 83.0621 | 83.1496 | 79.351 | 1.9822 | 1.9803 | 1.3877
4.4875 | 83.013 | 83.1009 | 79.3377 | 1.9834 | 1.9815 | 1.3878
4.4917 | 82.9718 | 83.0512 | 79.3251 | 1.9847 | 1.9827 | 1.3879
4.4958 | 82.9582 | 83.057 | 79.3273 | 1.9855 | 1.9837 | 1.3878
4.5 | 82.9489 | 83.0605 | 79.3333 | 1.9866 | 1.9848 | 1.3878
4.5042 | 82.9652 | 83.0533 | 79.3405 | 1.9878 | 1.9861 | 1.388
4.5083 | 82.9723 | 83.0448 | 79.3442 | 1.9892 | 1.9874 | 1.3881
4.5125 | 82.9296 | 82.9894 | 79.3298 | 1.9903 | 1.9885 | 1.3881
4.5167 | 82.8891 | 82.9366 | 79.3162 | 1.9916 | 1.9895 | 1.3882
4.5208 | 82.8909 | 82.9392 | 79.3216 | 1.9926 | 1.9905 | 1.3882
4.525 | 82.8937 | 82.9392 | 79.3285 | 1.9937 | 1.9914 | 1.3882
4.5292 | 82.9045 | 82.927 | 79.3306 | 1.995 | 1.9926 | 1.3883
4.5333 | 82.9093 | 82.9151 | 79.3314 | 1.9963 | 1.9938 | 1.3885
4.5375 | 82.8766 | 82.8699 | 79.3198 | 1.9974 | 1.9948 | 1.3885
4.5417 | 82.8433 | 82.8272 | 79.3089 | 1.9986 | 1.9957 | 1.3885
4.5458 | 82.8518 | 82.8306 | 79.3152 | 1.9996 | 1.9966 | 1.3886
4.55 | 82.8603 | 82.831 | 79.3217 | 2.0006 | 1.9975 | 1.3886
4.5542 | 82.866 | 82.8183 | 79.3219 | 2.0018 | 1.9986 | 1.3887
4.5583 | 82.8689 | 82.8072 | 79.322 | 2.003 | 1.9996 | 1.3888
4.5625 | 82.8498 | 82.7757 | 79.3157 | 2.004 | 2.0004 | 1.3888
4.5667 | 82.8301 | 82.7462 | 79.3094 | 2.005 | 2.0012 | 1.3889
4.5708 | 82.8338 | 82.746 | 79.3135 | 2.0059 | 2.002 | 1.3889
4.575 | 82.8434 | 82.7433 | 79.3174 | 2.0069 | 2.0028 | 1.3889
4.5792 | 82.8393 | 82.7272 | 79.3149 | 2.0079 | 2.0037 | 1.389
4.5833 | 82.8363 | 82.7129 | 79.3128 | 2.0089 | 2.0046 | 1.3891
4.5875 | 82.8273 | 82.6927 | 79.3099 | 2.0098 | 2.0053 | 1.3891
4.5917 | 82.8161 | 82.6734 | 79.307 | 2.0106 | 2.006 | 1.3891
4.5958 | 82.8227 | 82.6736 | 79.3107 | 2.0115 | 2.0068 | 1.3892
4.6 | 82.8323 | 82.6721 | 79.3143 | 2.0124 | 2.0075 | 1.3892
4.6042 | 82.8237 | 82.6546 | 79.3108 | 2.0132 | 2.0082 | 1.3893
4.6083 | 82.8174 | 82.639 | 79.3074 | 2.0141 | 2.009 | 1.3894
4.6125 | 82.8093 | 82.6239 | 79.3058 | 2.0149 | 2.0096 | 1.3894
4.6167 | 82.8048 | 82.609 | 79.3041 | 2.0156 | 2.0102 | 1.3894
4.6208 | 82.8077 | 82.6066 | 79.3061 | 2.0164 | 2.0109 | 1.3895
4.625 | 82.8176 | 82.603 | 79.3084 | 2.0172 | 2.0115 | 1.3895
4.6292 | 82.8071 | 82.5873 | 79.3057 | 2.0179 | 2.0121 | 1.3896
4.6333 | 82.7994 | 82.5731 | 79.3031 | 2.0186 | 2.0128 | 1.3896
4.6375 | 82.7931 | 82.56 | 79.3018 | 2.0193 | 2.0133 | 1.3896
4.6417 | 82.7842 | 82.5469 | 79.3004 | 2.02 | 2.0139 | 1.3897
4.6458 | 82.7866 | 82.5409 | 79.3007 | 2.0207 | 2.0145 | 1.3897
4.65 | 82.7889 | 82.5342 | 79.3014 | 2.0214 | 2.0151 | 1.3898
4.6542 | 82.7821 | 82.5213 | 79.2998 | 2.0221 | 2.0157 | 1.3898
4.6583 | 82.7791 | 82.5094 | 79.2982 | 2.0228 | 2.0162 | 1.3898
4.6625 | 82.7723 | 82.4977 | 79.2971 | 2.0234 | 2.0168 | 1.3899
4.6667 | 82.7692 | 82.4862 | 79.2958 | 2.0241 | 2.0173 | 1.3899
4.6708 | 82.7677 | 82.4783 | 79.2953 | 2.0247 | 2.0178 | 1.39
4.675 | 82.7656 | 82.47 | 79.295 | 2.0254 | 2.0184 | 1.39
4.6792 | 82.7621 | 82.4598 | 79.2941 | 2.026 | 2.0189 | 1.39
4.6833 | 82.756 | 82.45 | 79.2932 | 2.0266 | 2.0194 | 1.3901
4.6875 | 82.7544 | 82.4397 | 79.2923 | 2.0272 | 2.0199 | 1.3901
4.6917 | 82.747 | 82.4296 | 79.2911 | 2.0278 | 2.0204 | 1.3902
4.6958 | 82.7477 | 82.4212 | 79.2903 | 2.0284 | 2.0209 | 1.3902
4.7 | 82.7424 | 82.4125 | 79.2896 | 2.029 | 2.0214 | 1.3903
4.7042 | 82.7409 | 82.4038 | 79.2891 | 2.0295 | 2.0219 | 1.3903
4.7083 | 82.7396 | 82.3953 | 79.2886 | 2.0301 | 2.0224 | 1.3903
4.7125 | 82.7363 | 82.3863 | 79.2878 | 2.0307 | 2.0229 | 1.3904
4.7167 | 82.7312 | 82.3775 | 79.2868 | 2.0312 | 2.0233 | 1.3904
4.7208 | 82.7304 | 82.3698 | 79.286 | 2.0318 | 2.0238 | 1.3905
4.725 | 82.7242 | 82.3628 | 79.2852 | 2.0323 | 2.0242 | 1.3905
4.7292 | 82.7218 | 82.3571 | 79.2848 | 2.0328 | 2.0246 | 1.3905
4.7333 | 82.723 | 82.3522 | 79.2845 | 2.0334 | 2.0251 | 1.3906
4.7375 | 82.7159 | 82.3466 | 79.2839 | 2.0339 | 2.0255 | 1.3906
4.7417 | 82.7176 | 82.3405 | 79.2833 | 2.0344 | 2.0259 | 1.3906
4.7458 | 82.7169 | 82.3341 | 79.2826 | 2.0348 | 2.0262 | 1.3907
4.75 | 82.7144 | 82.3271 | 79.2818 | 2.0353 | 2.0266 | 1.3907
4.7542 | 82.7128 | 82.3201 | 79.2811 | 2.0358 | 2.027 | 1.3907
4.7583 | 82.7115 | 82.313 | 79.2805 | 2.0363 | 2.0274 | 1.3908
4.7625 | 82.7021 | 82.3062 | 79.2799 | 2.0367 | 2.0277 | 1.3908
4.7667 | 82.7064 | 82.2997 | 79.2792 | 2.0372 | 2.0281 | 1.3908
4.7708 | 82.7036 | 82.2934 | 79.2788 | 2.0376 | 2.0284 | 1.3909
4.775 | 82.6997 | 82.2868 | 79.2783 | 2.0381 | 2.0288 | 1.3909
4.7792 | 82.7034 | 82.2795 | 79.2777 | 2.0385 | 2.0291 | 1.3909
4.7833 | 82.6983 | 82.2717 | 79.277 | 2.0389 | 2.0295 | 1.391
4.7875 | 82.6959 | 82.2647 | 79.2764 | 2.0393 | 2.0298 | 1.391
4.7917 | 82.6982 | 82.2579 | 79.2756 | 2.0397 | 2.0302 | 1.391
4.7958 | 82.694 | 82.2509 | 79.2749 | 2.0401 | 2.0305 | 1.3911
4.8 | 82.6896 | 82.2443 | 79.2743 | 2.0405 | 2.0309 | 1.3911
4.8042 | 82.6892 | 82.2376 | 79.274 | 2.0409 | 2.0312 | 1.3911
4.8083 | 82.687 | 82.2308 | 79.2737 | 2.0412 | 2.0315 | 1.3912
4.8125 | 82.6847 | 82.2232 | 79.2732 | 2.0417 | 2.0319 | 1.3912
4.8167 | 82.687 | 82.2171 | 79.2727 | 2.042 | 2.0322 | 1.3912
4.8208 | 82.6839 | 82.2113 | 79.272 | 2.0424 | 2.0325 | 1.3913
4.825 | 82.6795 | 82.205 | 79.2712 | 2.0427 | 2.0328 | 1.3913
4.8292 | 82.6829 | 82.2004 | 79.2708 | 2.0431 | 2.0332 | 1.3913
4.8333 | 82.6768 | 82.1943 | 79.2703 | 2.0434 | 2.0335 | 1.3913
4.8375 | 82.6814 | 82.1882 | 79.2699 | 2.0437 | 2.0338 | 1.3914
4.8417 | 82.677 | 82.1832 | 79.2696 | 2.0441 | 2.0341 | 1.3914
4.8458 | 82.6745 | 82.1772 | 79.2691 | 2.0444 | 2.0344 | 1.3914
4.85 | 82.6718 | 82.1722 | 79.2686 | 2.0447 | 2.0347 | 1.3914
4.8542 | 82.6679 | 82.1674 | 79.2682 | 2.045 | 2.035 | 1.3915
4.8583 | 82.6724 | 82.1625 | 79.2679 | 2.0453 | 2.0353 | 1.3915
4.8625 | 82.6737 | 82.1596 | 79.2677 | 2.0456 | 2.0356 | 1.3915
4.8667 | 82.6708 | 82.1556 | 79.2674 | 2.0459 | 2.0358 | 1.3915
4.8708 | 82.6722 | 82.1505 | 79.267 | 2.0462 | 2.0361 | 1.3916
4.875 | 82.6668 | 82.1461 | 79.2664 | 2.0464 | 2.0364 | 1.3916
4.8792 | 82.6648 | 82.1408 | 79.2659 | 2.0467 | 2.0366 | 1.3916
4.8833 | 82.6672 | 82.1362 | 79.2654 | 2.0469 | 2.0369 | 1.3916
4.8875 | 82.6673 | 82.1339 | 79.2652 | 2.0472 | 2.0371 | 1.3917
4.8917 | 82.6638 | 82.1304 | 79.265 | 2.0474 | 2.0373 | 1.3917
4.8958 | 82.6632 | 82.1271 | 79.2648 | 2.0477 | 2.0376 | 1.3917
4.9 | 82.6619 | 82.1236 | 79.2649 | 2.0479 | 2.0378 | 1.3917
4.9042 | 82.6611 | 82.1185 | 79.2644 | 2.0481 | 2.038 | 1.3917
4.9083 | 82.6614 | 82.1144 | 79.2637 | 2.0484 | 2.0382 | 1.3918
4.9125 | 82.6654 | 82.1111 | 79.2633 | 2.0486 | 2.0385 | 1.3918
4.9167 | 82.6565 | 82.1077 | 79.2629 | 2.0488 | 2.0387 | 1.3918
4.9208 | 82.659 | 82.1051 | 79.2625 | 2.049 | 2.0389 | 1.3918
4.925 | 82.6559 | 82.1019 | 79.2617 | 2.0492 | 2.0391 | 1.3918
4.9292 | 82.653 | 82.0974 | 79.2613 | 2.0494 | 2.0393 | 1.3919
4.9333 | 82.6577 | 82.0936 | 79.2611 | 2.0497 | 2.0395 | 1.3919
4.9375 | 82.6575 | 82.0898 | 79.2607 | 2.0498 | 2.0397 | 1.3919
4.9417 | 82.6516 | 82.0863 | 79.261 | 2.0501 | 2.0399 | 1.3919
4.9458 | 82.6511 | 82.0839 | 79.2607 | 2.0503 | 2.0401 | 1.3919
4.95 | 82.6509 | 82.0807 | 79.26 | 2.0504 | 2.0402 | 1.392
4.9542 | 82.6455 | 82.0771 | 79.2597 | 2.0506 | 2.0404 | 1.392
4.9583 | 82.6513 | 82.0739 | 79.2592 | 2.0508 | 2.0406 | 1.392
4.9625 | 82.6516 | 82.0701 | 79.2587 | 2.051 | 2.0408 | 1.392
4.9667 | 82.6459 | 82.0669 | 79.2581 | 2.0512 | 2.041 | 1.392
4.9708 | 82.6449 | 82.0644 | 79.2578 | 2.0514 | 2.0411 | 1.392
4.975 | 82.6451 | 82.0613 | 79.2582 | 2.0516 | 2.0413 | 1.3921
4.9792 | 82.6394 | 82.0582 | 79.2582 | 2.0517 | 2.0415 | 1.3921
4.9833 | 82.6458 | 82.0554 | 79.2576 | 2.0519 | 2.0416 | 1.3921
4.9875 | 82.6435 | 82.0521 | 79.2572 | 2.0521 | 2.0418 | 1.3921
4.9917 | 82.6407 | 82.0492 | 79.2565 | 2.0523 | 2.042 | 1.3921
4.9958 | 82.6395 | 82.0469 | 79.2562 | 2.0525 | 2.0421 | 1.3921
5 | 82.6384 | 82.0441 | 79.2565 | 2.0526 | 2.0423 | 1.3922
5.0042 | 82.6355 | 82.0411 | 79.2563 | 2.0528 | 2.0424 | 1.3922
5.0083 | 82.6391 | 82.0382 | 79.2559 | 2.0529 | 2.0426 | 1.3922
5.0125 | 82.6378 | 82.0352 | 79.2556 | 2.0531 | 2.0427 | 1.3922
5.0167 | 82.634 | 82.0325 | 79.2549 | 2.0533 | 2.0429 | 1.3922
5.0208 | 82.6357 | 82.0304 | 79.2546 | 2.0534 | 2.043 | 1.3922
5.025 | 82.6326 | 82.028 | 79.2547 | 2.0535 | 2.0432 | 1.3923
5.0292 | 82.6337 | 82.0253 | 79.2544 | 2.0537 | 2.0433 | 1.3923
5.0333 | 82.6362 | 82.0227 | 79.2544 | 2.0538 | 2.0435 | 1.3923
5.0375 | 82.6353 | 82.0198 | 79.2541 | 2.054 | 2.0436 | 1.3923
5.0417 | 82.6324 | 82.0172 | 79.2535 | 2.0541 | 2.0437 | 1.3923
5.0458 | 82.63 | 82.0148 | 79.2531 | 2.0543 | 2.0439 | 1.3923
5.05 | 82.6238 | 82.0125 | 79.2528 | 2.0544 | 2.044 | 1.3923
5.0542 | 82.6253 | 82.0099 | 79.2525 | 2.0546 | 2.0442 | 1.3924
5.0583 | 82.6247 | 82.0073 | 79.2525 | 2.0547 | 2.0443 | 1.3924
5.0625 | 82.6268 | 82.0045 | 79.2522 | 2.0548 | 2.0444 | 1.3924
5.0667 | 82.628 | 82.0019 | 79.2517 | 2.055 | 2.0445 | 1.3924
5.0708 | 82.6261 | 81.9997 | 79.2514 | 2.0551 | 2.0447 | 1.3924
5.075 | 82.6216 | 81.9974 | 79.251 | 2.0553 | 2.0448 | 1.3924
5.0792 | 82.6227 | 81.9954 | 79.2508 | 2.0554 | 2.0449 | 1.3924
5.0833 | 82.6211 | 81.9933 | 79.2509 | 2.0555 | 2.0451 | 1.3925
5.0875 | 82.6206 | 81.9906 | 79.2506 | 2.0556 | 2.0452 | 1.3925
5.0917 | 82.6245 | 81.9879 | 79.2501 | 2.0558 | 2.0453 | 1.3925
5.0958 | 82.6183 | 81.9852 | 79.2496 | 2.0559 | 2.0454 | 1.3925
5.1 | 82.6164 | 81.9825 | 79.249 | 2.056 | 2.0455 | 1.3925
5.1042 | 82.6161 | 81.9811 | 79.2499 | 2.0561 | 2.0457 | 1.3925
5.1083 | 82.6154 | 81.9797 | 79.251 | 2.0563 | 2.0458 | 1.3925
5.1125 | 82.6125 | 81.9755 | 79.2502 | 2.0564 | 2.0459 | 1.3925
5.1167 | 82.6133 | 81.9715 | 79.2493 | 2.0566 | 2.046 | 1.3926
5.1208 | 82.6099 | 81.9675 | 79.249 | 2.0567 | 2.0462 | 1.3926
5.125 | 82.6082 | 81.9634 | 79.2484 | 2.0568 | 2.0463 | 1.3926
5.1292 | 82.597 | 81.9503 | 79.2387 | 2.057 | 2.0465 | 1.3927
5.1333 | 82.5866 | 81.9377 | 79.2296 | 2.0572 | 2.0467 | 1.3928
5.1375 | 82.5841 | 81.9356 | 79.2287 | 2.0574 | 2.0468 | 1.3928
5.1417 | 82.5848 | 81.9332 | 79.2279 | 2.0575 | 2.047 | 1.3928
5.1458 | 82.5757 | 81.937 | 79.2231 | 2.0579 | 2.0472 | 1.3929
5.15 | 82.5648 | 81.9402 | 79.2201 | 2.0582 | 2.0474 | 1.3931
5.1542 | 82.5939 | 81.9851 | 79.2518 | 2.0581 | 2.0471 | 1.3928
5.1583 | 82.6241 | 82.0278 | 79.2834 | 2.0579 | 2.0469 | 1.3925
5.1625 | 82.6233 | 82.0332 | 79.2867 | 2.0584 | 2.047 | 1.3928
5.1667 | 82.6402 | 82.0404 | 79.289 | 2.0587 | 2.0472 | 1.393
5.1708 | 82.6804 | 82.0181 | 79.292 | 2.058 | 2.0468 | 1.3924
5.175 | 82.705 | 81.9988 | 79.2917 | 2.0576 | 2.0464 | 1.3919
5.1792 | 82.7566 | 81.9174 | 79.2494 | 2.0582 | 2.0472 | 1.3925
5.1833 | 82.7303 | 81.84 | 79.207 | 2.059 | 2.048 | 1.3931
5.1875 | 82.6802 | 81.8209 | 79.1958 | 2.0592 | 2.0479 | 1.3926
5.1917 | 82.6096 | 81.8 | 79.1886 | 2.0588 | 2.0477 | 1.3922
5.1958 | 82.5435 | 81.8508 | 79.2163 | 2.0591 | 2.0486 | 1.3928
5.2 | 82.5096 | 81.8962 | 79.2453 | 2.0597 | 2.0494 | 1.3934
5.2042 | 82.5228 | 81.9059 | 79.2428 | 2.0595 | 2.0492 | 1.393
5.2083 | 82.5433 | 81.9157 | 79.239 | 2.0595 | 2.049 | 1.3927
5.2125 | 82.5951 | 81.9002 | 79.2512 | 2.0598 | 2.0495 | 1.393
5.2167 | 82.639 | 81.8858 | 79.2574 | 2.0604 | 2.0501 | 1.3933
5.2208 | 82.6246 | 81.8197 | 79.2106 | 2.0606 | 2.0503 | 1.3933
5.225 | 82.5449 | 81.7555 | 79.1665 | 2.0611 | 2.0505 | 1.3933
5.2292 | 82.5032 | 81.8202 | 79.2028 | 2.0613 | 2.0505 | 1.3932
5.2333 | 82.494 | 81.8792 | 79.2433 | 2.0615 | 2.0505 | 1.3931
5.2375 | 82.4248 | 81.893 | 79.2417 | 2.062 | 2.051 | 1.3935
5.2417 | 82.4335 | 81.9085 | 79.2388 | 2.0629 | 2.0515 | 1.3938
5.2458 | 82.4352 | 81.8875 | 79.2229 | 2.0634 | 2.0512 | 1.3935
5.25 | 82.4019 | 81.8699 | 79.2041 | 2.0639 | 2.0509 | 1.3933
5.2542 | 82.4281 | 81.903 | 79.2219 | 2.0645 | 2.051 | 1.3935
5.2583 | 82.4291 | 81.9329 | 79.2394 | 2.0653 | 2.0511 | 1.3937
5.2625 | 82.4165 | 81.952 | 79.2257 | 2.0658 | 2.0507 | 1.3936
5.2667 | 82.4493 | 81.9728 | 79.2178 | 2.0662 | 2.0504 | 1.3936
5.2708 | 82.4726 | 82.0096 | 79.2426 | 2.0664 | 2.05 | 1.3935
5.275 | 82.5338 | 82.0457 | 79.2637 | 2.0665 | 2.0497 | 1.3934
5.2792 | 82.6016 | 82.0064 | 79.2465 | 2.0666 | 2.0497 | 1.3936
5.2833 | 82.6422 | 81.9694 | 79.2237 | 2.0666 | 2.0496 | 1.3938
5.2875 | 82.6914 | 81.9796 | 79.2162 | 2.0667 | 2.049 | 1.3935
5.2917 | 82.7443 | 81.9885 | 79.2168 | 2.0666 | 2.0484 | 1.3933
5.2958 | 82.7534 | 82.0336 | 79.2467 | 2.0668 | 2.0483 | 1.3933
5.3 | 82.7894 | 82.0767 | 79.2759 | 2.0667 | 2.0483 | 1.3935
5.3042 | 82.8139 | 82.004 | 79.2497 | 2.0663 | 2.0483 | 1.3935
5.3083 | 82.83 | 81.9377 | 79.2158 | 2.0659 | 2.0482 | 1.3935
5.3125 | 82.8768 | 81.9333 | 79.2162 | 2.0655 | 2.048 | 1.3934
5.3167 | 82.884 | 81.9243 | 79.2234 | 2.0653 | 2.0477 | 1.3932
5.3208 | 82.866 | 81.9499 | 79.2394 | 2.065 | 2.048 | 1.3933
5.325 | 82.8273 | 81.9743 | 79.2587 | 2.0648 | 2.0483 | 1.3935
5.3292 | 82.7952 | 81.9144 | 79.2457 | 2.0644 | 2.0485 | 1.3934
5.3333 | 82.7801 | 81.8611 | 79.2238 | 2.0642 | 2.0488 | 1.3934
5.3375 | 82.7642 | 81.8385 | 79.2234 | 2.0642 | 2.049 | 1.3934
5.3417 | 82.7403 | 81.8119 | 79.2259 | 2.0644 | 2.0492 | 1.3934
5.3458 | 82.707 | 81.8206 | 79.2299 | 2.0645 | 2.0497 | 1.3934
5.35 | 82.6498 | 81.828 | 79.2392 | 2.0646 | 2.0502 | 1.3935
5.3542 | 82.6079 | 81.7948 | 79.2392 | 2.0646 | 2.0508 | 1.3934
5.3583 | 82.5569 | 81.7671 | 79.2319 | 2.0645 | 2.0513 | 1.3934
5.3625 | 82.5038 | 81.7344 | 79.2251 | 2.0648 | 2.0518 | 1.3935
5.3667 | 82.452 | 81.7017 | 79.2195 | 2.065 | 2.0523 | 1.3935
5.3708 | 82.4411 | 81.7164 | 79.2212 | 2.0654 | 2.0528 | 1.3935
5.375 | 82.4283 | 81.7268 | 79.2274 | 2.0658 | 2.0533 | 1.3935
5.3792 | 82.4288 | 81.72 | 79.2336 | 2.0664 | 2.054 | 1.3935
5.3833 | 82.4223 | 81.7147 | 79.2348 | 2.0671 | 2.0546 | 1.3936
5.3875 | 82.3743 | 81.6758 | 79.2238 | 2.0678 | 2.0551 | 1.3936
5.3917 | 82.3332 | 81.6397 | 79.2137 | 2.0686 | 2.0556 | 1.3937
5.3958 | 82.329 | 81.6524 | 79.2175 | 2.0691 | 2.0561 | 1.3936
5.4 | 82.3268 | 81.6603 | 79.2238 | 2.0698 | 2.0565 | 1.3936
5.4042 | 82.3376 | 81.6566 | 79.2281 | 2.0707 | 2.0572 | 1.3937
5.4083 | 82.341 | 81.6539 | 79.2294 | 2.0716 | 2.0578 | 1.3938
5.4125 | 82.3055 | 81.6167 | 79.218 | 2.0725 | 2.0583 | 1.3938
5.4167 | 82.2681 | 81.5832 | 79.2075 | 2.0733 | 2.0587 | 1.3938
5.4208 | 82.2732 | 81.5959 | 79.2132 | 2.074 | 2.0591 | 1.3938
5.425 | 82.2778 | 81.6034 | 79.2201 | 2.0747 | 2.0596 | 1.3938
5.4292 | 82.2872 | 81.6005 | 79.2225 | 2.0756 | 2.0602 | 1.3939
5.4333 | 82.2929 | 81.599 | 79.2238 | 2.0766 | 2.0607 | 1.394
5.4375 | 82.2668 | 81.5701 | 79.2157 | 2.0773 | 2.0611 | 1.394
5.4417 | 82.2414 | 81.5446 | 79.2081 | 2.0781 | 2.0616 | 1.394
5.4458 | 82.2458 | 81.5532 | 79.2127 | 2.0788 | 2.062 | 1.394
5.45 | 82.2518 | 81.5573 | 79.2174 | 2.0795 | 2.0623 | 1.394
5.4542 | 82.2555 | 81.5514 | 79.2172 | 2.0804 | 2.0629 | 1.3941
5.4583 | 82.2558 | 81.5472 | 79.2169 | 2.0812 | 2.0634 | 1.3941
5.4625 | 82.2428 | 81.5285 | 79.2125 | 2.0819 | 2.0637 | 1.3941
5.4667 | 82.224 | 81.512 | 79.2082 | 2.0826 | 2.0641 | 1.3941
5.4708 | 82.2338 | 81.5196 | 79.2126 | 2.0832 | 2.0644 | 1.3941
5.475 | 82.2409 | 81.5238 | 79.2168 | 2.0839 | 2.0648 | 1.3942
5.4792 | 82.2391 | 81.5147 | 79.2146 | 2.0846 | 2.0652 | 1.3942
5.4833 | 82.2346 | 81.5076 | 79.2125 | 2.0854 | 2.0657 | 1.3942
5.4875 | 82.2248 | 81.4958 | 79.2103 | 2.0859 | 2.0659 | 1.3942
5.4917 | 82.2185 | 81.485 | 79.2082 | 2.0865 | 2.0662 | 1.3942
5.4958 | 82.2235 | 81.4904 | 79.2114 | 2.0871 | 2.0666 | 1.3943
5.5 | 82.237 | 81.4935 | 79.2147 | 2.0877 | 2.0669 | 1.3943
5.5042 | 82.2294 | 81.4839 | 79.2123 | 2.0883 | 2.0673 | 1.3943
5.5083 | 82.2209 | 81.4762 | 79.21 | 2.089 | 2.0676 | 1.3944
5.5125 | 82.2127 | 81.4678 | 79.2088 | 2.0894 | 2.0679 | 1.3944
5.5167 | 82.2048 | 81.4596 | 79.2075 | 2.09 | 2.0681 | 1.3944
5.5208 | 82.2074 | 81.4615 | 79.2092 | 2.0905 | 2.0684 | 1.3944
5.525 | 82.2166 | 81.4619 | 79.211 | 2.0911 | 2.0687 | 1.3944
5.5292 | 82.2075 | 81.4537 | 79.2094 | 2.0916 | 2.069 | 1.3944
5.5333 | 82.2041 | 81.4469 | 79.2077 | 2.0921 | 2.0693 | 1.3945
5.5375 | 82.1978 | 81.4401 | 79.207 | 2.0926 | 2.0696 | 1.3945
5.5417 | 82.1941 | 81.4334 | 79.206 | 2.0931 | 2.0698 | 1.3945
5.5458 | 82.1938 | 81.4327 | 79.2065 | 2.0936 | 2.0701 | 1.3945
5.55 | 82.1987 | 81.4309 | 79.2074 | 2.0941 | 2.0704 | 1.3945
5.5542 | 82.191 | 81.4246 | 79.2064 | 2.0945 | 2.0706 | 1.3946
5.5583 | 82.1858 | 81.4193 | 79.2054 | 2.095 | 2.0709 | 1.3946
5.5625 | 82.1862 | 81.4136 | 79.2048 | 2.0955 | 2.0711 | 1.3946
5.5667 | 82.1778 | 81.4081 | 79.204 | 2.0959 | 2.0714 | 1.3946
5.5708 | 82.1789 | 81.4053 | 79.2039 | 2.0964 | 2.0716 | 1.3946
5.575 | 82.18 | 81.4019 | 79.204 | 2.0968 | 2.0719 | 1.3947
5.5792 | 82.1736 | 81.3964 | 79.2035 | 2.0972 | 2.0721 | 1.3947
5.5833 | 82.1729 | 81.3913 | 79.2031 | 2.0977 | 2.0724 | 1.3947
5.5875 | 82.1719 | 81.3857 | 79.2026 | 2.0981 | 2.0726 | 1.3947
5.5917 | 82.1654 | 81.3805 | 79.2019 | 2.0986 | 2.0729 | 1.3947
5.5958 | 82.1641 | 81.3771 | 79.2015 | 2.0989 | 2.0731 | 1.3948
5.6 | 82.1629 | 81.3741 | 79.2012 | 2.0994 | 2.0733 | 1.3948
5.6042 | 82.1554 | 81.3715 | 79.2011 | 2.0997 | 2.0735 | 1.3948
5.6083 | 82.1594 | 81.3697 | 79.2011 | 2.1002 | 2.0738 | 1.3948
5.6125 | 82.1551 | 81.367 | 79.2008 | 2.1005 | 2.074 | 1.3948
5.6167 | 82.1515 | 81.3639 | 79.2003 | 2.101 | 2.0742 | 1.3948
5.6208 | 82.1545 | 81.3611 | 79.1999 | 2.1013 | 2.0744 | 1.3949
5.625 | 82.1496 | 81.358 | 79.1995 | 2.1017 | 2.0746 | 1.3949
5.6292 | 82.1473 | 81.3552 | 79.1992 | 2.1021 | 2.0748 | 1.3949
5.6333 | 82.1489 | 81.3527 | 79.199 | 2.1024 | 2.0749 | 1.3949
5.6375 | 82.14 | 81.35 | 79.1987 | 2.1028 | 2.0751 | 1.3949
5.6417 | 82.1427 | 81.3473 | 79.1984 | 2.1031 | 2.0753 | 1.3949
5.6458 | 82.1407 | 81.3449 | 79.1982 | 2.1035 | 2.0755 | 1.395
5.65 | 82.1395 | 81.3421 | 79.198 | 2.1038 | 2.0756 | 1.395
5.6542 | 82.1384 | 81.3388 | 79.1976 | 2.1042 | 2.0758 | 1.395
5.6583 | 82.1372 | 81.3352 | 79.1972 | 2.1045 | 2.076 | 1.395
5.6625 | 82.131 | 81.3324 | 79.1969 | 2.1048 | 2.0761 | 1.395
5.6667 | 82.1348 | 81.3293 | 79.1964 | 2.1051 | 2.0763 | 1.395
5.6708 | 82.1333 | 81.3261 | 79.1962 | 2.1054 | 2.0765 | 1.3951
5.675 | 82.1308 | 81.3232 | 79.1959 | 2.1057 | 2.0766 | 1.3951
5.6792 | 82.1279 | 81.3197 | 79.1958 | 2.106 | 2.0768 | 1.3951
5.6833 | 82.1274 | 81.3163 | 79.1957 | 2.1063 | 2.0769 | 1.3951
5.6875 | 82.1213 | 81.3125 | 79.1954 | 2.1066 | 2.0771 | 1.3951
5.6917 | 82.1269 | 81.3095 | 79.1951 | 2.1069 | 2.0773 | 1.3951
5.6958 | 82.1255 | 81.3069 | 79.1947 | 2.1072 | 2.0774 | 1.3951
5.7 | 82.1232 | 81.3037 | 79.1942 | 2.1074 | 2.0776 | 1.3952
5.7042 | 82.1221 | 81.3017 | 79.194 | 2.1077 | 2.0778 | 1.3952
5.7083 | 82.118 | 81.2984 | 79.1939 | 2.1079 | 2.0779 | 1.3952
5.7125 | 82.119 | 81.2943 | 79.1936 | 2.1082 | 2.0781 | 1.3952
5.7167 | 82.1161 | 81.2918 | 79.1934 | 2.1084 | 2.0782 | 1.3952
5.7208 | 82.1176 | 81.2889 | 79.1931 | 2.1087 | 2.0784 | 1.3952
5.725 | 82.1147 | 81.2863 | 79.1928 | 2.109 | 2.0785 | 1.3952
5.7292 | 82.111 | 81.2844 | 79.1927 | 2.1092 | 2.0787 | 1.3953
5.7333 | 82.115 | 81.2818 | 79.1926 | 2.1094 | 2.0788 | 1.3953
5.7375 | 82.1148 | 81.2801 | 79.1925 | 2.1096 | 2.079 | 1.3953
5.7417 | 82.1133 | 81.2782 | 79.1924 | 2.1099 | 2.0791 | 1.3953
5.7458 | 82.1142 | 81.2751 | 79.1921 | 2.1101 | 2.0792 | 1.3953
5.75 | 82.1089 | 81.2728 | 79.1915 | 2.1103 | 2.0794 | 1.3953
5.7542 | 82.1066 | 81.2704 | 79.1913 | 2.1105 | 2.0795 | 1.3953
5.7583 | 82.1102 | 81.2681 | 79.1912 | 2.1107 | 2.0796 | 1.3953
5.7625 | 82.1092 | 81.2676 | 79.1912 | 2.1109 | 2.0798 | 1.3954
5.7667 | 82.1097 | 81.2661 | 79.1912 | 2.1111 | 2.0799 | 1.3954
5.7708 | 82.1079 | 81.2641 | 79.1911 | 2.1113 | 2.08 | 1.3954
5.775 | 82.1047 | 81.2624 | 79.1914 | 2.1115 | 2.0801 | 1.3954
5.7792 | 82.104 | 81.2597 | 79.1911 | 2.1117 | 2.0802 | 1.3954
5.7833 | 82.1051 | 81.2577 | 79.1906 | 2.1118 | 2.0803 | 1.3954
5.7875 | 82.1078 | 81.2569 | 79.1905 | 2.112 | 2.0805 | 1.3954
5.7917 | 82.1026 | 81.2555 | 79.1902 | 2.1122 | 2.0806 | 1.3954
5.7958 | 82.1048 | 81.2544 | 79.19 | 2.1123 | 2.0807 | 1.3954
5.8 | 82.1012 | 81.253 | 79.1898 | 2.1125 | 2.0808 | 1.3954
5.8042 | 82.0982 | 81.2504 | 79.1895 | 2.1126 | 2.0809 | 1.3955
5.8083 | 82.1034 | 81.2485 | 79.1894 | 2.1128 | 2.081 | 1.3955
5.8125 | 82.1021 | 81.2471 | 79.1893 | 2.1129 | 2.0811 | 1.3955
5.8167 | 82.0978 | 81.2455 | 79.1897 | 2.1131 | 2.0812 | 1.3955
5.8208 | 82.0979 | 81.2447 | 79.1896 | 2.1133 | 2.0812 | 1.3955
5.825 | 82.0975 | 81.2434 | 79.1889 | 2.1134 | 2.0813 | 1.3955
5.8292 | 82.095 | 81.2413 | 79.1886 | 2.1135 | 2.0814 | 1.3955
5.8333 | 82.0991 | 81.2397 | 79.1885 | 2.1137 | 2.0815 | 1.3955
5.8375 | 82.1011 | 81.238 | 79.1882 | 2.1138 | 2.0816 | 1.3955
5.8417 | 82.0929 | 81.2365 | 79.1881 | 2.114 | 2.0817 | 1.3955
5.8458 | 82.0936 | 81.2356 | 79.188 | 2.1141 | 2.0818 | 1.3955
5.85 | 82.0933 | 81.2342 | 79.1882 | 2.1142 | 2.0819 | 1.3955
5.8542 | 82.0894 | 81.2327 | 79.1882 | 2.1143 | 2.0819 | 1.3956
5.8583 | 82.0955 | 81.2315 | 79.1878 | 2.1145 | 2.082 | 1.3956
5.8625 | 82.0966 | 81.2298 | 79.1876 | 2.1146 | 2.0821 | 1.3956
5.8667 | 82.0897 | 81.2285 | 79.1873 | 2.1147 | 2.0822 | 1.3956
5.8708 | 82.0921 | 81.2277 | 79.1871 | 2.1149 | 2.0823 | 1.3956
5.875 | 82.089 | 81.2264 | 79.1875 | 2.115 | 2.0823 | 1.3956
5.8792 | 82.085 | 81.225 | 79.1875 | 2.1151 | 2.0824 | 1.3956
5.8833 | 82.0904 | 81.2237 | 79.1872 | 2.1152 | 2.0825 | 1.3956
5.8875 | 82.0878 | 81.2222 | 79.187 | 2.1153 | 2.0826 | 1.3956
5.8917 | 82.0864 | 81.221 | 79.1866 | 2.1155 | 2.0826 | 1.3956
5.8958 | 82.0878 | 81.2204 | 79.1865 | 2.1156 | 2.0827 | 1.3956
5.9 | 82.0869 | 81.2194 | 79.1868 | 2.1157 | 2.0828 | 1.3956
5.9042 | 82.0839 | 81.2182 | 79.1868 | 2.1158 | 2.0828 | 1.3956
5.9083 | 82.0897 | 81.2171 | 79.1867 | 2.1159 | 2.0829 | 1.3956
5.9125 | 82.086 | 81.2157 | 79.1866 | 2.116 | 2.083 | 1.3956
5.9167 | 82.085 | 81.2145 | 79.1862 | 2.1161 | 2.083 | 1.3957
5.9208 | 82.0842 | 81.2138 | 79.186 | 2.1162 | 2.0831 | 1.3957
5.925 | 82.079 | 81.2129 | 79.186 | 2.1163 | 2.0832 | 1.3957
5.9292 | 82.0795 | 81.2117 | 79.1859 | 2.1164 | 2.0832 | 1.3957
5.9333 | 82.0805 | 81.2105 | 79.186 | 2.1165 | 2.0833 | 1.3957
5.9375 | 82.0826 | 81.2089 | 79.1858 | 2.1166 | 2.0833 | 1.3957
5.9417 | 82.0825 | 81.2075 | 79.1854 | 2.1167 | 2.0834 | 1.3957
5.9458 | 82.0821 | 81.2064 | 79.1852 | 2.1168 | 2.0835 | 1.3957
5.95 | 82.0758 | 81.2053 | 79.1849 | 2.1169 | 2.0835 | 1.3957
5.9542 | 82.0767 | 81.2042 | 79.1851 | 2.117 | 2.0836 | 1.3957
5.9583 | 82.0753 | 81.2031 | 79.1855 | 2.117 | 2.0837 | 1.3957
5.9625 | 82.0778 | 81.2023 | 79.1866 | 2.1171 | 2.0837 | 1.3957
5.9667 | 82.0795 | 81.2017 | 79.1875 | 2.1172 | 2.0838 | 1.3957
5.9708 | 82.078 | 81.2009 | 79.1876 | 2.1173 | 2.0838 | 1.3957
5.975 | 82.0726 | 81.2 | 79.1877 | 2.1174 | 2.0839 | 1.3957
5.9792 | 82.0782 | 81.2034 | 79.1923 | 2.1174 | 2.0839 | 1.3957
5.9833 | 82.0811 | 81.2067 | 79.1969 | 2.1175 | 2.0839 | 1.3956
5.9875 | 82.0811 | 81.2036 | 79.1968 | 2.1176 | 2.084 | 1.3956
5.9917 | 82.0808 | 81.201 | 79.1965 | 2.1177 | 2.0841 | 1.3956
5.9958 | 82.0823 | 81.1973 | 79.1984 | 2.1177 | 2.0841 | 1.3955
6 | 82.0798 | 81.194 | 79.1995 | 2.1177 | 2.0841 | 1.3955
6.0042 | 82.0633 | 81.1708 | 79.1829 | 2.118 | 2.0843 | 1.3956
6.0083 | 82.044 | 81.1488 | 79.1667 | 2.1182 | 2.0846 | 1.3958
6.0125 | 82.0427 | 81.1464 | 79.1662 | 2.1182 | 2.0846 | 1.3957
6.0167 | 82.0398 | 81.1432 | 79.166 | 2.1182 | 2.0846 | 1.3956
6.0208 | 82.0181 | 81.1508 | 79.1599 | 2.1187 | 2.085 | 1.3959
6.025 | 82.0016 | 81.1559 | 79.1561 | 2.1192 | 2.0853 | 1.3962
6.0292 | 82.0227 | 81.2115 | 79.1914 | 2.119 | 2.0848 | 1.3957
6.0333 | 82.0445 | 81.2632 | 79.2268 | 2.1188 | 2.0844 | 1.3953
6.0375 | 82.0364 | 81.2716 | 79.2313 | 2.1196 | 2.0846 | 1.3957
6.0417 | 82.0453 | 81.2822 | 79.234 | 2.1201 | 2.0848 | 1.396
6.0458 | 82.0361 | 81.2538 | 79.2283 | 2.1198 | 2.0842 | 1.3954
6.05 | 82.0774 | 81.2312 | 79.2201 | 2.1191 | 2.0837 | 1.3948
6.0542 | 82.1438 | 81.1802 | 79.1973 | 2.1193 | 2.0843 | 1.3953
6.0583 | 82.1896 | 81.1332 | 79.1747 | 2.12 | 2.0849 | 1.3959
6.0625 | 82.1956 | 81.1258 | 79.1626 | 2.1202 | 2.0845 | 1.3954
6.0667 | 82.1522 | 81.1158 | 79.1551 | 2.1203 | 2.0842 | 1.3949
6.0708 | 82.0983 | 81.1718 | 79.1927 | 2.1205 | 2.0847 | 1.3953
6.075 | 82.0527 | 81.2223 | 79.2298 | 2.1206 | 2.0851 | 1.3957
6.0792 | 82.0415 | 81.1936 | 79.2073 | 2.1203 | 2.0851 | 1.3955
6.0833 | 82.0448 | 81.1686 | 79.1828 | 2.1199 | 2.085 | 1.3953
6.0875 | 82.1141 | 81.1532 | 79.1936 | 2.1199 | 2.0852 | 1.3953
6.0917 | 82.157 | 81.1392 | 79.201 | 2.12 | 2.0853 | 1.3953
6.0958 | 82.1972 | 81.1055 | 79.1758 | 2.1202 | 2.0857 | 1.3955
6.1 | 82.159 | 81.0705 | 79.1534 | 2.1208 | 2.0861 | 1.3957
6.1042 | 82.1311 | 81.1077 | 79.1734 | 2.1211 | 2.086 | 1.3955
6.1083 | 82.0788 | 81.1395 | 79.1963 | 2.1207 | 2.0859 | 1.3952
6.1125 | 82.0168 | 81.1387 | 79.2023 | 2.1209 | 2.0864 | 1.3956
6.1167 | 81.9895 | 81.1399 | 79.2044 | 2.1211 | 2.087 | 1.3959
6.1208 | 81.9784 | 81.098 | 79.1746 | 2.1212 | 2.0869 | 1.3957
6.125 | 81.9542 | 81.0596 | 79.1445 | 2.1218 | 2.0868 | 1.3955
6.1292 | 81.9376 | 81.1111 | 79.1728 | 2.1222 | 2.0869 | 1.3956
6.1333 | 81.9101 | 81.1556 | 79.2033 | 2.1228 | 2.087 | 1.3956
6.1375 | 81.8757 | 81.1644 | 79.1936 | 2.1233 | 2.0871 | 1.3958
6.1417 | 81.8706 | 81.1751 | 79.1854 | 2.124 | 2.0873 | 1.3959
6.1458 | 81.8704 | 81.1788 | 79.1892 | 2.1245 | 2.0869 | 1.3957
6.15 | 81.8785 | 81.1846 | 79.1901 | 2.1251 | 2.0867 | 1.3955
6.1542 | 81.8835 | 81.1876 | 79.1923 | 2.1258 | 2.0867 | 1.3957
6.1583 | 81.8853 | 81.1895 | 79.1924 | 2.1264 | 2.0868 | 1.3958
6.1625 | 81.8907 | 81.2014 | 79.1819 | 2.1268 | 2.0864 | 1.3957
6.1667 | 81.9189 | 81.2127 | 79.1767 | 2.127 | 2.086 | 1.3955
6.1708 | 81.9403 | 81.2463 | 79.1998 | 2.1274 | 2.0858 | 1.3955
6.175 | 81.9795 | 81.2795 | 79.2206 | 2.1276 | 2.0856 | 1.3955
6.1792 | 82.0127 | 81.236 | 79.2021 | 2.1276 | 2.0856 | 1.3956
6.1833 | 82.0377 | 81.1986 | 79.179 | 2.1275 | 2.0855 | 1.3957
6.1875 | 82.0938 | 81.2085 | 79.1766 | 2.1274 | 2.085 | 1.3956
6.1917 | 82.1353 | 81.2142 | 79.1807 | 2.1273 | 2.0846 | 1.3954
6.1958 | 82.1824 | 81.2476 | 79.2009 | 2.1276 | 2.0847 | 1.3954
6.2 | 82.2088 | 81.2796 | 79.2215 | 2.1277 | 2.0847 | 1.3955
6.2042 | 82.2216 | 81.2266 | 79.2042 | 2.1277 | 2.0847 | 1.3955
6.2083 | 82.2448 | 81.1824 | 79.1801 | 2.1275 | 2.0846 | 1.3955
6.2125 | 82.2708 | 81.1809 | 79.1818 | 2.1271 | 2.0845 | 1.3955
6.2167 | 82.3116 | 81.1738 | 79.1877 | 2.1267 | 2.0843 | 1.3954
6.2208 | 82.3305 | 81.1917 | 79.1968 | 2.1265 | 2.0845 | 1.3954
6.225 | 82.3307 | 81.2082 | 79.2095 | 2.1262 | 2.0847 | 1.3955
6.2292 | 82.3009 | 81.1685 | 79.2024 | 2.1259 | 2.0849 | 1.3954
6.2333 | 82.267 | 81.1377 | 79.1885 | 2.1256 | 2.085 | 1.3954
6.2375 | 82.2436 | 81.1247 | 79.1869 | 2.1255 | 2.0851 | 1.3954
6.2417 | 82.2236 | 81.1091 | 79.1874 | 2.1253 | 2.0853 | 1.3954
6.2458 | 82.2153 | 81.1273 | 79.1906 | 2.1252 | 2.0855 | 1.3954
6.25 | 82.2067 | 81.1412 | 79.198 | 2.1253 | 2.0857 | 1.3954
6.2542 | 82.1921 | 81.1269 | 79.2003 | 2.1253 | 2.086 | 1.3954
6.2583 | 82.1673 | 81.1173 | 79.197 | 2.1254 | 2.0863 | 1.3954
6.2625 | 82.1193 | 81.0937 | 79.1905 | 2.1256 | 2.0865 | 1.3954
6.2667 | 82.0697 | 81.0711 | 79.1854 | 2.1257 | 2.0867 | 1.3954
6.2708 | 82.0224 | 81.0873 | 79.1881 | 2.1255 | 2.0869 | 1.3954
6.275 | 81.9907 | 81.0983 | 79.194 | 2.1255 | 2.0871 | 1.3954
6.2792 | 81.9771 | 81.0941 | 79.1981 | 2.1256 | 2.0874 | 1.3954
6.2833 | 81.9641 | 81.0923 | 79.1982 | 2.1258 | 2.0878 | 1.3954
6.2875 | 81.9356 | 81.0636 | 79.1888 | 2.1262 | 2.088 | 1.3955
6.2917 | 81.9062 | 81.0381 | 79.1805 | 2.1266 | 2.0882 | 1.3955
6.2958 | 81.8957 | 81.0546 | 79.1853 | 2.1269 | 2.0884 | 1.3954
6.3 | 81.8893 | 81.065 | 79.192 | 2.1273 | 2.0885 | 1.3954
6.3042 | 81.8923 | 81.065 | 79.1956 | 2.1278 | 2.0889 | 1.3955
6.3083 | 81.8955 | 81.0669 | 79.197 | 2.1284 | 2.0892 | 1.3955
6.3125 | 81.8659 | 81.0402 | 79.1886 | 2.1289 | 2.0894 | 1.3955
6.3167 | 81.8427 | 81.0176 | 79.1807 | 2.1294 | 2.0896 | 1.3955
6.3208 | 81.8389 | 81.0304 | 79.1852 | 2.1298 | 2.0898 | 1.3955
6.325 | 81.8431 | 81.0376 | 79.1904 | 2.1303 | 2.0899 | 1.3955
6.3292 | 81.848 | 81.0371 | 79.1922 | 2.1309 | 2.0903 | 1.3955
6.3333 | 81.8515 | 81.0381 | 79.1931 | 2.1315 | 2.0906 | 1.3956
6.3375 | 81.8328 | 81.0185 | 79.1874 | 2.132 | 2.0907 | 1.3955
6.3417 | 81.8128 | 81.0022 | 79.182 | 2.1326 | 2.0909 | 1.3955
6.3458 | 81.8169 | 81.0132 | 79.1864 | 2.133 | 2.0911 | 1.3955
6.35 | 81.823 | 81.0197 | 79.1909 | 2.1335 | 2.0912 | 1.3955
6.3542 | 81.8248 | 81.016 | 79.1904 | 2.1341 | 2.0915 | 1.3956
6.3583 | 81.8245 | 81.0141 | 79.1897 | 2.1347 | 2.0918 | 1.3956
6.3625 | 81.8126 | 81.0016 | 79.1864 | 2.1351 | 2.0919 | 1.3956
6.3667 | 81.802 | 80.9911 | 79.1834 | 2.1356 | 2.092 | 1.3956
6.3708 | 81.8108 | 81.0005 | 79.1873 | 2.136 | 2.0922 | 1.3956
6.375 | 81.8206 | 81.0063 | 79.1912 | 2.1364 | 2.0924 | 1.3956
6.3792 | 81.8204 | 81.0005 | 79.1896 | 2.1369 | 2.0926 | 1.3956
6.3833 | 81.8109 | 80.9969 | 79.1879 | 2.1374 | 2.0928 | 1.3956
6.3875 | 81.8043 | 80.989 | 79.1863 | 2.1378 | 2.0929 | 1.3956
6.3917 | 81.7924 | 80.9821 | 79.1846 | 2.1382 | 2.093 | 1.3956
6.3958 | 81.8 | 80.9885 | 79.1874 | 2.1385 | 2.0932 | 1.3956
6.4 | 81.8087 | 80.9924 | 79.1901 | 2.139 | 2.0933 | 1.3956
6.4042 | 81.8049 | 80.9865 | 79.1886 | 2.1394 | 2.0935 | 1.3956
6.4083 | 81.7974 | 80.9826 | 79.187 | 2.1398 | 2.0936 | 1.3956
6.4125 | 81.7916 | 80.9772 | 79.1862 | 2.1401 | 2.0937 | 1.3956
6.4167 | 81.7876 | 80.9724 | 79.1852 | 2.1405 | 2.0938 | 1.3956
6.4208 | 81.7895 | 80.976 | 79.1868 | 2.1409 | 2.094 | 1.3956
6.425 | 81.7987 | 80.9779 | 79.1885 | 2.1412 | 2.0941 | 1.3956
6.4292 | 81.7925 | 80.9735 | 79.1874 | 2.1416 | 2.0943 | 1.3957
6.4333 | 81.7844 | 80.9706 | 79.1864 | 2.142 | 2.0944 | 1.3957
6.4375 | 81.7848 | 80.9669 | 79.186 | 2.1423 | 2.0945 | 1.3957
6.4417 | 81.7776 | 80.9635 | 79.1854 | 2.1426 | 2.0946 | 1.3957
6.4458 | 81.7802 | 80.9646 | 79.186 | 2.1429 | 2.0947 | 1.3957
6.45 | 81.785 | 80.9643 | 79.1869 | 2.1433 | 2.0948 | 1.3957
6.4542 | 81.7788 | 80.9602 | 79.1863 | 2.1435 | 2.095 | 1.3957
6.4583 | 81.775 | 80.9566 | 79.1857 | 2.1439 | 2.0951 | 1.3957
6.4625 | 81.7756 | 80.9527 | 79.1854 | 2.1442 | 2.0952 | 1.3957
6.4667 | 81.769 | 80.9493 | 79.1849 | 2.1445 | 2.0953 | 1.3957
6.4708 | 81.7684 | 80.9486 | 79.185 | 2.1448 | 2.0954 | 1.3957
6.475 | 81.7714 | 80.9479 | 79.1854 | 2.1451 | 2.0955 | 1.3957
6.4792 | 81.7626 | 80.9462 | 79.1853 | 2.1454 | 2.0957 | 1.3957
6.4833 | 81.7665 | 80.9451 | 79.1853 | 2.1457 | 2.0958 | 1.3957
6.4875 | 81.7633 | 80.9434 | 79.1851 | 2.1459 | 2.0959 | 1.3957
6.4917 | 81.7595 | 80.9414 | 79.1848 | 2.1463 | 2.096 | 1.3957
6.4958 | 81.7615 | 80.9404 | 79.1847 | 2.1465 | 2.0961 | 1.3957
6.5 | 81.759 | 80.9392 | 79.1846 | 2.1468 | 2.0962 | 1.3957
6.5042 | 81.7552 | 80.9382 | 79.1846 | 2.1471 | 2.0963 | 1.3957
6.5083 | 81.7575 | 80.9378 | 79.1847 | 2.1474 | 2.0964 | 1.3957
6.5125 | 81.7512 | 80.9365 | 79.1846 | 2.1476 | 2.0964 | 1.3958
6.5167 | 81.7514 | 80.9353 | 79.1845 | 2.1479 | 2.0965 | 1.3958
6.5208 | 81.7531 | 80.9348 | 79.1845 | 2.1481 | 2.0966 | 1.3958
6.525 | 81.7492 | 80.9338 | 79.1846 | 2.1484 | 2.0967 | 1.3958
6.5292 | 81.7491 | 80.9325 | 79.1844 | 2.1486 | 2.0968 | 1.3958
6.5333 | 81.7472 | 80.9312 | 79.1842 | 2.1488 | 2.0968 | 1.3958
6.5375 | 81.7437 | 80.9305 | 79.1841 | 2.149 | 2.0969 | 1.3958
6.5417 | 81.7452 | 80.9292 | 79.1839 | 2.1493 | 2.097 | 1.3958
6.5458 | 81.7484 | 80.928 | 79.184 | 2.1495 | 2.0971 | 1.3958
6.55 | 81.7441 | 80.9271 | 79.184 | 2.1498 | 2.0971 | 1.3958
6.5542 | 81.7415 | 80.9251 | 79.184 | 2.15 | 2.0972 | 1.3958
6.5583 | 81.7405 | 80.9237 | 79.1841 | 2.1502 | 2.0973 | 1.3958
6.5625 | 81.7349 | 80.9223 | 79.184 | 2.1504 | 2.0973 | 1.3958
6.5667 | 81.7416 | 80.9211 | 79.1838 | 2.1506 | 2.0974 | 1.3958
6.5708 | 81.7417 | 80.9201 | 79.1837 | 2.1508 | 2.0975 | 1.3958
6.575 | 81.7413 | 80.9187 | 79.1835 | 2.151 | 2.0975 | 1.3958
6.5792 | 81.7368 | 80.9178 | 79.1835 | 2.1512 | 2.0976 | 1.3958
6.5833 | 81.7343 | 80.9162 | 79.1836 | 2.1514 | 2.0977 | 1.3958
6.5875 | 81.7306 | 80.9137 | 79.1835 | 2.1516 | 2.0977 | 1.3958
6.5917 | 81.7336 | 80.9126 | 79.1833 | 2.1518 | 2.0978 | 1.3958
6.5958 | 81.7344 | 80.9115 | 79.1833 | 2.1519 | 2.0979 | 1.3958
6.6 | 81.7329 | 80.9104 | 79.1833 | 2.1521 | 2.0979 | 1.3958
6.6042 | 81.7301 | 80.9099 | 79.1833 | 2.1523 | 2.098 | 1.3958
6.6083 | 81.7304 | 80.9086 | 79.1834 | 2.1525 | 2.0981 | 1.3958
6.6125 | 81.7301 | 80.9072 | 79.1834 | 2.1526 | 2.0981 | 1.3958
6.6167 | 81.7315 | 80.9063 | 79.1833 | 2.1528 | 2.0982 | 1.3958
6.6208 | 81.7314 | 80.9047 | 79.1832 | 2.1529 | 2.0983 | 1.3958
6.625 | 81.7281 | 80.9035 | 79.1827 | 2.1531 | 2.0983 | 1.3958
6.6292 | 81.7242 | 80.9027 | 79.1827 | 2.1532 | 2.0984 | 1.3959
6.6333 | 81.7286 | 80.9016 | 79.1829 | 2.1534 | 2.0984 | 1.3959
6.6375 | 81.725 | 80.9017 | 79.183 | 2.1535 | 2.0985 | 1.3959
6.6417 | 81.7307 | 80.9011 | 79.1832 | 2.1537 | 2.0986 | 1.3959
6.6458 | 81.7263 | 80.8998 | 79.1832 | 2.1538 | 2.0986 | 1.3959
6.65 | 81.7266 | 80.899 | 79.1834 | 2.154 | 2.0987 | 1.3959
6.6542 | 81.7229 | 80.8979 | 79.1834 | 2.1541 | 2.0987 | 1.3959
6.6583 | 81.7258 | 80.8969 | 79.1832 | 2.1542 | 2.0988 | 1.3959
6.6625 | 81.7256 | 80.8973 | 79.1832 | 2.1543 | 2.0988 | 1.3959
6.6667 | 81.7232 | 80.8969 | 79.183 | 2.1545 | 2.0989 | 1.3959
6.6708 | 81.7266 | 80.8964 | 79.183 | 2.1546 | 2.0989 | 1.3959
6.675 | 81.7219 | 80.8959 | 79.1832 | 2.1547 | 2.099 | 1.3959
6.6792 | 81.7207 | 80.8944 | 79.1831 | 2.1548 | 2.099 | 1.3959
6.6833 | 81.7254 | 80.8936 | 79.1831 | 2.1549 | 2.0991 | 1.3959
6.6875 | 81.7218 | 80.8936 | 79.1832 | 2.155 | 2.0991 | 1.3959
6.6917 | 81.7211 | 80.8931 | 79.1836 | 2.1551 | 2.0991 | 1.3959
6.6958 | 81.7207 | 80.893 | 79.1837 | 2.1552 | 2.0992 | 1.3959
6.7 | 81.7222 | 80.8927 | 79.1831 | 2.1553 | 2.0992 | 1.3959
6.7042 | 81.7195 | 80.8915 | 79.183 | 2.1554 | 2.0992 | 1.3959
6.7083 | 81.7254 | 80.8907 | 79.1831 | 2.1555 | 2.0993 | 1.3959
6.7125 | 81.7237 | 80.8903 | 79.1831 | 2.1556 | 2.0993 | 1.3959
6.7167 | 81.7169 | 80.8897 | 79.1833 | 2.1557 | 2.0994 | 1.3959
6.7208 | 81.7168 | 80.8898 | 79.1834 | 2.1558 | 2.0994 | 1.3959
6.725 | 81.7191 | 80.8894 | 79.1833 | 2.1558 | 2.0994 | 1.3959
6.7292 | 81.7152 | 80.8886 | 79.1833 | 2.1559 | 2.0995 | 1.3959
6.7333 | 81.7243 | 80.8883 | 79.1833 | 2.156 | 2.0995 | 1.3959
6.7375 | 81.7237 | 80.8877 | 79.1832 | 2.1561 | 2.0995 | 1.3959
6.7417 | 81.7141 | 80.8873 | 79.1832 | 2.1562 | 2.0995 | 1.3959
6.7458 | 81.7187 | 80.8873 | 79.1832 | 2.1563 | 2.0996 | 1.3959
6.75 | 81.7138 | 80.8868 | 79.1836 | 2.1563 | 2.0996 | 1.3959
6.7542 | 81.7111 | 80.8862 | 79.1837 | 2.1564 | 2.0996 | 1.3959
6.7583 | 81.7199 | 80.8858 | 79.1835 | 2.1565 | 2.0997 | 1.3959
6.7625 | 81.7171 | 80.8852 | 79.1834 | 2.1565 | 2.0997 | 1.3959
6.7667 | 81.7132 | 80.8849 | 79.1833 | 2.1567 | 2.0997 | 1.3959
6.7708 | 81.7175 | 80.885 | 79.1833 | 2.1567 | 2.0997 | 1.3959
6.775 | 81.7154 | 80.8848 | 79.1838 | 2.1568 | 2.0998 | 1.3959
6.7792 | 81.7129 | 80.8845 | 79.1839 | 2.1568 | 2.0998 | 1.3959
6.7833 | 81.7201 | 80.8842 | 79.1839 | 2.1569 | 2.0998 | 1.3959
6.7875 | 81.7159 | 80.8837 | 79.1841 | 2.157 | 2.0998 | 1.3959
6.7917 | 81.7142 | 80.8835 | 79.184 | 2.157 | 2.0998 | 1.3959
6.7958 | 81.7128 | 80.8835 | 79.1842 | 2.1571 | 2.0999 | 1.3959
6.8 | 81.7125 | 80.8833 | 79.1847 | 2.1571 | 2.0999 | 1.3958
6.8042 | 81.7107 | 80.8831 | 79.1858 | 2.1572 | 2.0999 | 1.3958
6.8083 | 81.7143 | 80.883 | 79.1869 | 2.1573 | 2.0999 | 1.3958
6.8125 | 81.7161 | 80.8825 | 79.1883 | 2.1573 | 2.0999 | 1.3958
6.8167 | 81.716 | 80.8821 | 79.1894 | 2.1574 | 2.0999 | 1.3958
6.8208 | 81.714 | 80.8819 | 79.1901 | 2.1574 | 2.1 | 1.3958
6.825 | 81.7125 | 80.8816 | 79.1909 | 2.1575 | 2.1 | 1.3958
6.8292 | 81.7112 | 80.8802 | 79.1907 | 2.1575 | 2.1 | 1.3957
6.8333 | 81.7114 | 80.879 | 79.1906 | 2.1576 | 2.1 | 1.3957
6.8375 | 81.7141 | 80.8801 | 79.1925 | 2.1576 | 2.1 | 1.3957
6.8417 | 81.7171 | 80.8811 | 79.1943 | 2.1576 | 2.1 | 1.3957
6.8458 | 81.7128 | 80.8817 | 79.1934 | 2.1577 | 2.1001 | 1.3957
6.85 | 81.7073 | 80.882 | 79.193 | 2.1578 | 2.1001 | 1.3957
6.8542 | 81.7173 | 80.8924 | 79.2026 | 2.1577 | 2.1 | 1.3955
6.8583 | 81.7268 | 80.9022 | 79.2121 | 2.1576 | 2.0999 | 1.3954
6.8625 | 81.7297 | 80.9002 | 79.2122 | 2.1578 | 2.1 | 1.3954
6.8667 | 81.7393 | 80.899 | 79.2121 | 2.1579 | 2.1 | 1.3955
6.8708 | 81.7472 | 80.8952 | 79.2167 | 2.1577 | 2.0999 | 1.3952
6.875 | 81.7578 | 80.8927 | 79.2199 | 2.1576 | 2.0997 | 1.395
6.8792 | 81.7456 | 80.86 | 79.1979 | 2.158 | 2.1001 | 1.3953
6.8833 | 81.7316 | 80.8296 | 79.1762 | 2.1583 | 2.1004 | 1.3955
6.8875 | 81.7192 | 80.8263 | 79.1761 | 2.158 | 2.1003 | 1.3953
6.8917 | 81.7143 | 80.8215 | 79.1765 | 2.1578 | 2.1002 | 1.395
6.8958 | 81.6922 | 80.8335 | 79.1729 | 2.1583 | 2.1006 | 1.3955
6.9 | 81.6515 | 80.8412 | 79.1714 | 2.1588 | 2.1011 | 1.3958
6.9042 | 81.663 | 80.8928 | 79.2019 | 2.1586 | 2.1005 | 1.3953
6.9083 | 81.671 | 80.9397 | 79.2323 | 2.1582 | 2.1 | 1.3948
6.9125 | 81.6665 | 80.9471 | 79.239 | 2.1589 | 2.1003 | 1.3952
6.9167 | 81.6658 | 80.9574 | 79.2429 | 2.1596 | 2.1006 | 1.3956
6.9208 | 81.6358 | 80.9219 | 79.2262 | 2.1596 | 2.1 | 1.395
6.925 | 81.6185 | 80.8931 | 79.2083 | 2.1593 | 2.0995 | 1.3945
6.9292 | 81.6702 | 80.8778 | 79.2071 | 2.1595 | 2.0999 | 1.3949
6.9333 | 81.7389 | 80.8637 | 79.2065 | 2.1597 | 2.1003 | 1.3953
6.9375 | 81.7532 | 80.8634 | 79.1933 | 2.1598 | 2.1 | 1.3949
6.9417 | 81.7799 | 80.8604 | 79.1842 | 2.16 | 2.0997 | 1.3946
6.9458 | 81.7396 | 80.9095 | 79.2211 | 2.1603 | 2.0998 | 1.3947
6.95 | 81.7265 | 80.9555 | 79.2562 | 2.1604 | 2.0999 | 1.3948
6.9542 | 81.6754 | 80.9142 | 79.2286 | 2.1604 | 2.0999 | 1.3948
6.9583 | 81.6535 | 80.8795 | 79.1988 | 2.1603 | 2.0999 | 1.3948
6.9625 | 81.6715 | 80.8705 | 79.2048 | 2.1602 | 2.0998 | 1.3946
6.9667 | 81.7504 | 80.862 | 79.2105 | 2.1598 | 2.0996 | 1.3944
6.9708 | 81.8012 | 80.8614 | 79.2087 | 2.1598 | 2.1 | 1.3947
6.975 | 81.8731 | 80.8571 | 79.2087 | 2.1602 | 2.1003 | 1.3949
6.9792 | 81.8987 | 80.861 | 79.2087 | 2.1604 | 2.1001 | 1.3946
6.9833 | 81.8706 | 80.8637 | 79.21 | 2.1605 | 2.0999 | 1.3944
6.9875 | 81.8581 | 80.8589 | 79.2213 | 2.1606 | 2.1003 | 1.3946
6.9917 | 81.8311 | 80.856 | 79.2288 | 2.1604 | 2.1007 | 1.3948
6.9958 | 81.8187 | 80.8175 | 79.2002 | 2.1603 | 2.1008 | 1.3947
7 | 81.7983 | 80.7806 | 79.1729 | 2.1604 | 2.1009 | 1.3947
7.0042 | 81.7841 | 80.8256 | 79.1981 | 2.1605 | 2.1008 | 1.3946
7.0083 | 81.7417 | 80.863 | 79.226 | 2.1606 | 2.1008 | 1.3945
7.0125 | 81.6956 | 80.8629 | 79.2234 | 2.1608 | 2.1012 | 1.3947
7.0167 | 81.6401 | 80.8654 | 79.2192 | 2.1608 | 2.1015 | 1.3949
7.0208 | 81.6283 | 80.8454 | 79.2067 | 2.161 | 2.1013 | 1.3947
7.025 | 81.6003 | 80.8282 | 79.193 | 2.1612 | 2.1011 | 1.3945
7.0292 | 81.5854 | 80.8574 | 79.2091 | 2.1616 | 2.1012 | 1.3946
7.0333 | 81.5786 | 80.881 | 79.2257 | 2.1621 | 2.1013 | 1.3946
7.0375 | 81.5543 | 80.8857 | 79.2153 | 2.1625 | 2.1012 | 1.3946
7.0417 | 81.5509 | 80.8916 | 79.207 | 2.1629 | 2.1011 | 1.3946
7.0458 | 81.5589 | 80.9043 | 79.2179 | 2.1633 | 2.1009 | 1.3945
7.05 | 81.5651 | 80.9181 | 79.2263 | 2.1638 | 2.1007 | 1.3944
7.0542 | 81.5506 | 80.9051 | 79.2206 | 2.1645 | 2.1007 | 1.3945
7.0583 | 81.5326 | 80.894 | 79.213 | 2.1649 | 2.1007 | 1.3946
7.0625 | 81.5218 | 80.9046 | 79.2069 | 2.1653 | 2.1003 | 1.3945
7.0667 | 81.5287 | 80.9127 | 79.2059 | 2.1656 | 2.1 | 1.3943
7.0708 | 81.5654 | 80.9413 | 79.2246 | 2.166 | 2.0999 | 1.3943
7.075 | 81.5892 | 80.9692 | 79.2418 | 2.1664 | 2.0998 | 1.3944
7.0792 | 81.6054 | 80.9318 | 79.227 | 2.1666 | 2.0998 | 1.3944
7.0833 | 81.6263 | 80.9015 | 79.2076 | 2.1666 | 2.0997 | 1.3945
7.0875 | 81.6521 | 80.9098 | 79.2082 | 2.1665 | 2.0994 | 1.3943
7.0917 | 81.701 | 80.9123 | 79.2132 | 2.1663 | 2.0991 | 1.3942
7.0958 | 81.7447 | 80.9335 | 79.2261 | 2.1663 | 2.0992 | 1.3942
7.1 | 81.7987 | 80.9539 | 79.2403 | 2.1665 | 2.0992 | 1.3943
7.1042 | 81.8205 | 80.9138 | 79.2288 | 2.1666 | 2.0992 | 1.3943
7.1083 | 81.8348 | 80.8834 | 79.2117 | 2.1667 | 2.0992 | 1.3943
7.1125 | 81.8474 | 80.8845 | 79.213 | 2.1666 | 2.0991 | 1.3942
7.1167 | 81.8572 | 80.8807 | 79.2171 | 2.1665 | 2.099 | 1.3941
7.1208 | 81.8737 | 80.9001 | 79.2229 | 2.1664 | 2.0991 | 1.3942
7.125 | 81.9033 | 80.9163 | 79.2318 | 2.1662 | 2.0992 | 1.3942
7.1292 | 81.9391 | 80.8943 | 79.2293 | 2.1658 | 2.0993 | 1.3942
7.1333 | 81.953 | 80.8795 | 79.2213 | 2.1655 | 2.0994 | 1.3941
7.1375 | 81.9538 | 80.87 | 79.2192 | 2.1653 | 2.0994 | 1.3941
7.1417 | 81.9421 | 80.8589 | 79.2189 | 2.165 | 2.0994 | 1.3941
7.1458 | 81.9133 | 80.8759 | 79.2216 | 2.1647 | 2.0995 | 1.3941
7.15 | 81.8951 | 80.8884 | 79.2276 | 2.1644 | 2.0996 | 1.394
7.1542 | 81.8954 | 80.8794 | 79.2296 | 2.1643 | 2.0997 | 1.3941
7.1583 | 81.8867 | 80.8748 | 79.2271 | 2.1642 | 2.0999 | 1.3941
7.1625 | 81.8712 | 80.8563 | 79.221 | 2.1642 | 2.0999 | 1.3941
7.1667 | 81.8497 | 80.8393 | 79.2162 | 2.1643 | 2.1 | 1.394
7.1708 | 81.8299 | 80.8568 | 79.22 | 2.1642 | 2.1001 | 1.394
7.175 | 81.8032 | 80.8684 | 79.2262 | 2.1642 | 2.1001 | 1.394
7.1792 | 81.7927 | 80.8671 | 79.2297 | 2.1642 | 2.1003 | 1.394
7.1833 | 81.7727 | 80.8686 | 79.2301 | 2.1642 | 2.1004 | 1.394
7.1875 | 81.7453 | 80.8466 | 79.2227 | 2.1643 | 2.1005 | 1.394
7.1917 | 81.715 | 80.8283 | 79.2162 | 2.1644 | 2.1006 | 1.394
7.1958 | 81.6837 | 80.8433 | 79.2202 | 2.1643 | 2.1006 | 1.394
7.2 | 81.6572 | 80.8521 | 79.2255 | 2.1642 | 2.1007 | 1.3939
7.2042 | 81.6409 | 80.8535 | 79.2285 | 2.1642 | 2.1009 | 1.394
7.2083 | 81.6263 | 80.8567 | 79.2298 | 2.1643 | 2.101 | 1.394
7.2125 | 81.6174 | 80.8373 | 79.2235 | 2.1646 | 2.1011 | 1.394
7.2167 | 81.5958 | 80.8217 | 79.2177 | 2.1648 | 2.1012 | 1.394
7.2208 | 81.5889 | 80.8345 | 79.2219 | 2.165 | 2.1012 | 1.3939
7.225 | 81.5855 | 80.8418 | 79.2265 | 2.1652 | 2.1012 | 1.3939
7.2292 | 81.5803 | 80.8418 | 79.2276 | 2.1655 | 2.1014 | 1.3939
7.2333 | 81.5807 | 80.8433 | 79.228 | 2.1658 | 2.1016 | 1.394
7.2375 | 81.5689 | 80.8294 | 79.2238 | 2.1661 | 2.1016 | 1.3939
7.2417 | 81.5566 | 80.8185 | 79.2198 | 2.1664 | 2.1017 | 1.3939
7.2458 | 81.5616 | 80.8299 | 79.2239 | 2.1667 | 2.1017 | 1.3939
7.25 | 81.5678 | 80.8368 | 79.2282 | 2.1669 | 2.1018 | 1.3939
7.2542 | 81.5666 | 80.8344 | 79.2277 | 2.1673 | 2.1019 | 1.3939
7.2583 | 81.5618 | 80.8338 | 79.2269 | 2.1676 | 2.102 | 1.3939
7.2625 | 81.5535 | 80.8249 | 79.2245 | 2.1679 | 2.102 | 1.3939
7.2667 | 81.5415 | 80.8179 | 79.2222 | 2.1681 | 2.1021 | 1.3939
7.2708 | 81.5522 | 80.827 | 79.2256 | 2.1684 | 2.1021 | 1.3939
7.275 | 81.5587 | 80.8326 | 79.229 | 2.1687 | 2.1022 | 1.3939
7.2792 | 81.5571 | 80.8288 | 79.2279 | 2.169 | 2.1023 | 1.3939
7.2833 | 81.5523 | 80.8271 | 79.2267 | 2.1693 | 2.1024 | 1.3939
7.2875 | 81.5434 | 80.8215 | 79.2256 | 2.1695 | 2.1024 | 1.3939
7.2917 | 81.5381 | 80.8169 | 79.2243 | 2.1697 | 2.1024 | 1.3938
7.2958 | 81.544 | 80.8235 | 79.2267 | 2.17 | 2.1025 | 1.3938
7.3 | 81.5521 | 80.8278 | 79.2291 | 2.1702 | 2.1025 | 1.3938
7.3042 | 81.5475 | 80.8247 | 79.2281 | 2.1705 | 2.1026 | 1.3938
7.3083 | 81.5405 | 80.8235 | 79.2271 | 2.1708 | 2.1026 | 1.3938
7.3125 | 81.5403 | 80.8205 | 79.2267 | 2.171 | 2.1027 | 1.3938
7.3167 | 81.5316 | 80.8181 | 79.226 | 2.1712 | 2.1027 | 1.3938
7.3208 | 81.5414 | 80.8222 | 79.2274 | 2.1714 | 2.1027 | 1.3938
7.325 | 81.5431 | 80.8243 | 79.229 | 2.1716 | 2.1028 | 1.3938
7.3292 | 81.5403 | 80.8211 | 79.2283 | 2.1718 | 2.1028 | 1.3938
7.3333 | 81.5329 | 80.8188 | 79.2276 | 2.1721 | 2.1029 | 1.3938
7.3375 | 81.5341 | 80.8159 | 79.2275 | 2.1722 | 2.1029 | 1.3938
7.3417 | 81.5287 | 80.8136 | 79.2271 | 2.1725 | 2.1029 | 1.3938
7.3458 | 81.5325 | 80.8155 | 79.2278 | 2.1726 | 2.103 | 1.3938
7.35 | 81.5355 | 80.8166 | 79.2287 | 2.1729 | 2.103 | 1.3938
7.3542 | 81.5287 | 80.815 | 79.2286 | 2.173 | 2.103 | 1.3938
7.3583 | 81.5299 | 80.8143 | 79.2284 | 2.1733 | 2.1031 | 1.3938
7.3625 | 81.5271 | 80.813 | 79.2284 | 2.1734 | 2.1031 | 1.3938
7.3667 | 81.5257 | 80.8116 | 79.2282 | 2.1737 | 2.1032 | 1.3937
7.3708 | 81.5282 | 80.8122 | 79.2284 | 2.1738 | 2.1032 | 1.3937
7.375 | 81.5275 | 80.8125 | 79.2288 | 2.174 | 2.1032 | 1.3937
7.3792 | 81.5247 | 80.8121 | 79.2289 | 2.1741 | 2.1033 | 1.3937
7.3833 | 81.5257 | 80.8126 | 79.2291 | 2.1744 | 2.1033 | 1.3937
7.3875 | 81.5218 | 80.8118 | 79.2292 | 2.1745 | 2.1033 | 1.3937
7.3917 | 81.5221 | 80.8114 | 79.2292 | 2.1747 | 2.1033 | 1.3937
7.3958 | 81.5234 | 80.8122 | 79.2294 | 2.1748 | 2.1034 | 1.3937
7.4 | 81.5207 | 80.8123 | 79.2297 | 2.175 | 2.1034 | 1.3937
7.4042 | 81.5189 | 80.8123 | 79.2297 | 2.1751 | 2.1034 | 1.3937
7.4083 | 81.5174 | 80.8123 | 79.2297 | 2.1753 | 2.1034 | 1.3937
7.4125 | 81.5136 | 80.8126 | 79.2298 | 2.1754 | 2.1034 | 1.3937
7.4167 | 81.5158 | 80.8126 | 79.2299 | 2.1756 | 2.1034 | 1.3937
7.4208 | 81.5202 | 80.8129 | 79.2302 | 2.1757 | 2.1035 | 1.3937
7.425 | 81.5158 | 80.8133 | 79.2305 | 2.1759 | 2.1035 | 1.3937
7.4292 | 81.5166 | 80.8126 | 79.2307 | 2.176 | 2.1035 | 1.3937
7.4333 | 81.5155 | 80.8125 | 79.2309 | 2.1761 | 2.1035 | 1.3937
7.4375 | 81.5095 | 80.8129 | 79.231 | 2.1762 | 2.1035 | 1.3937
7.4417 | 81.5163 | 80.8129 | 79.2311 | 2.1764 | 2.1035 | 1.3936
7.4458 | 81.5183 | 80.8132 | 79.2312 | 2.1765 | 2.1035 | 1.3936
7.45 | 81.5158 | 80.8132 | 79.2313 | 2.1766 | 2.1035 | 1.3936
7.4542 | 81.5154 | 80.813 | 79.2314 | 2.1768 | 2.1035 | 1.3936
7.4583 | 81.513 | 80.8127 | 79.2316 | 2.1769 | 2.1035 | 1.3936
7.4625 | 81.5064 | 80.8117 | 79.2317 | 2.1769 | 2.1035 | 1.3936
7.4667 | 81.5136 | 80.8117 | 79.2317 | 2.1771 | 2.1035 | 1.3936
7.4708 | 81.5137 | 80.8121 | 79.2319 | 2.1772 | 2.1036 | 1.3936
7.475 | 81.513 | 80.8121 | 79.2322 | 2.1773 | 2.1036 | 1.3936
7.4792 | 81.5124 | 80.8126 | 79.2324 | 2.1774 | 2.1036 | 1.3936
7.4833 | 81.5086 | 80.8124 | 79.2326 | 2.1775 | 2.1036 | 1.3936
7.4875 | 81.5098 | 80.8116 | 79.2327 | 2.1775 | 2.1036 | 1.3936
7.4917 | 81.511 | 80.8117 | 79.2328 | 2.1777 | 2.1036 | 1.3936
7.4958 | 81.5158 | 80.8115 | 79.2329 | 2.1777 | 2.1036 | 1.3936
7.5 | 81.5106 | 80.8114 | 79.2326 | 2.1779 | 2.1036 | 1.3936
7.5042 | 81.5093 | 80.812 | 79.2328 | 2.1779 | 2.1036 | 1.3935
7.5083 | 81.5087 | 80.8119 | 79.2333 | 2.178 | 2.1036 | 1.3935
7.5125 | 81.5073 | 80.812 | 79.2335 | 2.178 | 2.1036 | 1.3935
7.5167 | 81.5127 | 80.8121 | 79.2338 | 2.1782 | 2.1036 | 1.3935
7.5208 | 81.5138 | 80.8115 | 79.2339 | 2.1782 | 2.1036 | 1.3935
7.525 | 81.5121 | 80.8114 | 79.234 | 2.1783 | 2.1036 | 1.3935
7.5292 | 81.5101 | 80.8116 | 79.2343 | 2.1784 | 2.1036 | 1.3935
7.5333 | 81.5117 | 80.8116 | 79.2343 | 2.1784 | 2.1036 | 1.3935
7.5375 | 81.509 | 80.8125 | 79.2345 | 2.1785 | 2.1036 | 1.3935
7.5417 | 81.5102 | 80.8129 | 79.2344 | 2.1786 | 2.1036 | 1.3935
7.5458 | 81.5146 | 80.8128 | 79.2345 | 2.1786 | 2.1036 | 1.3935
7.55 | 81.5073 | 80.8131 | 79.235 | 2.1787 | 2.1036 | 1.3935
7.5542 | 81.5104 | 80.8128 | 79.2352 | 2.1787 | 2.1036 | 1.3935
7.5583 | 81.5109 | 80.8129 | 79.2353 | 2.1788 | 2.1036 | 1.3935
7.5625 | 81.5094 | 80.8139 | 79.2355 | 2.1788 | 2.1036 | 1.3934
7.5667 | 81.5104 | 80.8143 | 79.2359 | 2.1789 | 2.1036 | 1.3934
7.5708 | 81.5121 | 80.8148 | 79.2361 | 2.1789 | 2.1036 | 1.3934
7.575 | 81.5114 | 80.8153 | 79.236 | 2.179 | 2.1036 | 1.3934
7.5792 | 81.5147 | 80.8149 | 79.236 | 2.179 | 2.1036 | 1.3934
7.5833 | 81.514 | 80.815 | 79.2362 | 2.1791 | 2.1036 | 1.3934
7.5875 | 81.515 | 80.8157 | 79.2365 | 2.1791 | 2.1036 | 1.3934
7.5917 | 81.507 | 80.816 | 79.2369 | 2.1792 | 2.1036 | 1.3934
7.5958 | 81.5066 | 80.8168 | 79.2371 | 2.1792 | 2.1035 | 1.3934
7.6 | 81.5119 | 80.8173 | 79.237 | 2.1792 | 2.1035 | 1.3934
7.6042 | 81.512 | 80.8173 | 79.2372 | 2.1792 | 2.1035 | 1.3934
7.6083 | 81.5195 | 80.8177 | 79.2374 | 2.1793 | 2.1035 | 1.3934
7.6125 | 81.5196 | 80.8177 | 79.2375 | 2.1793 | 2.1035 | 1.3933
7.6167 | 81.5145 | 80.8177 | 79.2377 | 2.1794 | 2.1035 | 1.3933
7.6208 | 81.5166 | 80.818 | 79.2378 | 2.1794 | 2.1035 | 1.3933
7.625 | 81.5123 | 80.818 | 79.238 | 2.1794 | 2.1035 | 1.3933
7.6292 | 81.5144 | 80.818 | 79.2381 | 2.1795 | 2.1035 | 1.3933
7.6333 | 81.5133 | 80.8183 | 79.2381 | 2.1795 | 2.1034 | 1.3933
7.6375 | 81.5126 | 80.8186 | 79.2385 | 2.1795 | 2.1034 | 1.3933
7.6417 | 81.5116 | 80.8191 | 79.2389 | 2.1795 | 2.1034 | 1.3933
7.6458 | 81.5145 | 80.8199 | 79.2394 | 2.1795 | 2.1034 | 1.3933
7.65 | 81.5123 | 80.8202 | 79.2402 | 2.1795 | 2.1034 | 1.3933
7.6542 | 81.5151 | 80.8204 | 79.2416 | 2.1796 | 2.1034 | 1.3933
7.6583 | 81.5175 | 80.8208 | 79.2426 | 2.1796 | 2.1034 | 1.3932
7.6625 | 81.5151 | 80.8207 | 79.2448 | 2.1796 | 2.1034 | 1.3932
7.6667 | 81.5166 | 80.821 | 79.2467 | 2.1796 | 2.1033 | 1.3932
7.6708 | 81.513 | 80.821 | 79.2477 | 2.1797 | 2.1033 | 1.3931
7.675 | 81.5127 | 80.8207 | 79.2489 | 2.1797 | 2.1033 | 1.3931
7.6792 | 81.5133 | 80.822 | 79.2513 | 2.1797 | 2.1033 | 1.3931
7.6833 | 81.5151 | 80.8232 | 79.2535 | 2.1797 | 2.1033 | 1.393
7.6875 | 81.519 | 80.8232 | 79.2552 | 2.1797 | 2.1033 | 1.393
7.6917 | 81.5194 | 80.8233 | 79.2566 | 2.1797 | 2.1033 | 1.3929
7.6958 | 81.5222 | 80.8234 | 79.2575 | 2.1798 | 2.1032 | 1.3929
7.7 | 81.521 | 80.8234 | 79.2584 | 2.1798 | 2.1032 | 1.3928
7.7042 | 81.5191 | 80.82 | 79.2561 | 2.1798 | 2.1032 | 1.3928
7.7083 | 81.517 | 80.8167 | 79.2539 | 2.1799 | 2.1033 | 1.3928
7.7125 | 81.5173 | 80.819 | 79.2565 | 2.1798 | 2.1032 | 1.3927
7.7167 | 81.5206 | 80.821 | 79.2589 | 2.1798 | 2.1032 | 1.3926
7.7208 | 81.5127 | 80.8225 | 79.2565 | 2.1799 | 2.1032 | 1.3927
7.725 | 81.5043 | 80.8233 | 79.2548 | 2.1801 | 2.1033 | 1.3927
7.7292 | 81.5095 | 80.8419 | 79.27 | 2.1799 | 2.1031 | 1.3925
7.7333 | 81.5201 | 80.8592 | 79.2849 | 2.1798 | 2.1029 | 1.3923
7.7375 | 81.523 | 80.8583 | 79.2849 | 2.1801 | 2.1029 | 1.3924
7.7417 | 81.5215 | 80.8588 | 79.2845 | 2.1803 | 2.103 | 1.3924
7.7458 | 81.5426 | 80.8544 | 79.2906 | 2.1799 | 2.1027 | 1.3921
7.75 | 81.5582 | 80.8526 | 79.2949 | 2.1796 | 2.1024 | 1.3918
7.7542 | 81.5778 | 80.8158 | 79.2714 | 2.18 | 2.1028 | 1.3921
7.7583 | 81.5915 | 80.7823 | 79.2482 | 2.1803 | 2.1032 | 1.3924
7.7625 | 81.5867 | 80.7787 | 79.2475 | 2.1801 | 2.103 | 1.392
7.7667 | 81.5999 | 80.773 | 79.248 | 2.1798 | 2.1027 | 1.3917
7.7708 | 81.5834 | 80.7909 | 79.2507 | 2.1801 | 2.1032 | 1.3921
7.775 | 81.5647 | 80.8033 | 79.2551 | 2.1807 | 2.1037 | 1.3926
7.7792 | 81.552 | 80.8388 | 79.2737 | 2.1804 | 2.1031 | 1.392
7.7833 | 81.5255 | 80.8706 | 79.2923 | 2.1799 | 2.1026 | 1.3915
7.7875 | 81.5116 | 80.8761 | 79.3021 | 2.1803 | 2.103 | 1.3919
7.7917 | 81.4993 | 80.8848 | 79.3088 | 2.1806 | 2.1033 | 1.3922
7.7958 | 81.4786 | 80.846 | 79.2836 | 2.1805 | 2.1028 | 1.3918
7.8 | 81.4419 | 80.8129 | 79.2585 | 2.1806 | 2.1024 | 1.3914
7.8042 | 81.4653 | 80.8259 | 79.274 | 2.1806 | 2.1026 | 1.3916
7.8083 | 81.4999 | 80.8366 | 79.2904 | 2.1808 | 2.1028 | 1.3918
7.8125 | 81.5374 | 80.8391 | 79.278 | 2.1807 | 2.1027 | 1.3916
7.8167 | 81.5297 | 80.8396 | 79.2682 | 2.1809 | 2.1025 | 1.3915
7.8208 | 81.5435 | 80.8722 | 79.2947 | 2.1812 | 2.1023 | 1.3914
7.825 | 81.5078 | 80.9046 | 79.3193 | 2.1812 | 2.1022 | 1.3912
7.8292 | 81.4731 | 80.8726 | 79.2993 | 2.1814 | 2.1023 | 1.3914
7.8333 | 81.4302 | 80.8466 | 79.2774 | 2.1817 | 2.1024 | 1.3916
7.8375 | 81.413 | 80.8437 | 79.2765 | 2.1818 | 2.1021 | 1.3912
7.8417 | 81.422 | 80.84 | 79.2774 | 2.1818 | 2.1017 | 1.3909
7.8458 | 81.4527 | 80.8624 | 79.2932 | 2.1819 | 2.1019 | 1.3911
7.85 | 81.5212 | 80.8808 | 79.3093 | 2.182 | 2.1021 | 1.3913
7.8542 | 81.5475 | 80.8609 | 79.2946 | 2.1821 | 2.1019 | 1.3912
7.8583 | 81.5807 | 80.8443 | 79.2796 | 2.1823 | 2.1018 | 1.391
7.8625 | 81.5987 | 80.8424 | 79.292 | 2.1823 | 2.1019 | 1.391
7.8667 | 81.6195 | 80.8413 | 79.3019 | 2.1822 | 2.1019 | 1.391
7.8708 | 81.6461 | 80.8213 | 79.285 | 2.1821 | 2.1021 | 1.3911
7.875 | 81.6954 | 80.8004 | 79.2696 | 2.1819 | 2.1022 | 1.3911
7.8792 | 81.7181 | 80.8249 | 79.2826 | 2.182 | 2.102 | 1.3909
7.8833 | 81.7454 | 80.8448 | 79.2978 | 2.182 | 2.1019 | 1.3907
7.8875 | 81.7392 | 80.8427 | 79.3026 | 2.1821 | 2.1022 | 1.3909
7.8917 | 81.6866 | 80.8432 | 79.3048 | 2.182 | 2.1025 | 1.3911
7.8958 | 81.6716 | 80.8154 | 79.285 | 2.1819 | 2.1024 | 1.391
7.9 | 81.6511 | 80.7899 | 79.2655 | 2.1817 | 2.1023 | 1.3908
7.9042 | 81.6399 | 80.827 | 79.2864 | 2.1818 | 2.1023 | 1.3908
7.9083 | 81.6325 | 80.8566 | 79.3087 | 2.1819 | 2.1023 | 1.3908
7.9125 | 81.6059 | 80.8552 | 79.3022 | 2.1819 | 2.1024 | 1.3908
7.9167 | 81.5847 | 80.8564 | 79.2952 | 2.182 | 2.1025 | 1.3909
7.9208 | 81.5563 | 80.8503 | 79.2933 | 2.1819 | 2.1023 | 1.3908
7.925 | 81.5318 | 80.8465 | 79.29 | 2.1819 | 2.1021 | 1.3906
7.9292 | 81.4966 | 80.8582 | 79.2964 | 2.1821 | 2.1021 | 1.3907
7.9333 | 81.4538 | 80.867 | 79.3031 | 2.1822 | 2.1022 | 1.3908
7.9375 | 81.4156 | 80.8723 | 79.2951 | 2.1823 | 2.1019 | 1.3907
7.9417 | 81.4115 | 80.8775 | 79.2899 | 2.1825 | 2.1018 | 1.3906
7.9458 | 81.4167 | 80.8947 | 79.3022 | 2.1826 | 2.1016 | 1.3905
7.95 | 81.4249 | 80.9122 | 79.3126 | 2.183 | 2.1015 | 1.3905
7.9542 | 81.4229 | 80.8958 | 79.3051 | 2.1834 | 2.1014 | 1.3906
7.9583 | 81.3962 | 80.8826 | 79.2955 | 2.1838 | 2.1014 | 1.3906
7.9625 | 81.3711 | 80.892 | 79.2931 | 2.184 | 2.101 | 1.3905
7.9667 | 81.3665 | 80.8972 | 79.2945 | 2.1844 | 2.1007 | 1.3904
7.9708 | 81.3833 | 80.9166 | 79.3082 | 2.1846 | 2.1007 | 1.3904
7.975 | 81.4127 | 80.9362 | 79.3215 | 2.1849 | 2.1006 | 1.3904
7.9792 | 81.4181 | 80.904 | 79.3098 | 2.1852 | 2.1006 | 1.3904
7.9833 | 81.4149 | 80.8801 | 79.2943 | 2.1855 | 2.1005 | 1.3904
7.9875 | 81.4127 | 80.8888 | 79.2957 | 2.1856 | 2.1003 | 1.3903
7.9917 | 81.4219 | 80.8918 | 79.3003 | 2.1856 | 2.1001 | 1.3902
7.9958 | 81.453 | 80.911 | 79.3088 | 2.1856 | 2.1001 | 1.3902
8 | 81.4938 | 80.9284 | 79.3189 | 2.1855 | 2.1001 | 1.3903
8.0042 | 81.5362 | 80.9033 | 79.3125 | 2.1855 | 2.1 | 1.3902
8.0083 | 81.582 | 80.8865 | 79.3016 | 2.1855 | 2.1 | 1.3902
8.0125 | 81.6184 | 80.8878 | 79.3024 | 2.1856 | 2.0999 | 1.3901
8.0167 | 81.6485 | 80.8851 | 79.3052 | 2.1857 | 2.0998 | 1.3901
8.0208 | 81.6579 | 80.9013 | 79.309 | 2.1858 | 2.0998 | 1.3901
8.025 | 81.6685 | 80.9141 | 79.3154 | 2.1858 | 2.0998 | 1.3901
8.0292 | 81.6785 | 80.9001 | 79.3144 | 2.1856 | 2.0998 | 1.3901
8.0333 | 81.703 | 80.8923 | 79.3089 | 2.1854 | 2.0998 | 1.39
8.0375 | 81.7221 | 80.8846 | 79.3063 | 2.1853 | 2.0998 | 1.39
8.0417 | 81.7359 | 80.8761 | 79.3052 | 2.1851 | 2.0997 | 1.39
8.0458 | 81.7325 | 80.893 | 79.3086 | 2.1849 | 2.0997 | 1.3899
8.05 | 81.7343 | 80.9052 | 79.3144 | 2.1846 | 2.0997 | 1.3899
8.0542 | 81.7464 | 80.9002 | 79.3165 | 2.1842 | 2.0997 | 1.3899
8.0583 | 81.7606 | 80.8995 | 79.3149 | 2.1839 | 2.0998 | 1.3899
8.0625 | 81.7755 | 80.8849 | 79.3097 | 2.1836 | 2.0997 | 1.3899
8.0667 | 81.7758 | 80.8725 | 79.3056 | 2.1834 | 2.0997 | 1.3899
8.0708 | 81.7523 | 80.8883 | 79.309 | 2.1831 | 2.0997 | 1.3898
8.075 | 81.7354 | 80.8982 | 79.3141 | 2.1829 | 2.0996 | 1.3898
8.0792 | 81.7261 | 80.8989 | 79.3173 | 2.1826 | 2.0997 | 1.3898
8.0833 | 81.7216 | 80.9022 | 79.318 | 2.1824 | 2.0998 | 1.3898
8.0875 | 81.7235 | 80.886 | 79.3122 | 2.1824 | 2.0997 | 1.3898
8.0917 | 81.7062 | 80.8732 | 79.3073 | 2.1824 | 2.0997 | 1.3898
8.0958 | 81.6933 | 80.8872 | 79.3109 | 2.1824 | 2.0997 | 1.3897
8.1 | 81.6829 | 80.8954 | 79.3155 | 2.1823 | 2.0996 | 1.3897
8.1042 | 81.6709 | 80.8972 | 79.3177 | 2.1823 | 2.0997 | 1.3897
8.1083 | 81.665 | 80.9008 | 79.3186 | 2.1823 | 2.0998 | 1.3897
8.1125 | 81.6518 | 80.8882 | 79.314 | 2.1823 | 2.0997 | 1.3897
8.1167 | 81.638 | 80.8791 | 79.31 | 2.1823 | 2.0997 | 1.3897
8.1208 | 81.6292 | 80.8931 | 79.314 | 2.1823 | 2.0997 | 1.3896
8.125 | 81.6228 | 80.902 | 79.3184 | 2.1822 | 2.0996 | 1.3896
8.1292 | 81.6138 | 80.9027 | 79.3191 | 2.1822 | 2.0997 | 1.3896
8.1333 | 81.6102 | 80.9052 | 79.3193 | 2.1823 | 2.0997 | 1.3896
8.1375 | 81.5953 | 80.8964 | 79.3162 | 2.1823 | 2.0996 | 1.3896
8.1417 | 81.5816 | 80.8902 | 79.3135 | 2.1823 | 2.0996 | 1.3896
8.1458 | 81.5783 | 80.902 | 79.3172 | 2.1822 | 2.0995 | 1.3896
8.15 | 81.5695 | 80.9096 | 79.321 | 2.1821 | 2.0995 | 1.3895
8.1542 | 81.5677 | 80.9087 | 79.3207 | 2.1822 | 2.0995 | 1.3895
8.1583 | 81.5645 | 80.9096 | 79.3202 | 2.1822 | 2.0995 | 1.3895
8.1625 | 81.5523 | 80.9042 | 79.3185 | 2.1823 | 2.0994 | 1.3895
8.1667 | 81.5475 | 80.9005 | 79.317 | 2.1823 | 2.0993 | 1.3895
8.1708 | 81.5388 | 80.9102 | 79.32 | 2.1822 | 2.0993 | 1.3895
8.175 | 81.5421 | 80.917 | 79.323 | 2.1822 | 2.0992 | 1.3894
8.1792 | 81.5336 | 80.9162 | 79.3224 | 2.1823 | 2.0992 | 1.3894
8.1833 | 81.5361 | 80.9175 | 79.3218 | 2.1823 | 2.0992 | 1.3894
8.1875 | 81.5263 | 80.9156 | 79.3211 | 2.1823 | 2.0991 | 1.3894
8.1917 | 81.5233 | 80.9145 | 79.3204 | 2.1823 | 2.099 | 1.3894
8.1958 | 81.5237 | 80.9221 | 79.3226 | 2.1823 | 2.099 | 1.3893
8.2 | 81.5212 | 80.9271 | 79.3248 | 2.1823 | 2.0989 | 1.3893
8.2042 | 81.5233 | 80.9261 | 79.3242 | 2.1823 | 2.0988 | 1.3893
8.2083 | 81.5161 | 80.9264 | 79.3237 | 2.1824 | 2.0988 | 1.3893
8.2125 | 81.5174 | 80.9239 | 79.3234 | 2.1824 | 2.0987 | 1.3893
8.2167 | 81.5056 | 80.9222 | 79.323 | 2.1824 | 2.0987 | 1.3893
8.2208 | 81.5101 | 80.9263 | 79.3243 | 2.1824 | 2.0986 | 1.3892
8.225 | 81.5011 | 80.9288 | 79.3257 | 2.1824 | 2.0985 | 1.3892
8.2292 | 81.5038 | 80.9284 | 79.3256 | 2.1824 | 2.0985 | 1.3892
8.2333 | 81.4961 | 80.9289 | 79.3253 | 2.1825 | 2.0985 | 1.3892
8.2375 | 81.4973 | 80.9285 | 79.3254 | 2.1825 | 2.0984 | 1.3892
8.2417 | 81.491 | 80.9281 | 79.3253 | 2.1825 | 2.0983 | 1.3892
8.2458 | 81.4944 | 80.9309 | 79.326 | 2.1825 | 2.0983 | 1.3892
8.25 | 81.4898 | 80.933 | 79.3269 | 2.1825 | 2.0983 | 1.3891
8.2542 | 81.4919 | 80.9339 | 79.3271 | 2.1825 | 2.0982 | 1.3891
8.2583 | 81.4908 | 80.9357 | 79.3273 | 2.1825 | 2.0982 | 1.3891
8.2625 | 81.4911 | 80.9361 | 79.3276 | 2.1826 | 2.0981 | 1.3891
8.2667 | 81.4911 | 80.9369 | 79.3278 | 2.1826 | 2.0981 | 1.3891
8.2708 | 81.493 | 80.9396 | 79.3283 | 2.1826 | 2.098 | 1.3891
8.275 | 81.492 | 80.9415 | 79.3289 | 2.1826 | 2.0979 | 1.389
8.2792 | 81.4938 | 80.9431 | 79.3291 | 2.1826 | 2.0979 | 1.389
8.2833 | 81.4923 | 80.9449 | 79.3293 | 2.1827 | 2.0978 | 1.389
8.2875 | 81.4905 | 80.9464 | 79.3296 | 2.1827 | 2.0977 | 1.389
8.2917 | 81.4911 | 80.9478 | 79.3299 | 2.1827 | 2.0977 | 1.389
8.2958 | 81.4943 | 80.9501 | 79.3304 | 2.1827 | 2.0976 | 1.389
8.3 | 81.4919 | 80.9523 | 79.331 | 2.1827 | 2.0975 | 1.3889
8.3042 | 81.4993 | 80.9534 | 79.3314 | 2.1827 | 2.0975 | 1.3889
8.3083 | 81.4967 | 80.9553 | 79.3317 | 2.1827 | 2.0974 | 1.3889
8.3125 | 81.4993 | 80.9576 | 79.3321 | 2.1828 | 2.0973 | 1.3889
8.3167 | 81.5016 | 80.9593 | 79.3324 | 2.1828 | 2.0972 | 1.3889
8.3208 | 81.5066 | 80.9614 | 79.3327 | 2.1828 | 2.0972 | 1.3889
8.325 | 81.5061 | 80.9633 | 79.3331 | 2.1828 | 2.0971 | 1.3888
8.3292 | 81.515 | 80.9648 | 79.3335 | 2.1828 | 2.097 | 1.3888
8.3333 | 81.511 | 80.9665 | 79.3339 | 2.1828 | 2.0969 | 1.3888
8.3375 | 81.5152 | 80.968 | 79.3343 | 2.1829 | 2.0969 | 1.3888
8.3417 | 81.5192 | 80.9698 | 79.3345 | 2.1828 | 2.0968 | 1.3888
8.3458 | 81.522 | 80.9723 | 79.3349 | 2.1828 | 2.0967 | 1.3888
8.35 | 81.5279 | 80.9743 | 79.3356 | 2.1829 | 2.0966 | 1.3887
8.3542 | 81.5306 | 80.9763 | 79.336 | 2.1829 | 2.0965 | 1.3887
8.3583 | 81.532 | 80.9779 | 79.3363 | 2.1829 | 2.0964 | 1.3887
8.3625 | 81.5371 | 80.9789 | 79.3366 | 2.1829 | 2.0964 | 1.3887
8.3667 | 81.5384 | 80.9808 | 79.3369 | 2.1829 | 2.0963 | 1.3887
8.3708 | 81.5491 | 80.9829 | 79.3372 | 2.1829 | 2.0962 | 1.3886
8.375 | 81.5482 | 80.985 | 79.3373 | 2.1829 | 2.0961 | 1.3886
8.3792 | 81.5567 | 80.9874 | 79.3378 | 2.183 | 2.096 | 1.3886
8.3833 | 81.5554 | 80.9892 | 79.3384 | 2.183 | 2.0959 | 1.3886
8.3875 | 81.5602 | 80.9908 | 79.3388 | 2.183 | 2.0958 | 1.3886
8.3917 | 81.5659 | 80.993 | 79.3394 | 2.1829 | 2.0957 | 1.3886
8.3958 | 81.573 | 80.9946 | 79.3397 | 2.1829 | 2.0957 | 1.3885
8.4 | 81.5796 | 80.9966 | 79.3399 | 2.1829 | 2.0956 | 1.3885
8.4042 | 81.5855 | 80.9991 | 79.3404 | 2.183 | 2.0955 | 1.3885
8.4083 | 81.5928 | 81.0012 | 79.3409 | 2.1829 | 2.0954 | 1.3885
8.4125 | 81.595 | 81.0042 | 79.3413 | 2.1829 | 2.0953 | 1.3885
8.4167 | 81.6046 | 81.0071 | 79.3416 | 2.1829 | 2.0952 | 1.3884
8.4208 | 81.6109 | 81.0096 | 79.342 | 2.1829 | 2.0951 | 1.3884
8.425 | 81.6148 | 81.0124 | 79.3428 | 2.1829 | 2.095 | 1.3884
8.4292 | 81.6258 | 81.0148 | 79.3433 | 2.1829 | 2.0949 | 1.3884
8.4333 | 81.6275 | 81.0173 | 79.3436 | 2.1829 | 2.0948 | 1.3884
8.4375 | 81.6355 | 81.0206 | 79.3441 | 2.1829 | 2.0946 | 1.3883
8.4417 | 81.6439 | 81.0236 | 79.3447 | 2.1829 | 2.0945 | 1.3883
8.4458 | 81.6493 | 81.0263 | 79.3452 | 2.1829 | 2.0944 | 1.3883
8.45 | 81.6613 | 81.0293 | 79.3456 | 2.1828 | 2.0943 | 1.3883
8.4542 | 81.6701 | 81.0312 | 79.3459 | 2.1828 | 2.0942 | 1.3883
8.4583 | 81.6787 | 81.0335 | 79.3463 | 2.1828 | 2.0941 | 1.3882
8.4625 | 81.6868 | 81.0366 | 79.3468 | 2.1828 | 2.0939 | 1.3882
8.4667 | 81.6906 | 81.0393 | 79.3474 | 2.1828 | 2.0938 | 1.3882
8.4708 | 81.6956 | 81.0426 | 79.3479 | 2.1828 | 2.0937 | 1.3882
8.475 | 81.7009 | 81.0458 | 79.3481 | 2.1827 | 2.0936 | 1.3882
8.4792 | 81.7067 | 81.0482 | 79.3484 | 2.1827 | 2.0935 | 1.3881
8.4833 | 81.7118 | 81.0511 | 79.3489 | 2.1826 | 2.0933 | 1.3881
8.4875 | 81.7166 | 81.0547 | 79.35 | 2.1825 | 2.0932 | 1.3881
8.4917 | 81.7225 | 81.058 | 79.351 | 2.1824 | 2.0931 | 1.3881
8.4958 | 81.7247 | 81.0617 | 79.352 | 2.1823 | 2.0929 | 1.388
8.5 | 81.727 | 81.0652 | 79.3529 | 2.1822 | 2.0928 | 1.388
8.5042 | 81.7312 | 81.0662 | 79.3541 | 2.1821 | 2.0927 | 1.388
8.5083 | 81.7314 | 81.0676 | 79.3553 | 2.1819 | 2.0925 | 1.3879
8.5125 | 81.7259 | 81.0651 | 79.3567 | 2.1818 | 2.0924 | 1.3879
8.5167 | 81.7229 | 81.0627 | 79.3581 | 2.1817 | 2.0923 | 1.3879
8.5208 | 81.72 | 81.0614 | 79.3586 | 2.1816 | 2.0922 | 1.3878
8.525 | 81.7131 | 81.0599 | 79.3593 | 2.1815 | 2.0922 | 1.3878
8.5292 | 81.7194 | 81.0624 | 79.3611 | 2.1815 | 2.0921 | 1.3878
8.5333 | 81.7229 | 81.0649 | 79.3627 | 2.1814 | 2.092 | 1.3877
8.5375 | 81.7238 | 81.0674 | 79.3653 | 2.1813 | 2.0919 | 1.3877
8.5417 | 81.7277 | 81.07 | 79.3677 | 2.1813 | 2.0919 | 1.3876
8.5458 | 81.7259 | 81.0721 | 79.368 | 2.1812 | 2.0918 | 1.3876
8.55 | 81.7244 | 81.0739 | 79.3685 | 2.1811 | 2.0917 | 1.3875
8.5542 | 81.7275 | 81.079 | 79.3724 | 2.181 | 2.0916 | 1.3874
8.5583 | 81.7332 | 81.0842 | 79.3759 | 2.1809 | 2.0915 | 1.3874
8.5625 | 81.7336 | 81.0851 | 79.377 | 2.1808 | 2.0914 | 1.3873
8.5667 | 81.7341 | 81.0865 | 79.3781 | 2.1807 | 2.0913 | 1.3873
8.5708 | 81.7413 | 81.0886 | 79.38 | 2.1806 | 2.0912 | 1.3872
8.575 | 81.7457 | 81.0908 | 79.3818 | 2.1804 | 2.091 | 1.3871
8.5792 | 81.7415 | 81.0854 | 79.3766 | 2.1804 | 2.091 | 1.3871
8.5833 | 81.7383 | 81.0807 | 79.3713 | 2.1803 | 2.091 | 1.3871
8.5875 | 81.748 | 81.0852 | 79.3745 | 2.1801 | 2.0909 | 1.387
8.5917 | 81.7466 | 81.0891 | 79.3775 | 2.1798 | 2.0907 | 1.3869
8.5958 | 81.7354 | 81.0935 | 79.3735 | 2.18 | 2.0907 | 1.387
8.6 | 81.7251 | 81.0964 | 79.3706 | 2.18 | 2.0907 | 1.3871
8.6042 | 81.7285 | 81.1231 | 79.3899 | 2.1797 | 2.0903 | 1.3868
8.6083 | 81.7377 | 81.1479 | 79.4087 | 2.1794 | 2.09 | 1.3865
8.6125 | 81.734 | 81.149 | 79.4087 | 2.1798 | 2.09 | 1.3866
8.6167 | 81.7192 | 81.152 | 79.4081 | 2.18 | 2.09 | 1.3868
8.6208 | 81.7151 | 81.1465 | 79.4127 | 2.1797 | 2.0896 | 1.3863
8.625 | 81.7192 | 81.1448 | 79.4157 | 2.1792 | 2.0891 | 1.3859
8.6292 | 81.7404 | 81.1141 | 79.3961 | 2.1793 | 2.0894 | 1.3863
8.6333 | 81.7537 | 81.0871 | 79.3766 | 2.1796 | 2.0897 | 1.3866
8.6375 | 81.7666 | 81.0848 | 79.3739 | 2.1792 | 2.0893 | 1.3862
8.6417 | 81.7882 | 81.0801 | 79.3729 | 2.1787 | 2.0889 | 1.3857
8.6458 | 81.7921 | 81.1055 | 79.3841 | 2.1787 | 2.0893 | 1.3862
8.65 | 81.8107 | 81.125 | 79.396 | 2.1787 | 2.0896 | 1.3866
8.6542 | 81.8012 | 81.1418 | 79.4 | 2.1784 | 2.0891 | 1.3861
8.6583 | 81.7731 | 81.1569 | 79.404 | 2.1779 | 2.0887 | 1.3857
8.6625 | 81.7737 | 81.1639 | 79.4168 | 2.1779 | 2.0888 | 1.3859
8.6667 | 81.7697 | 81.1739 | 79.4267 | 2.1778 | 2.0889 | 1.3861
8.6708 | 81.7496 | 81.1408 | 79.3992 | 2.1777 | 2.0886 | 1.3859
8.675 | 81.7442 | 81.1113 | 79.3729 | 2.1775 | 2.0884 | 1.3857
8.6792 | 81.738 | 81.1399 | 79.3956 | 2.1775 | 2.0882 | 1.3857
8.6833 | 81.7823 | 81.1637 | 79.4194 | 2.1772 | 2.0881 | 1.3856
8.6875 | 81.8016 | 81.168 | 79.4109 | 2.177 | 2.0881 | 1.3857
8.6917 | 81.8054 | 81.1717 | 79.4032 | 2.177 | 2.0881 | 1.3858
8.6958 | 81.8143 | 81.1849 | 79.4141 | 2.1769 | 2.0877 | 1.3855
8.7 | 81.7794 | 81.2005 | 79.4234 | 2.1766 | 2.0873 | 1.3852
8.7042 | 81.7411 | 81.1911 | 79.4177 | 2.1766 | 2.0874 | 1.3854
8.7083 | 81.7205 | 81.1849 | 79.4109 | 2.1767 | 2.0874 | 1.3856
8.7125 | 81.6996 | 81.1881 | 79.4037 | 2.1766 | 2.0869 | 1.3853
8.7167 | 81.6587 | 81.1901 | 79.3989 | 2.1766 | 2.0865 | 1.3851
8.7208 | 81.6606 | 81.2242 | 79.4196 | 2.1766 | 2.0864 | 1.3851
8.725 | 81.6422 | 81.2556 | 79.4422 | 2.1764 | 2.0863 | 1.3852
8.7292 | 81.6467 | 81.2309 | 79.4225 | 2.1764 | 2.0861 | 1.3852
8.7333 | 81.6498 | 81.2121 | 79.402 | 2.1764 | 2.0859 | 1.3851
8.7375 | 81.6511 | 81.2175 | 79.413 | 2.1764 | 2.0856 | 1.385
8.7417 | 81.6562 | 81.2225 | 79.4212 | 2.1764 | 2.0852 | 1.3848
8.7458 | 81.6647 | 81.2275 | 79.4185 | 2.1763 | 2.0853 | 1.385
8.75 | 81.7118 | 81.23 | 79.4178 | 2.176 | 2.0852 | 1.3851
8.7542 | 81.7482 | 81.2349 | 79.4166 | 2.1758 | 2.0849 | 1.3849
8.7583 | 81.8236 | 81.2398 | 79.4166 | 2.1759 | 2.0845 | 1.3847
8.7625 | 81.8384 | 81.2449 | 79.4273 | 2.1757 | 2.0845 | 1.3848
8.7667 | 81.8417 | 81.2515 | 79.435 | 2.1756 | 2.0845 | 1.3848
8.7708 | 81.8439 | 81.2339 | 79.417 | 2.1752 | 2.0843 | 1.3848
8.775 | 81.8395 | 81.2172 | 79.4004 | 2.1747 | 2.0841 | 1.3848
8.7792 | 81.8695 | 81.2502 | 79.417 | 2.1741 | 2.0838 | 1.3846
8.7833 | 81.9155 | 81.2769 | 79.4351 | 2.1738 | 2.0836 | 1.3845
8.7875 | 81.9277 | 81.2785 | 79.435 | 2.1733 | 2.0836 | 1.3846
8.7917 | 81.9356 | 81.2832 | 79.4327 | 2.1728 | 2.0835 | 1.3847
8.7958 | 81.9275 | 81.2706 | 79.4219 | 2.1722 | 2.0832 | 1.3846
8.8 | 81.9084 | 81.2608 | 79.4109 | 2.1717 | 2.0828 | 1.3844
8.8042 | 81.9065 | 81.29 | 79.4248 | 2.1712 | 2.0826 | 1.3844
8.8083 | 81.8953 | 81.3131 | 79.4398 | 2.1708 | 2.0824 | 1.3844
8.8125 | 81.8774 | 81.3179 | 79.433 | 2.1705 | 2.0822 | 1.3844
8.8167 | 81.8792 | 81.3248 | 79.4268 | 2.1702 | 2.082 | 1.3844
8.8208 | 81.8822 | 81.3344 | 79.4306 | 2.1698 | 2.0816 | 1.3843
8.825 | 81.8768 | 81.3452 | 79.4329 | 2.1696 | 2.0812 | 1.3842
8.8292 | 81.8775 | 81.3544 | 79.4346 | 2.1694 | 2.0809 | 1.3842
8.8333 | 81.8564 | 81.3623 | 79.436 | 2.1693 | 2.0807 | 1.3843
8.8375 | 81.8317 | 81.3726 | 79.4312 | 2.1691 | 2.0802 | 1.3842
8.8417 | 81.8287 | 81.3817 | 79.4288 | 2.169 | 2.0798 | 1.3841
8.8458 | 81.8405 | 81.4008 | 79.4399 | 2.1687 | 2.0794 | 1.384
8.85 | 81.8522 | 81.4209 | 79.4497 | 2.1687 | 2.0791 | 1.384
8.8542 | 81.8529 | 81.4084 | 79.4421 | 2.1687 | 2.0788 | 1.384
8.8583 | 81.8418 | 81.4008 | 79.4324 | 2.1687 | 2.0785 | 1.384
8.8625 | 81.8274 | 81.4157 | 79.4322 | 2.1686 | 2.078 | 1.3839
8.8667 | 81.8122 | 81.4261 | 79.4347 | 2.1685 | 2.0775 | 1.3838
8.8708 | 81.8113 | 81.4494 | 79.4447 | 2.1685 | 2.0772 | 1.3838
8.875 | 81.8107 | 81.4721 | 79.4549 | 2.1684 | 2.0769 | 1.3838
8.8792 | 81.8188 | 81.4568 | 79.4474 | 2.1683 | 2.0765 | 1.3838
8.8833 | 81.8326 | 81.449 | 79.4367 | 2.1682 | 2.0762 | 1.3838
8.8875 | 81.8597 | 81.4638 | 79.4386 | 2.1681 | 2.0757 | 1.3837
8.8917 | 81.8767 | 81.4737 | 79.4426 | 2.168 | 2.0752 | 1.3836
8.8958 | 81.8868 | 81.496 | 79.4482 | 2.1679 | 2.0749 | 1.3836
8.9 | 81.8999 | 81.5164 | 79.4554 | 2.1676 | 2.0746 | 1.3836
8.9042 | 81.9111 | 81.5078 | 79.4518 | 2.1672 | 2.0742 | 1.3835
8.9083 | 81.9357 | 81.5062 | 79.4446 | 2.1669 | 2.0738 | 1.3835
8.9125 | 81.9486 | 81.5042 | 79.4444 | 2.1665 | 2.0735 | 1.3835
8.9167 | 81.9547 | 81.4955 | 79.4459 | 2.1662 | 2.0732 | 1.3834
8.9208 | 81.9508 | 81.506 | 79.4492 | 2.1657 | 2.0729 | 1.3834
8.925 | 81.9531 | 81.5123 | 79.4545 | 2.1653 | 2.0726 | 1.3833
8.9292 | 81.9704 | 81.509 | 79.4545 | 2.1647 | 2.0724 | 1.3833
8.9333 | 81.9942 | 81.514 | 79.4509 | 2.1642 | 2.0722 | 1.3833
8.9375 | 82.0121 | 81.5095 | 79.4483 | 2.1637 | 2.0719 | 1.3833
8.9417 | 82.0191 | 81.5039 | 79.4471 | 2.1633 | 2.0717 | 1.3832
8.9458 | 82.0036 | 81.52 | 79.45 | 2.1628 | 2.0715 | 1.3832
8.95 | 81.9943 | 81.5313 | 79.4549 | 2.1623 | 2.0712 | 1.3832
8.9542 | 81.9953 | 81.5349 | 79.4573 | 2.1617 | 2.071 | 1.3831
8.9583 | 82.0058 | 81.543 | 79.4568 | 2.1612 | 2.0709 | 1.3831
8.9625 | 82.0188 | 81.5364 | 79.4527 | 2.1607 | 2.0706 | 1.3831
8.9667 | 82.0254 | 81.5316 | 79.4496 | 2.1604 | 2.0704 | 1.3831
8.9708 | 82.019 | 81.5483 | 79.4527 | 2.1599 | 2.0701 | 1.383
8.975 | 82.0142 | 81.5597 | 79.4571 | 2.1594 | 2.0699 | 1.383
8.9792 | 82.0197 | 81.5657 | 79.4598 | 2.1589 | 2.0697 | 1.383
8.9833 | 82.033 | 81.5743 | 79.4606 | 2.1584 | 2.0695 | 1.383
8.9875 | 82.0384 | 81.568 | 79.4564 | 2.158 | 2.0693 | 1.3829
8.9917 | 82.0397 | 81.5647 | 79.453 | 2.1576 | 2.069 | 1.3829
8.9958 | 82.039 | 81.5825 | 79.4566 | 2.1571 | 2.0687 | 1.3829
9 | 82.034 | 81.595 | 79.4609 | 2.1567 | 2.0684 | 1.3828
9.0042 | 82.0444 | 81.6015 | 79.4627 | 2.1562 | 2.0683 | 1.3828
9.0083 | 82.0598 | 81.6099 | 79.4634 | 2.1558 | 2.068 | 1.3828
9.0125 | 82.0575 | 81.6055 | 79.4601 | 2.1554 | 2.0678 | 1.3828
9.0167 | 82.0576 | 81.6042 | 79.4573 | 2.155 | 2.0675 | 1.3827
9.0208 | 82.0566 | 81.6208 | 79.4611 | 2.1545 | 2.0672 | 1.3827
9.025 | 82.0488 | 81.633 | 79.4651 | 2.1541 | 2.0669 | 1.3826
9.0292 | 82.0658 | 81.6381 | 79.4658 | 2.1536 | 2.0667 | 1.3826
9.0333 | 82.0734 | 81.6451 | 79.466 | 2.1532 | 2.0664 | 1.3826
9.0375 | 82.0747 | 81.644 | 79.4639 | 2.1529 | 2.0661 | 1.3826
9.0417 | 82.072 | 81.645 | 79.4621 | 2.1525 | 2.0658 | 1.3825
9.0458 | 82.0737 | 81.6608 | 79.4655 | 2.152 | 2.0655 | 1.3825
9.05 | 82.0728 | 81.673 | 79.469 | 2.1516 | 2.0652 | 1.3825
9.0542 | 82.08 | 81.677 | 79.469 | 2.1512 | 2.065 | 1.3825
9.0583 | 82.0919 | 81.6833 | 79.4687 | 2.1509 | 2.0647 | 1.3824
9.0625 | 82.0831 | 81.685 | 79.4677 | 2.1505 | 2.0644 | 1.3824
9.0667 | 82.0877 | 81.688 | 79.4668 | 2.1501 | 2.0641 | 1.3824
9.0708 | 82.0867 | 81.7028 | 79.4696 | 2.1497 | 2.0638 | 1.3823
9.075 | 82.0947 | 81.7144 | 79.4725 | 2.1493 | 2.0634 | 1.3823
9.0792 | 82.1014 | 81.7189 | 79.4722 | 2.149 | 2.0632 | 1.3823
9.0833 | 82.1109 | 81.7253 | 79.4719 | 2.1485 | 2.0629 | 1.3823
9.0875 | 82.1084 | 81.7286 | 79.4716 | 2.1482 | 2.0625 | 1.3822
9.0917 | 82.1109 | 81.7329 | 79.4712 | 2.1478 | 2.0622 | 1.3822
9.0958 | 82.1134 | 81.7448 | 79.4733 | 2.1474 | 2.0619 | 1.3822
9.1 | 82.1199 | 81.7545 | 79.4755 | 2.1469 | 2.0616 | 1.3821
9.1042 | 82.1258 | 81.7598 | 79.4754 | 2.1466 | 2.0613 | 1.3821
9.1083 | 82.1315 | 81.7662 | 79.4753 | 2.1462 | 2.0609 | 1.3821
9.1125 | 82.131 | 81.7716 | 79.4755 | 2.1458 | 2.0606 | 1.382
9.1167 | 82.1338 | 81.7773 | 79.4755 | 2.1454 | 2.0603 | 1.382
9.1208 | 82.1361 | 81.7876 | 79.4769 | 2.145 | 2.06 | 1.382
9.125 | 82.1396 | 81.7968 | 79.4784 | 2.1446 | 2.0596 | 1.382
9.1292 | 82.1459 | 81.8033 | 79.4787 | 2.1442 | 2.0593 | 1.3819
9.1333 | 82.1491 | 81.8112 | 79.4791 | 2.1438 | 2.059 | 1.3819
9.1375 | 82.1537 | 81.8179 | 79.4796 | 2.1435 | 2.0586 | 1.3819
9.1417 | 82.1577 | 81.8251 | 79.4799 | 2.143 | 2.0583 | 1.3818
9.1458 | 82.1615 | 81.835 | 79.4809 | 2.1427 | 2.0579 | 1.3818
9.15 | 82.167 | 81.844 | 79.482 | 2.1422 | 2.0576 | 1.3818
9.1542 | 82.1736 | 81.8522 | 79.4825 | 2.1418 | 2.0572 | 1.3817
9.1583 | 82.1778 | 81.8607 | 79.4829 | 2.1414 | 2.0569 | 1.3817
9.1625 | 82.1785 | 81.8686 | 79.4836 | 2.1411 | 2.0565 | 1.3817
9.1667 | 82.185 | 81.8769 | 79.4841 | 2.1406 | 2.0561 | 1.3817
9.1708 | 82.1831 | 81.8868 | 79.485 | 2.1402 | 2.0558 | 1.3816
9.175 | 82.1917 | 81.8963 | 79.4861 | 2.1398 | 2.0554 | 1.3816
9.1792 | 82.1993 | 81.9047 | 79.4867 | 2.1394 | 2.055 | 1.3816
9.1833 | 82.2009 | 81.9141 | 79.4873 | 2.1389 | 2.0546 | 1.3815
9.1875 | 82.2041 | 81.9237 | 79.488 | 2.1386 | 2.0542 | 1.3815
9.1917 | 82.211 | 81.9329 | 79.4887 | 2.1381 | 2.0538 | 1.3815
9.1958 | 82.2101 | 81.9429 | 79.4895 | 2.1377 | 2.0534 | 1.3814
9.2 | 82.2216 | 81.9527 | 79.4903 | 2.1373 | 2.053 | 1.3814
9.2042 | 82.2286 | 81.9619 | 79.491 | 2.1368 | 2.0526 | 1.3814
9.2083 | 82.2293 | 81.9717 | 79.4918 | 2.1364 | 2.0522 | 1.3813
9.2125 | 82.2331 | 81.9818 | 79.4926 | 2.136 | 2.0518 | 1.3813
9.2167 | 82.2388 | 81.9918 | 79.4932 | 2.1355 | 2.0513 | 1.3813
9.2208 | 82.2408 | 82.0025 | 79.4941 | 2.135 | 2.0509 | 1.3812
9.225 | 82.2537 | 82.013 | 79.4952 | 2.1346 | 2.0505 | 1.3812
9.2292 | 82.2575 | 82.0231 | 79.496 | 2.1341 | 2.05 | 1.3811
9.2333 | 82.2613 | 82.0335 | 79.4967 | 2.1337 | 2.0496 | 1.3811
9.2375 | 82.2627 | 82.0436 | 79.4974 | 2.1332 | 2.0492 | 1.3811
9.2417 | 82.2684 | 82.0543 | 79.498 | 2.1327 | 2.0487 | 1.381
9.2458 | 82.276 | 82.0655 | 79.4989 | 2.1322 | 2.0482 | 1.381
9.25 | 82.2843 | 82.0767 | 79.4997 | 2.1317 | 2.0478 | 1.381
9.2542 | 82.2929 | 82.0884 | 79.5006 | 2.1313 | 2.0473 | 1.3809
9.2583 | 82.2927 | 82.1 | 79.5016 | 2.1308 | 2.0468 | 1.3809
9.2625 | 82.2965 | 82.1112 | 79.5025 | 2.1303 | 2.0464 | 1.3809
9.2667 | 82.3017 | 82.123 | 79.5036 | 2.1298 | 2.0459 | 1.3808
9.2708 | 82.3112 | 82.1344 | 79.5045 | 2.1293 | 2.0454 | 1.3808
9.275 | 82.319 | 82.1461 | 79.505 | 2.1288 | 2.0449 | 1.3807
9.2792 | 82.3285 | 82.1585 | 79.506 | 2.1283 | 2.0444 | 1.3807
9.2833 | 82.3302 | 82.1707 | 79.5071 | 2.1277 | 2.0439 | 1.3807
9.2875 | 82.3329 | 82.1833 | 79.5081 | 2.1272 | 2.0434 | 1.3806
9.2917 | 82.344 | 82.1961 | 79.5089 | 2.1266 | 2.0428 | 1.3806
9.2958 | 82.3473 | 82.2088 | 79.5098 | 2.1261 | 2.0423 | 1.3805
9.3 | 82.3573 | 82.2218 | 79.511 | 2.1256 | 2.0418 | 1.3805
9.3042 | 82.3651 | 82.2351 | 79.5121 | 2.125 | 2.0412 | 1.3804
9.3083 | 82.3656 | 82.2484 | 79.5131 | 2.1244 | 2.0407 | 1.3804
9.3125 | 82.3758 | 82.2624 | 79.5142 | 2.1239 | 2.0401 | 1.3804
9.3167 | 82.3825 | 82.2764 | 79.5152 | 2.1233 | 2.0396 | 1.3803
9.3208 | 82.3871 | 82.29 | 79.5162 | 2.1227 | 2.039 | 1.3803
9.325 | 82.3992 | 82.3041 | 79.5173 | 2.1221 | 2.0384 | 1.3802
9.3292 | 82.4049 | 82.3176 | 79.5182 | 2.1215 | 2.0378 | 1.3802
9.3333 | 82.4135 | 82.3313 | 79.519 | 2.1209 | 2.0372 | 1.3801
9.3375 | 82.4291 | 82.3483 | 79.5211 | 2.1203 | 2.0366 | 1.3801
9.3417 | 82.4393 | 82.3649 | 79.5232 | 2.1196 | 2.036 | 1.38
9.3458 | 82.4544 | 82.3837 | 79.5254 | 2.1189 | 2.0354 | 1.38
9.35 | 82.4709 | 82.4027 | 79.5273 | 2.1182 | 2.0347 | 1.3799
9.3542 | 82.4704 | 82.4052 | 79.5264 | 2.1175 | 2.0342 | 1.3799
9.3583 | 82.47 | 82.4086 | 79.5256 | 2.1169 | 2.0336 | 1.3798
9.3625 | 82.4485 | 82.3914 | 79.5215 | 2.1164 | 2.0332 | 1.3798
9.3667 | 82.4278 | 82.3745 | 79.5177 | 2.1158 | 2.0327 | 1.3798
9.3708 | 82.4154 | 82.3688 | 79.5148 | 2.1153 | 2.0324 | 1.3798
9.375 | 82.4078 | 82.3625 | 79.5119 | 2.1148 | 2.032 | 1.3798
9.3792 | 82.4182 | 82.3736 | 79.5136 | 2.1144 | 2.0317 | 1.3798
9.3833 | 82.4272 | 82.3844 | 79.5152 | 2.114 | 2.0314 | 1.3798
9.3875 | 82.4327 | 82.3922 | 79.5163 | 2.1136 | 2.0312 | 1.3798
9.3917 | 82.4369 | 82.4 | 79.5174 | 2.1132 | 2.0309 | 1.3798
9.3958 | 82.4499 | 82.4133 | 79.5173 | 2.1127 | 2.0305 | 1.3798
9.4 | 82.4583 | 82.4259 | 79.5172 | 2.1122 | 2.0301 | 1.3798
9.4042 | 82.4765 | 82.4411 | 79.5188 | 2.1117 | 2.0298 | 1.3797
9.4083 | 82.4909 | 82.4562 | 79.5202 | 2.1112 | 2.0294 | 1.3797
9.4125 | 82.4956 | 82.4659 | 79.5219 | 2.1106 | 2.029 | 1.3797
9.4167 | 82.5048 | 82.4762 | 79.5237 | 2.1101 | 2.0286 | 1.3797
9.4208 | 82.5111 | 82.4904 | 79.5231 | 2.1095 | 2.0281 | 1.3797
9.425 | 82.5196 | 82.5043 | 79.5229 | 2.1089 | 2.0277 | 1.3797
9.4292 | 82.5343 | 82.5216 | 79.5286 | 2.1082 | 2.0272 | 1.3796
9.4333 | 82.5495 | 82.5391 | 79.534 | 2.1076 | 2.0267 | 1.3795
9.4375 | 82.5539 | 82.5484 | 79.5339 | 2.107 | 2.0262 | 1.3795
9.4417 | 82.561 | 82.5588 | 79.5339 | 2.1063 | 2.0257 | 1.3795
9.4458 | 82.5791 | 82.5738 | 79.5372 | 2.1055 | 2.0252 | 1.3794
9.45 | 82.5949 | 82.5891 | 79.54 | 2.1047 | 2.0246 | 1.3793
9.4542 | 82.5987 | 82.5903 | 79.5312 | 2.1041 | 2.0242 | 1.3794
9.4583 | 82.6066 | 82.593 | 79.5224 | 2.1035 | 2.0238 | 1.3794
9.4625 | 82.617 | 82.6072 | 79.5255 | 2.1025 | 2.0232 | 1.3793
9.4667 | 82.6295 | 82.6206 | 79.5288 | 2.1016 | 2.0225 | 1.3791
9.4708 | 82.6323 | 82.6406 | 79.524 | 2.1011 | 2.0222 | 1.3793
9.475 | 82.6341 | 82.6581 | 79.5207 | 2.1005 | 2.0218 | 1.3795
9.4792 | 82.6392 | 82.696 | 79.5405 | 2.0995 | 2.0209 | 1.3791
9.4833 | 82.6544 | 82.732 | 79.56 | 2.0985 | 2.02 | 1.3788
9.4875 | 82.6605 | 82.7492 | 79.5607 | 2.0979 | 2.0196 | 1.3791
9.4917 | 82.6548 | 82.7691 | 79.5607 | 2.0975 | 2.0191 | 1.3793
9.4958 | 82.6575 | 82.7758 | 79.5608 | 2.0966 | 2.0181 | 1.3788
9.5 | 82.6589 | 82.7874 | 79.5598 | 2.0955 | 2.0172 | 1.3784
9.5042 | 82.6865 | 82.7831 | 79.5485 | 2.0949 | 2.0169 | 1.3787
9.5083 | 82.7189 | 82.7821 | 79.5373 | 2.0943 | 2.0165 | 1.3791
9.5125 | 82.7373 | 82.7929 | 79.5312 | 2.0933 | 2.0156 | 1.3787
9.5167 | 82.7606 | 82.8014 | 79.5273 | 2.0922 | 2.0147 | 1.3783
9.5208 | 82.7782 | 82.8429 | 79.5455 | 2.0913 | 2.0143 | 1.3786
9.525 | 82.8042 | 82.8795 | 79.5635 | 2.0904 | 2.0138 | 1.3789
9.5292 | 82.8156 | 82.8951 | 79.5551 | 2.0893 | 2.0129 | 1.3786
9.5333 | 82.8008 | 82.9118 | 79.5465 | 2.0882 | 2.0121 | 1.3783
9.5375 | 82.8127 | 82.9351 | 79.56 | 2.0873 | 2.0114 | 1.3784
9.5417 | 82.8192 | 82.9607 | 79.5714 | 2.0862 | 2.0107 | 1.3785
9.5458 | 82.8189 | 82.9584 | 79.549 | 2.0852 | 2.01 | 1.3784
9.55 | 82.835 | 82.9577 | 79.5279 | 2.0843 | 2.0092 | 1.3784
9.5542 | 82.8521 | 82.9982 | 79.5477 | 2.0832 | 2.0083 | 1.3782
9.5583 | 82.8944 | 83.0345 | 79.5686 | 2.0819 | 2.0074 | 1.378
9.5625 | 82.926 | 83.0597 | 79.5642 | 2.0808 | 2.0067 | 1.3783
9.5667 | 82.9544 | 83.0853 | 79.5615 | 2.0797 | 2.0061 | 1.3784
9.5708 | 82.9754 | 83.0994 | 79.5578 | 2.0784 | 2.005 | 1.3781
9.575 | 82.9734 | 83.117 | 79.5529 | 2.077 | 2.004 | 1.3778
9.5792 | 82.9767 | 83.147 | 79.5631 | 2.0758 | 2.0032 | 1.378
9.5833 | 83.0071 | 83.1767 | 79.5707 | 2.0743 | 2.0024 | 1.3782
9.5875 | 83.0099 | 83.1975 | 79.5587 | 2.0731 | 2.0014 | 1.378
9.5917 | 83.0094 | 83.2186 | 79.5502 | 2.0719 | 2.0003 | 1.3779
9.5958 | 83.0186 | 83.2634 | 79.5688 | 2.0708 | 1.9993 | 1.3778
9.6 | 82.9981 | 83.3078 | 79.5881 | 2.0695 | 1.9982 | 1.3777
9.6042 | 83.0024 | 83.3158 | 79.5739 | 2.0683 | 1.9973 | 1.3778
9.6083 | 83.0122 | 83.3288 | 79.5581 | 2.0672 | 1.9964 | 1.3779
9.6125 | 83.0132 | 83.3526 | 79.5613 | 2.0661 | 1.9952 | 1.3777
9.6167 | 82.9975 | 83.3762 | 79.5642 | 2.0653 | 1.9939 | 1.3774
9.6208 | 83.0124 | 83.4153 | 79.5733 | 2.0642 | 1.993 | 1.3776
9.625 | 83.0206 | 83.4521 | 79.5836 | 2.0631 | 1.9921 | 1.3777
9.6292 | 83.0512 | 83.4653 | 79.5727 | 2.0618 | 1.9909 | 1.3775
9.6333 | 83.1158 | 83.4824 | 79.5618 | 2.0608 | 1.9898 | 1.3774
9.6375 | 83.1374 | 83.5154 | 79.5732 | 2.0595 | 1.9887 | 1.3774
9.6417 | 83.1479 | 83.5483 | 79.5827 | 2.0584 | 1.9875 | 1.3773
9.6458 | 83.1706 | 83.5698 | 79.5728 | 2.0569 | 1.9865 | 1.3774
9.65 | 83.1888 | 83.5909 | 79.5644 | 2.0553 | 1.9854 | 1.3774
9.6542 | 83.2336 | 83.6293 | 79.5714 | 2.0537 | 1.9841 | 1.3773
9.6583 | 83.3036 | 83.6657 | 79.5794 | 2.0522 | 1.9829 | 1.3771
9.6625 | 83.3362 | 83.6986 | 79.5854 | 2.0505 | 1.9818 | 1.3772
9.6667 | 83.3525 | 83.7275 | 79.5886 | 2.0489 | 1.9806 | 1.3773
9.6708 | 83.3652 | 83.7342 | 79.5746 | 2.047 | 1.9793 | 1.3772
9.675 | 83.3732 | 83.74 | 79.5617 | 2.0451 | 1.9779 | 1.3771
9.6792 | 83.397 | 83.782 | 79.576 | 2.0432 | 1.9764 | 1.377
9.6833 | 83.4276 | 83.8194 | 79.5918 | 2.0414 | 1.975 | 1.3769
9.6875 | 83.44 | 83.8419 | 79.5888 | 2.0396 | 1.9736 | 1.377
9.6917 | 83.4507 | 83.8644 | 79.5847 | 2.0378 | 1.9722 | 1.377
9.6958 | 83.4654 | 83.8787 | 79.5806 | 2.0359 | 1.9706 | 1.3769
9.7 | 83.4783 | 83.8951 | 79.5759 | 2.034 | 1.9689 | 1.3768
9.7042 | 83.5013 | 83.9328 | 79.5847 | 2.0322 | 1.9673 | 1.3768
9.7083 | 83.5169 | 83.9666 | 79.5941 | 2.0304 | 1.9657 | 1.3768
9.7125 | 83.5192 | 83.987 | 79.5887 | 2.0286 | 1.9641 | 1.3768
9.7167 | 83.5373 | 84.0082 | 79.5842 | 2.0268 | 1.9624 | 1.3767
9.7208 | 83.5607 | 84.0343 | 79.59 | 2.0248 | 1.9606 | 1.3766
9.725 | 83.5904 | 84.0628 | 79.5946 | 2.0229 | 1.9588 | 1.3765
9.7292 | 83.6147 | 84.0841 | 79.5932 | 2.0211 | 1.957 | 1.3766
9.7333 | 83.6333 | 84.1066 | 79.5912 | 2.0193 | 1.9553 | 1.3766
9.7375 | 83.6322 | 84.129 | 79.5887 | 2.0174 | 1.9533 | 1.3765
9.7417 | 83.6437 | 84.1507 | 79.5882 | 2.0155 | 1.9514 | 1.3764
9.7458 | 83.6579 | 84.1854 | 79.5974 | 2.0136 | 1.9495 | 1.3764
9.75 | 83.6745 | 84.2202 | 79.606 | 2.0117 | 1.9476 | 1.3763
9.7542 | 83.6899 | 84.2254 | 79.5997 | 2.0099 | 1.9457 | 1.3763
9.7583 | 83.7041 | 84.2321 | 79.5916 | 2.0081 | 1.9439 | 1.3763
9.7625 | 83.7316 | 84.2592 | 79.5922 | 2.0061 | 1.9418 | 1.3762
9.7667 | 83.7575 | 84.2827 | 79.5948 | 2.0042 | 1.9397 | 1.3761
9.7708 | 83.7986 | 84.3278 | 79.6016 | 2.0021 | 1.9377 | 1.3761
9.775 | 83.839 | 84.3748 | 79.6091 | 2.0001 | 1.9357 | 1.3761
9.7792 | 83.8681 | 84.3863 | 79.6041 | 1.998 | 1.9336 | 1.3761
9.7833 | 83.9046 | 84.4047 | 79.5964 | 1.9958 | 1.9314 | 1.376
9.7875 | 83.9375 | 84.4312 | 79.5975 | 1.9935 | 1.9292 | 1.376
9.7917 | 83.9661 | 84.4535 | 79.6002 | 1.9912 | 1.9269 | 1.3759
9.7958 | 83.9975 | 84.4873 | 79.6043 | 1.9889 | 1.9247 | 1.3759
9.8 | 84.0307 | 84.5191 | 79.6098 | 1.9864 | 1.9225 | 1.3759
9.8042 | 84.0658 | 84.5336 | 79.6076 | 1.9839 | 1.9202 | 1.3758
9.8083 | 84.1075 | 84.5544 | 79.6023 | 1.9814 | 1.9179 | 1.3758
9.8125 | 84.1509 | 84.5817 | 79.6017 | 1.9787 | 1.9155 | 1.3758
9.8167 | 84.1825 | 84.6059 | 79.6025 | 1.9761 | 1.9132 | 1.3757
9.8208 | 84.2076 | 84.6402 | 79.6053 | 1.9735 | 1.9108 | 1.3757
9.825 | 84.2293 | 84.6725 | 79.6098 | 1.9707 | 1.9084 | 1.3757
9.8292 | 84.2596 | 84.6958 | 79.6105 | 1.9679 | 1.9059 | 1.3756
9.8333 | 84.2932 | 84.7238 | 79.6082 | 1.9651 | 1.9034 | 1.3756
9.8375 | 84.3357 | 84.7508 | 79.6057 | 1.9623 | 1.9008 | 1.3756
9.8417 | 84.369 | 84.7768 | 79.6043 | 1.9595 | 1.8982 | 1.3756
9.8458 | 84.3928 | 84.812 | 79.6067 | 1.9566 | 1.8956 | 1.3755
9.85 | 84.419 | 84.8449 | 79.6104 | 1.9537 | 1.8929 | 1.3755
9.8542 | 84.4523 | 84.8739 | 79.6124 | 1.9506 | 1.8902 | 1.3755
9.8583 | 84.4933 | 84.9056 | 79.612 | 1.9476 | 1.8875 | 1.3755
9.8625 | 84.5347 | 84.9314 | 79.6084 | 1.9446 | 1.8847 | 1.3754
9.8667 | 84.5696 | 84.9582 | 79.6056 | 1.9416 | 1.8818 | 1.3754
9.8708 | 84.5991 | 84.9949 | 79.6081 | 1.9385 | 1.8789 | 1.3754
9.875 | 84.6286 | 85.03 | 79.6115 | 1.9352 | 1.8759 | 1.3753
9.8792 | 84.6702 | 85.0624 | 79.6131 | 1.932 | 1.873 | 1.3753
9.8833 | 84.7162 | 85.096 | 79.6132 | 1.9287 | 1.8699 | 1.3754
9.8875 | 84.7542 | 85.1227 | 79.6093 | 1.9255 | 1.8668 | 1.3753
9.8917 | 84.7902 | 85.1501 | 79.606 | 1.9221 | 1.8636 | 1.3753
9.8958 | 84.8212 | 85.1886 | 79.6085 | 1.9187 | 1.8604 | 1.3753
9.9 | 84.8535 | 85.2246 | 79.6113 | 1.9152 | 1.8571 | 1.3753
9.9042 | 84.9015 | 85.2569 | 79.6116 | 1.9117 | 1.8538 | 1.3753
9.9083 | 84.9465 | 85.2897 | 79.6108 | 1.9082 | 1.8505 | 1.3753
9.9125 | 84.9881 | 85.3182 | 79.607 | 1.9046 | 1.847 | 1.3753
9.9167 | 85.025 | 85.3473 | 79.6034 | 1.901 | 1.8435 | 1.3753
9.9208 | 85.0635 | 85.3868 | 79.6049 | 1.8972 | 1.8399 | 1.3753
9.925 | 85.1034 | 85.4247 | 79.6063 | 1.8935 | 1.8363 | 1.3753
9.9292 | 85.1526 | 85.4551 | 79.6044 | 1.8896 | 1.8326 | 1.3753
9.9333 | 85.2011 | 85.4874 | 79.6016 | 1.8859 | 1.8289 | 1.3753
9.9375 | 85.2377 | 85.5166 | 79.597 | 1.8819 | 1.8251 | 1.3754
9.9417 | 85.2799 | 85.5466 | 79.5921 | 1.878 | 1.8212 | 1.3754
9.9458 | 85.3207 | 85.5852 | 79.5909 | 1.8739 | 1.8172 | 1.3754
9.95 | 85.3702 | 85.6217 | 79.589 | 1.8698 | 1.8132 | 1.3755
9.9542 | 85.4199 | 85.6511 | 79.5831 | 1.8657 | 1.8092 | 1.3756
9.9583 | 85.4717 | 85.6818 | 79.576 | 1.8616 | 1.8051 | 1.3757
9.9625 | 85.5131 | 85.7113 | 79.5676 | 1.8573 | 1.8008 | 1.3758
9.9667 | 85.5563 | 85.7411 | 79.5579 | 1.853 | 1.7965 | 1.3759
9.9708 | 85.6064 | 85.7765 | 79.5496 | 1.8486 | 1.7922 | 1.3761
9.975 | 85.6578 | 85.8097 | 79.539 | 1.8441 | 1.7878 | 1.3763
9.9792 | 85.7115 | 85.8372 | 79.5239 | 1.8396 | 1.7833 | 1.3766
9.9833 | 85.7619 | 85.8655 | 79.5054 | 1.8351 | 1.7788 | 1.3768
9.9875 | 85.8104 | 85.8948 | 79.4854 | 1.8305 | 1.7741 | 1.3772
9.9917 | 85.8559 | 85.9236 | 79.4624 | 1.8257 | 1.7694 | 1.3776
9.9958 | 85.9092 | 85.9549 | 79.4375 | 1.8209 | 1.7646 | 1.378
10 | 85.9651 | 85.9847 | 79.4095 | 1.8161 | 1.7598 | 1.3786
10.0042 | 86.0181 | 86.0099 | 79.3746 | 1.8112 | 1.7549 | 1.3792
10.0083 | 86.0675 | 86.0345 | 79.3357 | 1.8063 | 1.7499 | 1.3799
10.0125 | 85.6632 | 85.6164 | 79.3755 | 1.805 | 1.7484 | 1.3801
10.0167 | 85.2521 | 85.1919 | 79.4223 | 1.8036 | 1.7469 | 1.3802
10.0208 | 84.9792 | 84.9069 | 79.456 | 1.8009 | 1.7442 | 1.3807
10.025 | 84.7049 | 84.6182 | 79.4949 | 1.7982 | 1.7414 | 1.3812
10.0292 | 84.7244 | 84.7089 | 79.4744 | 1.7988 | 1.7426 | 1.3812
10.0333 | 84.8216 | 84.8005 | 79.451 | 1.8 | 1.7439 | 1.3811
10.0375 | 84.6616 | 84.6149 | 79.4794 | 1.8009 | 1.745 | 1.381
10.0417 | 84.471 | 84.4248 | 79.5122 | 1.8019 | 1.7461 | 1.381
10.0458 | 84.5304 | 84.5261 | 79.5001 | 1.8018 | 1.7457 | 1.3812
10.05 | 84.6329 | 84.632 | 79.4863 | 1.8013 | 1.7453 | 1.3814
10.0542 | 84.6231 | 84.7252 | 79.4728 | 1.8021 | 1.7472 | 1.3812
10.0583 | 84.707 | 84.8195 | 79.4575 | 1.8039 | 1.7491 | 1.381
10.0625 | 84.6567 | 84.7047 | 79.4764 | 1.8036 | 1.7488 | 1.3812
10.0667 | 84.5485 | 84.584 | 79.4981 | 1.8034 | 1.7485 | 1.3813
10.0708 | 84.5971 | 84.7208 | 79.4777 | 1.8036 | 1.7485 | 1.3814
10.075 | 84.744 | 84.8634 | 79.4542 | 1.8037 | 1.7485 | 1.3815
10.0792 | 84.709 | 84.8159 | 79.4597 | 1.8042 | 1.7495 | 1.3814
10.0833 | 84.6832 | 84.7635 | 79.4661 | 1.8055 | 1.7506 | 1.3813
10.0875 | 84.6482 | 84.7113 | 79.4732 | 1.8051 | 1.7499 | 1.3815
10.0917 | 84.6219 | 84.657 | 79.4814 | 1.8047 | 1.7491 | 1.3817
10.0958 | 84.6261 | 84.7551 | 79.4656 | 1.8048 | 1.7498 | 1.3817
10.1 | 84.7182 | 84.8595 | 79.4476 | 1.8053 | 1.7505 | 1.3817
10.1042 | 84.682 | 84.7644 | 79.4601 | 1.8056 | 1.7509 | 1.3817
10.1083 | 84.632 | 84.6619 | 79.4747 | 1.8062 | 1.7514 | 1.3817
10.1125 | 84.59 | 84.6903 | 79.4699 | 1.8061 | 1.751 | 1.3818
10.1167 | 84.6359 | 84.7229 | 79.4642 | 1.806 | 1.7506 | 1.382
10.1208 | 84.6262 | 84.7602 | 79.4577 | 1.8061 | 1.7515 | 1.3819
10.125 | 84.6549 | 84.7999 | 79.4504 | 1.8069 | 1.7525 | 1.3819
10.1292 | 84.6314 | 84.7235 | 79.4606 | 1.8072 | 1.7525 | 1.3819
10.1333 | 84.5819 | 84.6402 | 79.4724 | 1.8071 | 1.7525 | 1.382
10.1375 | 84.5732 | 84.705 | 79.4624 | 1.8074 | 1.7526 | 1.3821
10.1417 | 84.6161 | 84.7775 | 79.4511 | 1.8075 | 1.7527 | 1.3822
10.1458 | 84.6267 | 84.7569 | 79.453 | 1.8079 | 1.7534 | 1.3821
10.15 | 84.6029 | 84.733 | 79.4554 | 1.8084 | 1.7543 | 1.3821
10.1542 | 84.5969 | 84.7019 | 79.4589 | 1.8087 | 1.7541 | 1.3822
10.1583 | 84.5726 | 84.668 | 79.463 | 1.8086 | 1.7538 | 1.3823
10.1625 | 84.5788 | 84.7235 | 79.4545 | 1.8089 | 1.7543 | 1.3823
10.1667 | 84.6121 | 84.7859 | 79.4449 | 1.8093 | 1.7548 | 1.3823
10.1708 | 84.6113 | 84.7377 | 79.4503 | 1.8096 | 1.7553 | 1.3823
10.175 | 84.5761 | 84.6828 | 79.4566 | 1.81 | 1.7558 | 1.3824
10.1792 | 84.5653 | 84.6923 | 79.4529 | 1.8102 | 1.7557 | 1.3825
10.1833 | 84.5704 | 84.7044 | 79.449 | 1.8103 | 1.7556 | 1.3826
10.1875 | 84.5825 | 84.7352 | 79.4523 | 1.8105 | 1.7562 | 1.3825
10.1917 | 84.5981 | 84.7681 | 79.4547 | 1.811 | 1.7568 | 1.3824
10.1958 | 84.6171 | 84.752 | 79.4842 | 1.8111 | 1.7568 | 1.3823
10.2 | 84.6138 | 84.7285 | 79.5135 | 1.8111 | 1.7568 | 1.3822
10.2042 | 84.5589 | 84.7084 | 79.4389 | 1.8117 | 1.7573 | 1.3827
10.2083 | 84.5331 | 84.6963 | 79.367 | 1.8122 | 1.7578 | 1.3833
10.2125 | 84.3928 | 84.5387 | 79.1683 | 1.8134 | 1.7592 | 1.3845
10.2167 | 84.2445 | 84.3857 | 78.9776 | 1.8146 | 1.7606 | 1.3857
10.2208 | 84.1944 | 84.3205 | 78.88 | 1.8159 | 1.7617 | 1.3873
10.225 | 84.1386 | 84.2571 | 78.7852 | 1.8169 | 1.7628 | 1.3888
10.2292 | 84.1566 | 84.3083 | 78.7671 | 1.8189 | 1.765 | 1.3911
10.2333 | 84.1895 | 84.3677 | 78.7494 | 1.8208 | 1.7671 | 1.3933
10.2375 | 84.1821 | 84.3419 | 78.7217 | 1.8224 | 1.769 | 1.3952
10.2417 | 84.1566 | 84.3123 | 78.6941 | 1.8239 | 1.7707 | 1.397
10.2458 | 84.2085 | 84.3824 | 78.7418 | 1.825 | 1.7719 | 1.3984
10.25 | 84.2689 | 84.45 | 78.783 | 1.826 | 1.7729 | 1.3998
10.2542 | 84.2796 | 84.4789 | 78.7808 | 1.8274 | 1.7747 | 1.4014
10.2583 | 84.295 | 84.5095 | 78.7798 | 1.8288 | 1.7764 | 1.4029
10.2625 | 84.2723 | 84.4699 | 78.7445 | 1.8296 | 1.7772 | 1.4038
10.2667 | 84.2354 | 84.4254 | 78.7118 | 1.8303 | 1.778 | 1.4047
10.2708 | 84.2683 | 84.4807 | 78.7338 | 1.8312 | 1.779 | 1.4057
10.275 | 84.3088 | 84.5367 | 78.7527 | 1.8321 | 1.78 | 1.4067
10.2792 | 84.2837 | 84.5049 | 78.7083 | 1.8331 | 1.7814 | 1.4079
10.2833 | 84.2484 | 84.4738 | 78.6696 | 1.8343 | 1.7827 | 1.409
10.2875 | 84.2374 | 84.459 | 78.6513 | 1.8349 | 1.7834 | 1.4097
10.2917 | 84.2255 | 84.4416 | 78.6326 | 1.8354 | 1.784 | 1.4104
10.2958 | 84.242 | 84.4849 | 78.6452 | 1.8364 | 1.7852 | 1.4115
10.3 | 84.2744 | 84.5301 | 78.6552 | 1.8375 | 1.7864 | 1.4125
10.3042 | 84.2407 | 84.4891 | 78.6138 | 1.8384 | 1.7875 | 1.4134
10.3083 | 84.2032 | 84.4473 | 78.5777 | 1.8392 | 1.7885 | 1.4142
10.3125 | 84.2153 | 84.4697 | 78.586 | 1.8399 | 1.7892 | 1.4148
10.3167 | 84.2336 | 84.4915 | 78.5906 | 1.8405 | 1.7898 | 1.4155
10.3208 | 84.2414 | 84.5054 | 78.5866 | 1.8414 | 1.791 | 1.4164
10.325 | 84.2513 | 84.5216 | 78.5822 | 1.8424 | 1.7922 | 1.4173
10.3292 | 84.2295 | 84.4796 | 78.546 | 1.843 | 1.793 | 1.4179
10.3333 | 84.2018 | 84.4374 | 78.5132 | 1.8436 | 1.7937 | 1.4185
10.3375 | 84.217 | 84.4648 | 78.5229 | 1.8443 | 1.7945 | 1.4192
10.3417 | 84.244 | 84.4924 | 78.5288 | 1.8449 | 1.7953 | 1.4198
10.3458 | 84.2318 | 84.484 | 78.5091 | 1.8457 | 1.7965 | 1.4206
10.35 | 84.216 | 84.4735 | 78.4926 | 1.8466 | 1.7976 | 1.4214
10.3542 | 84.1999 | 84.4707 | 78.4835 | 1.8471 | 1.7982 | 1.4218
10.3583 | 84.1834 | 84.464 | 78.4758 | 1.8476 | 1.7987 | 1.4222
10.3625 | 84.1895 | 84.4993 | 78.4927 | 1.8484 | 1.7996 | 1.4229
10.3667 | 84.1996 | 84.5352 | 78.5061 | 1.8492 | 1.8005 | 1.4235
10.3708 | 84.1754 | 84.5044 | 78.4782 | 1.85 | 1.8013 | 1.424
10.375 | 84.1376 | 84.4763 | 78.453 | 1.8508 | 1.8021 | 1.4245
10.3792 | 84.1423 | 84.4708 | 78.4494 | 1.8514 | 1.8027 | 1.4249
10.3833 | 84.1541 | 84.4683 | 78.4444 | 1.8519 | 1.8033 | 1.4252
10.3875 | 84.1654 | 84.4683 | 78.4363 | 1.8527 | 1.8043 | 1.4259
10.3917 | 84.1842 | 84.4692 | 78.4285 | 1.8536 | 1.8053 | 1.4265
10.3958 | 84.1718 | 84.4532 | 78.4144 | 1.8542 | 1.806 | 1.4268
10.4 | 84.1563 | 84.4334 | 78.4033 | 1.8547 | 1.8067 | 1.4272
10.4042 | 84.1677 | 84.4537 | 78.4109 | 1.8552 | 1.8075 | 1.4276
10.4083 | 84.1748 | 84.473 | 78.4157 | 1.8558 | 1.8083 | 1.4281
10.4125 | 84.1641 | 84.4624 | 78.4019 | 1.8565 | 1.8092 | 1.4285
10.4167 | 84.1375 | 84.4528 | 78.3893 | 1.8572 | 1.81 | 1.4289
10.4208 | 84.1193 | 84.4391 | 78.3794 | 1.8578 | 1.8107 | 1.4293
10.425 | 84.1071 | 84.425 | 78.3723 | 1.8583 | 1.8114 | 1.4296
10.4292 | 84.109 | 84.4354 | 78.3719 | 1.859 | 1.8123 | 1.43
10.4333 | 84.1294 | 84.4452 | 78.3709 | 1.8597 | 1.8131 | 1.4304
10.4375 | 84.1256 | 84.4374 | 78.366 | 1.8604 | 1.8139 | 1.4307
10.4417 | 84.1237 | 84.4278 | 78.3616 | 1.8609 | 1.8148 | 1.4311
10.4458 | 84.1313 | 84.4239 | 78.3539 | 1.8614 | 1.8155 | 1.4314
10.45 | 84.1375 | 84.4212 | 78.3453 | 1.8619 | 1.8162 | 1.4317
10.4542 | 84.1364 | 84.423 | 78.3448 | 1.8625 | 1.817 | 1.432
10.4583 | 84.1408 | 84.4254 | 78.3425 | 1.863 | 1.8179 | 1.4323
10.4625 | 84.123 | 84.413 | 78.3315 | 1.8635 | 1.8187 | 1.4326
10.4667 | 84.1065 | 84.3992 | 78.3223 | 1.864 | 1.8195 | 1.433
10.4708 | 84.1014 | 84.403 | 78.3153 | 1.8646 | 1.8202 | 1.4332
10.475 | 84.0821 | 84.4072 | 78.3089 | 1.8651 | 1.8209 | 1.4335
10.4792 | 84.0676 | 84.4047 | 78.3086 | 1.8658 | 1.8218 | 1.4338
10.4833 | 84.0458 | 84.4031 | 78.307 | 1.8665 | 1.8227 | 1.4342
10.4875 | 84.0259 | 84.3866 | 78.2925 | 1.8672 | 1.8235 | 1.4345
10.4917 | 84.0004 | 84.3711 | 78.2792 | 1.8681 | 1.8242 | 1.4348
10.4958 | 83.9934 | 84.379 | 78.2841 | 1.8689 | 1.825 | 1.435
10.5 | 83.976 | 84.3859 | 78.2888 | 1.8698 | 1.8258 | 1.4352
10.5042 | 83.9681 | 84.3754 | 78.2824 | 1.8706 | 1.8267 | 1.4356
10.5083 | 83.9771 | 84.3655 | 78.2758 | 1.8715 | 1.8276 | 1.4359
10.5125 | 83.9735 | 84.352 | 78.2651 | 1.8722 | 1.8284 | 1.4361
10.5167 | 83.9775 | 84.34 | 78.2548 | 1.8732 | 1.8291 | 1.4363
10.5208 | 83.978 | 84.3442 | 78.2603 | 1.874 | 1.83 | 1.4366
10.525 | 83.9689 | 84.349 | 78.2654 | 1.8748 | 1.8309 | 1.4368
10.5292 | 83.9739 | 84.3392 | 78.2525 | 1.8754 | 1.8318 | 1.4371
10.5333 | 83.9975 | 84.3331 | 78.2406 | 1.876 | 1.8327 | 1.4374
10.5375 | 84.0084 | 84.3415 | 78.2421 | 1.8766 | 1.8334 | 1.4375
10.5417 | 84.0181 | 84.3495 | 78.2427 | 1.8773 | 1.8341 | 1.4377
10.5458 | 84.0126 | 84.3488 | 78.2396 | 1.8778 | 1.835 | 1.438
10.55 | 83.9977 | 84.3462 | 78.2361 | 1.8783 | 1.8359 | 1.4383
10.5542 | 83.9907 | 84.339 | 78.2254 | 1.8788 | 1.8366 | 1.4384
10.5583 | 83.9975 | 84.3307 | 78.2163 | 1.8793 | 1.8372 | 1.4386
10.5625 | 83.9947 | 84.3442 | 78.2244 | 1.8798 | 1.838 | 1.4388
10.5667 | 83.9806 | 84.3542 | 78.2313 | 1.8805 | 1.8387 | 1.439
10.5708 | 83.9674 | 84.3407 | 78.2192 | 1.8811 | 1.8395 | 1.4392
10.575 | 83.9478 | 84.3281 | 78.207 | 1.8816 | 1.8403 | 1.4395
10.5792 | 83.9415 | 84.3267 | 78.2053 | 1.8821 | 1.8408 | 1.4396
10.5833 | 83.94 | 84.3236 | 78.2047 | 1.8828 | 1.8415 | 1.4397
10.5875 | 83.9272 | 84.3321 | 78.2088 | 1.8835 | 1.8422 | 1.4399
10.5917 | 83.9096 | 84.3376 | 78.2121 | 1.8843 | 1.843 | 1.4402
10.5958 | 83.8964 | 84.3212 | 78.1989 | 1.8849 | 1.8437 | 1.4403
10.6 | 83.8933 | 84.308 | 78.186 | 1.8856 | 1.8444 | 1.4405
10.6042 | 83.9003 | 84.3145 | 78.1912 | 1.8862 | 1.845 | 1.4406
10.6083 | 83.9033 | 84.3197 | 78.1964 | 1.887 | 1.8456 | 1.4407
10.6125 | 83.8985 | 84.3254 | 78.1923 | 1.8877 | 1.8463 | 1.4409
10.6167 | 83.8897 | 84.3295 | 78.1882 | 1.8884 | 1.847 | 1.4411
10.6208 | 83.8776 | 84.3263 | 78.1829 | 1.889 | 1.8475 | 1.4412
10.625 | 83.8786 | 84.3261 | 78.178 | 1.8897 | 1.848 | 1.4413
10.6292 | 83.8698 | 84.3258 | 78.1833 | 1.8904 | 1.8486 | 1.4414
10.6333 | 83.8549 | 84.3255 | 78.1876 | 1.8912 | 1.8493 | 1.4416
10.6375 | 83.8392 | 84.3103 | 78.1774 | 1.8919 | 1.8499 | 1.4418
10.6417 | 83.8221 | 84.2938 | 78.1678 | 1.8926 | 1.8505 | 1.4419
10.6458 | 83.8231 | 84.2988 | 78.17 | 1.8933 | 1.851 | 1.442
10.65 | 83.826 | 84.3033 | 78.1729 | 1.8941 | 1.8515 | 1.442
10.6542 | 83.8278 | 84.3015 | 78.173 | 1.8948 | 1.8522 | 1.4422
10.6583 | 83.8244 | 84.3028 | 78.1719 | 1.8956 | 1.8529 | 1.4424
10.6625 | 83.8182 | 84.2855 | 78.1631 | 1.8962 | 1.8535 | 1.4425
10.6667 | 83.8164 | 84.2692 | 78.155 | 1.8969 | 1.8541 | 1.4425
10.6708 | 83.8176 | 84.2768 | 78.1615 | 1.8976 | 1.8546 | 1.4426
10.675 | 83.8171 | 84.281 | 78.1685 | 1.8983 | 1.8552 | 1.4427
10.6792 | 83.8105 | 84.2688 | 78.1633 | 1.8989 | 1.856 | 1.4429
10.6833 | 83.8079 | 84.2597 | 78.1568 | 1.8995 | 1.8567 | 1.443
10.6875 | 83.8065 | 84.2451 | 78.1523 | 1.9001 | 1.8573 | 1.4431
10.6917 | 83.8105 | 84.2305 | 78.1483 | 1.9007 | 1.8579 | 1.4431
10.6958 | 83.8081 | 84.2384 | 78.153 | 1.9014 | 1.8586 | 1.4432
10.7 | 83.7975 | 84.2417 | 78.1586 | 1.902 | 1.8593 | 1.4433
10.7042 | 83.7829 | 84.2275 | 78.1519 | 1.9026 | 1.8601 | 1.4434
10.7083 | 83.7732 | 84.2172 | 78.144 | 1.9032 | 1.8608 | 1.4436
10.7125 | 83.7711 | 84.2098 | 78.144 | 1.9038 | 1.8615 | 1.4436
10.7167 | 83.7701 | 84.2028 | 78.1445 | 1.9045 | 1.8622 | 1.4436
10.7208 | 83.7594 | 84.2061 | 78.1456 | 1.9052 | 1.8629 | 1.4438
10.725 | 83.7467 | 84.2067 | 78.1476 | 1.9059 | 1.8637 | 1.4439
10.7292 | 83.7276 | 84.1944 | 78.143 | 1.9065 | 1.8644 | 1.4439
10.7333 | 83.7246 | 84.1846 | 78.1373 | 1.9072 | 1.8652 | 1.444
10.7375 | 83.7226 | 84.1813 | 78.139 | 1.9079 | 1.8659 | 1.4441
10.7417 | 83.719 | 84.1773 | 78.1409 | 1.9086 | 1.8666 | 1.4441
10.7458 | 83.7081 | 84.1743 | 78.1389 | 1.9095 | 1.8674 | 1.4442
10.75 | 83.6918 | 84.1704 | 78.1375 | 1.9102 | 1.8681 | 1.4443
10.7542 | 83.6834 | 84.1624 | 78.1365 | 1.9109 | 1.8689 | 1.4443
10.7583 | 83.6807 | 84.1566 | 78.1346 | 1.9116 | 1.8696 | 1.4444
10.7625 | 83.6805 | 84.1533 | 78.1353 | 1.9124 | 1.8704 | 1.4444
10.7667 | 83.6738 | 84.1498 | 78.1365 | 1.9132 | 1.8711 | 1.4445
10.7708 | 83.6575 | 84.144 | 78.1338 | 1.914 | 1.8719 | 1.4446
10.775 | 83.6401 | 84.137 | 78.1318 | 1.9148 | 1.8726 | 1.4446
10.7792 | 83.6347 | 84.1339 | 78.1342 | 1.9155 | 1.8734 | 1.4446
10.7833 | 83.6304 | 84.1301 | 78.1362 | 1.9163 | 1.8741 | 1.4447
10.7875 | 83.6275 | 84.1244 | 78.136 | 1.9171 | 1.8749 | 1.4447
10.7917 | 83.6169 | 84.1184 | 78.1367 | 1.9181 | 1.8757 | 1.4448
10.7958 | 83.5998 | 84.1135 | 78.1371 | 1.9188 | 1.8764 | 1.4448
10.8 | 83.585 | 84.1078 | 78.138 | 1.9197 | 1.8771 | 1.4447
10.8042 | 83.5812 | 84.1064 | 78.1432 | 1.9205 | 1.8779 | 1.4448
10.8083 | 83.5795 | 84.1053 | 78.1488 | 1.9214 | 1.8786 | 1.4447
10.8125 | 83.568 | 84.0957 | 78.1502 | 1.9223 | 1.8794 | 1.4447
10.8167 | 83.5567 | 84.0878 | 78.153 | 1.9232 | 1.8802 | 1.4447
10.8208 | 83.5379 | 84.0854 | 78.1596 | 1.9241 | 1.8809 | 1.4446
10.825 | 83.5275 | 84.0822 | 78.1668 | 1.925 | 1.8816 | 1.4445
10.8292 | 83.5233 | 84.0805 | 78.1771 | 1.9259 | 1.8823 | 1.4444
10.8333 | 83.5213 | 84.0792 | 78.1882 | 1.9268 | 1.8831 | 1.4443
10.8375 | 83.5066 | 84.0689 | 78.1975 | 1.9278 | 1.8838 | 1.4441
10.8417 | 83.491 | 84.0602 | 78.2098 | 1.9288 | 1.8846 | 1.4439
10.8458 | 83.478 | 84.0605 | 78.2284 | 1.9297 | 1.8853 | 1.4436
10.85 | 83.4671 | 84.0591 | 78.2494 | 1.9306 | 1.886 | 1.4433
10.8542 | 83.4655 | 84.0553 | 78.271 | 1.9317 | 1.8867 | 1.443
10.8583 | 83.4591 | 84.0527 | 78.2942 | 1.9327 | 1.8875 | 1.4426
10.8625 | 83.7332 | 84.3241 | 78.2661 | 1.9314 | 1.8859 | 1.4425
10.8667 | 84.0059 | 84.6006 | 78.2329 | 1.93 | 1.8842 | 1.4424
10.8708 | 84.4838 | 84.991 | 78.1767 | 1.9286 | 1.8819 | 1.4425
10.875 | 84.8777 | 85.3837 | 78.1114 | 1.9264 | 1.8795 | 1.4425
10.8792 | 84.9739 | 85.4171 | 78.0922 | 1.9238 | 1.8757 | 1.4428
10.8833 | 85.0121 | 85.4507 | 78.0707 | 1.9203 | 1.8719 | 1.4431
10.8875 | 84.9762 | 85.3623 | 78.0596 | 1.9158 | 1.8676 | 1.4436
10.8917 | 84.8969 | 85.2708 | 78.0479 | 1.9116 | 1.8632 | 1.4441
10.8958 | 84.7233 | 84.9817 | 78.0708 | 1.9102 | 1.8619 | 1.4442
10.9 | 84.4493 | 84.6848 | 78.0975 | 1.909 | 1.8607 | 1.4444
10.9042 | 84.1649 | 84.4432 | 78.119 | 1.9075 | 1.8593 | 1.4446
10.9083 | 83.9382 | 84.1986 | 78.1443 | 1.9061 | 1.8578 | 1.4449
10.9125 | 83.9102 | 84.2049 | 78.1361 | 1.9056 | 1.8589 | 1.4449
10.9167 | 83.8855 | 84.207 | 78.1267 | 1.9063 | 1.8601 | 1.4448
10.9208 | 83.8075 | 84.0692 | 78.1491 | 1.9073 | 1.8617 | 1.4447
10.925 | 83.6218 | 83.9296 | 78.1747 | 1.9082 | 1.8633 | 1.4446
10.9292 | 83.6381 | 84.0488 | 78.1611 | 1.9081 | 1.8633 | 1.4448
10.9333 | 83.7226 | 84.1742 | 78.1456 | 1.9079 | 1.8632 | 1.4449
10.9375 | 83.79 | 84.2633 | 78.1361 | 1.9088 | 1.8652 | 1.4447
10.9417 | 83.8285 | 84.3501 | 78.125 | 1.9108 | 1.8671 | 1.4445
10.9458 | 83.7873 | 84.2542 | 78.1426 | 1.9109 | 1.8668 | 1.4446
10.95 | 83.6712 | 84.1611 | 78.1629 | 1.9108 | 1.8665 | 1.4447
10.9542 | 83.7654 | 84.3306 | 78.1384 | 1.9104 | 1.8662 | 1.4448
10.9583 | 83.9404 | 84.5033 | 78.1105 | 1.9106 | 1.866 | 1.4449
10.9625 | 83.978 | 84.4152 | 78.1218 | 1.9115 | 1.8672 | 1.4448
10.9667 | 83.9252 | 84.3218 | 78.1348 | 1.9131 | 1.8684 | 1.4446
10.9708 | 83.8969 | 84.2741 | 78.1408 | 1.9128 | 1.8671 | 1.4448
10.975 | 83.801 | 84.2309 | 78.148 | 1.9117 | 1.8659 | 1.4451
10.9792 | 83.8798 | 84.3594 | 78.1277 | 1.9114 | 1.8667 | 1.445
10.9833 | 83.9691 | 84.4861 | 78.1045 | 1.9118 | 1.8676 | 1.445
10.9875 | 83.9928 | 84.3208 | 78.1264 | 1.9125 | 1.8681 | 1.4449
10.9917 | 83.8965 | 84.1525 | 78.1515 | 1.9134 | 1.8686 | 1.4449
10.9958 | 83.8527 | 84.2309 | 78.1402 | 1.9132 | 1.8677 | 1.4451
11 | 83.8563 | 84.315 | 78.1272 | 1.9123 | 1.8668 | 1.4453
11.0042 | 83.8658 | 84.3529 | 78.1208 | 1.9121 | 1.8683 | 1.4451
11.0083 | 83.9001 | 84.3859 | 78.1134 | 1.9127 | 1.8698 | 1.445
11.0125 | 83.877 | 84.2513 | 78.1316 | 1.9132 | 1.8694 | 1.4451
11.0167 | 83.8149 | 84.118 | 78.1526 | 1.9134 | 1.869 | 1.4452
11.0208 | 83.7584 | 84.2637 | 78.1322 | 1.9132 | 1.8689 | 1.4452
11.025 | 83.8297 | 84.4131 | 78.1089 | 1.9132 | 1.8689 | 1.4453
11.0292 | 83.8419 | 84.3378 | 78.1172 | 1.9133 | 1.8702 | 1.4452
11.0333 | 83.8189 | 84.2569 | 78.127 | 1.9141 | 1.8715 | 1.4451
11.0375 | 83.7933 | 84.2202 | 78.1359 | 1.9144 | 1.8705 | 1.4452
11.0417 | 83.777 | 84.1876 | 78.1454 | 1.9141 | 1.8696 | 1.4454
11.0458 | 83.7678 | 84.3159 | 78.1361 | 1.914 | 1.8704 | 1.4453
11.05 | 83.8331 | 84.4436 | 78.1242 | 1.9144 | 1.8712 | 1.4452
11.0542 | 83.8309 | 84.2845 | 78.1097 | 1.9149 | 1.8718 | 1.4454
11.0583 | 83.7663 | 84.1233 | 78.0991 | 1.9156 | 1.8725 | 1.4455
11.0625 | 83.6961 | 84.1632 | 78.0613 | 1.9158 | 1.8719 | 1.4458
11.0667 | 83.7135 | 84.2085 | 78.0232 | 1.9158 | 1.8713 | 1.4461
11.0708 | 83.765 | 84.2995 | 78.0736 | 1.9155 | 1.8724 | 1.4459
11.075 | 83.8339 | 84.3838 | 78.1206 | 1.9161 | 1.8736 | 1.4457
11.0792 | 83.8375 | 84.2729 | 78.1416 | 1.9168 | 1.8735 | 1.446
11.0833 | 83.8105 | 84.1616 | 78.1654 | 1.9171 | 1.8735 | 1.4463
11.0875 | 83.6853 | 84.1737 | 78.0485 | 1.9174 | 1.8738 | 1.4467
11.0917 | 83.6408 | 84.1894 | 77.9333 | 1.9178 | 1.8741 | 1.4471
11.0958 | 83.6043 | 84.0661 | 77.8516 | 1.9187 | 1.8759 | 1.4478
11.1 | 83.5119 | 83.9384 | 77.773 | 1.9197 | 1.8777 | 1.4485
11.1042 | 83.4585 | 83.8545 | 77.7097 | 1.9213 | 1.8785 | 1.4501
11.1083 | 83.4119 | 83.7775 | 77.6515 | 1.9223 | 1.8793 | 1.4515
11.1125 | 83.3916 | 83.8579 | 77.6062 | 1.9235 | 1.8813 | 1.4528
11.1167 | 83.4036 | 83.9382 | 77.5596 | 1.925 | 1.8832 | 1.4541
11.1208 | 83.463 | 83.8837 | 77.5913 | 1.9264 | 1.885 | 1.4553
11.125 | 83.4586 | 83.8238 | 77.6212 | 1.9276 | 1.8866 | 1.4565
11.1292 | 83.4605 | 83.8929 | 77.6316 | 1.9287 | 1.8873 | 1.4576
11.1333 | 83.511 | 83.9661 | 77.6412 | 1.9295 | 1.8878 | 1.4587
11.1375 | 83.5265 | 84.0096 | 77.6369 | 1.9302 | 1.8895 | 1.4594
11.1417 | 83.5366 | 84.0487 | 77.6309 | 1.9312 | 1.8912 | 1.46
11.1458 | 83.5558 | 83.9825 | 77.6426 | 1.9321 | 1.8917 | 1.4606
11.15 | 83.5386 | 83.9156 | 77.655 | 1.9325 | 1.8921 | 1.4613
11.1542 | 83.5221 | 83.9894 | 77.6383 | 1.9331 | 1.8927 | 1.4619
11.1583 | 83.551 | 84.0664 | 77.6227 | 1.9337 | 1.8933 | 1.4625
11.1625 | 83.5513 | 84.0137 | 77.5996 | 1.9343 | 1.8947 | 1.463
11.1667 | 83.5078 | 83.958 | 77.5778 | 1.9352 | 1.8961 | 1.4636
11.1708 | 83.5043 | 83.9319 | 77.5783 | 1.9358 | 1.8962 | 1.4641
11.175 | 83.5033 | 83.9079 | 77.579 | 1.9362 | 1.8963 | 1.4646
11.1792 | 83.4901 | 83.9678 | 77.5625 | 1.9368 | 1.8975 | 1.4653
11.1833 | 83.5126 | 84.0278 | 77.5463 | 1.9377 | 1.8987 | 1.4659
11.1875 | 83.5066 | 83.951 | 77.5324 | 1.9384 | 1.8996 | 1.4663
11.1917 | 83.4651 | 83.8724 | 77.5197 | 1.939 | 1.9005 | 1.4668
11.1958 | 83.47 | 83.9166 | 77.531 | 1.9396 | 1.9007 | 1.4673
11.2 | 83.5027 | 83.962 | 77.5402 | 1.94 | 1.901 | 1.4678
11.2042 | 83.4985 | 83.9728 | 77.5233 | 1.9406 | 1.9023 | 1.4683
11.2083 | 83.4946 | 83.9837 | 77.5072 | 1.9415 | 1.9036 | 1.4688
11.2125 | 83.4896 | 83.9129 | 77.4957 | 1.942 | 1.904 | 1.4691
11.2167 | 83.4618 | 83.8439 | 77.4846 | 1.9423 | 1.9044 | 1.4695
11.2208 | 83.4672 | 83.9067 | 77.4882 | 1.9428 | 1.905 | 1.4699
11.225 | 83.5061 | 83.9686 | 77.4901 | 1.9434 | 1.9056 | 1.4704
11.2292 | 83.4957 | 83.9311 | 77.4693 | 1.944 | 1.9068 | 1.4708
11.2333 | 83.4657 | 83.8913 | 77.4519 | 1.9447 | 1.908 | 1.4713
11.2375 | 83.4604 | 83.8829 | 77.4571 | 1.9451 | 1.9081 | 1.4715
11.2417 | 83.4537 | 83.8724 | 77.4617 | 1.9453 | 1.9082 | 1.4717
11.2458 | 83.4499 | 83.9335 | 77.471 | 1.946 | 1.9091 | 1.4722
11.25 | 83.4629 | 83.9934 | 77.4784 | 1.9467 | 1.91 | 1.4725
11.2542 | 83.4468 | 83.9175 | 77.4508 | 1.9473 | 1.9107 | 1.4729
11.2583 | 83.3961 | 83.8476 | 77.4258 | 1.9479 | 1.9114 | 1.4732
11.2625 | 83.4047 | 83.8656 | 77.4337 | 1.9484 | 1.9116 | 1.4733
11.2667 | 83.437 | 83.8851 | 77.4395 | 1.9487 | 1.9118 | 1.4735
11.2708 | 83.4372 | 83.8928 | 77.4304 | 1.9494 | 1.913 | 1.474
11.275 | 83.4491 | 83.8989 | 77.423 | 1.9502 | 1.9141 | 1.4745
11.2792 | 83.4447 | 83.8469 | 77.409 | 1.9506 | 1.9145 | 1.4746
11.2833 | 83.4169 | 83.7949 | 77.3964 | 1.9508 | 1.9149 | 1.4747
11.2875 | 83.4329 | 83.8501 | 77.4151 | 1.9513 | 1.9154 | 1.475
11.2917 | 83.4598 | 83.9013 | 77.4301 | 1.9517 | 1.916 | 1.4753
11.2958 | 83.4421 | 83.8628 | 77.4041 | 1.9522 | 1.917 | 1.4756
11.3 | 83.4008 | 83.8269 | 77.3818 | 1.953 | 1.918 | 1.476
11.3042 | 83.3876 | 83.8099 | 77.3843 | 1.9533 | 1.9182 | 1.476
11.3083 | 83.3842 | 83.792 | 77.3871 | 1.9535 | 1.9185 | 1.4761
11.3125 | 83.3909 | 83.833 | 77.3929 | 1.9541 | 1.9194 | 1.4765
11.3167 | 83.4223 | 83.8699 | 77.3976 | 1.9548 | 1.9203 | 1.4768
11.3208 | 83.4115 | 83.8186 | 77.3776 | 1.9553 | 1.9209 | 1.477
11.325 | 83.379 | 83.7713 | 77.3602 | 1.9557 | 1.9216 | 1.4771
11.3292 | 83.3855 | 83.7878 | 77.3723 | 1.9561 | 1.922 | 1.4773
11.3333 | 83.4162 | 83.803 | 77.3808 | 1.9562 | 1.9224 | 1.4774
11.3375 | 83.4124 | 83.8066 | 77.3713 | 1.9568 | 1.9233 | 1.4777
11.3417 | 83.4113 | 83.8096 | 77.3622 | 1.9574 | 1.9243 | 1.478
11.3458 | 83.3954 | 83.7725 | 77.3536 | 1.9578 | 1.9247 | 1.4781
11.35 | 83.3561 | 83.7375 | 77.3473 | 1.958 | 1.9252 | 1.4782
11.3542 | 83.3604 | 83.7666 | 77.3524 | 1.9585 | 1.9258 | 1.4784
11.3583 | 83.3806 | 83.7935 | 77.3546 | 1.959 | 1.9264 | 1.4787
11.3625 | 83.3587 | 83.7678 | 77.3419 | 1.9596 | 1.9273 | 1.4789
11.3667 | 83.3152 | 83.7449 | 77.3307 | 1.9604 | 1.9281 | 1.479
11.3708 | 83.2991 | 83.73 | 77.3304 | 1.9609 | 1.9285 | 1.4792
11.375 | 83.272 | 83.7157 | 77.3308 | 1.9614 | 1.929 | 1.4793
11.3792 | 83.2748 | 83.7394 | 77.333 | 1.962 | 1.9297 | 1.4795
11.3833 | 83.3044 | 83.7609 | 77.3337 | 1.9629 | 1.9305 | 1.4797
11.3875 | 83.2843 | 83.7236 | 77.3243 | 1.9635 | 1.9312 | 1.4799
11.3917 | 83.2614 | 83.6894 | 77.3163 | 1.9643 | 1.932 | 1.4801
11.3958 | 83.2607 | 83.6888 | 77.3151 | 1.9648 | 1.9325 | 1.4802
11.4 | 83.2681 | 83.687 | 77.3137 | 1.9654 | 1.933 | 1.4803
11.4042 | 83.2757 | 83.6959 | 77.3148 | 1.966 | 1.9338 | 1.4805
11.4083 | 83.2975 | 83.7051 | 77.316 | 1.9667 | 1.9347 | 1.4807
11.4125 | 83.2966 | 83.6791 | 77.3081 | 1.9672 | 1.9353 | 1.4808
11.4167 | 83.2888 | 83.6574 | 77.3007 | 1.9676 | 1.9359 | 1.481
11.4208 | 83.301 | 83.6741 | 77.3011 | 1.968 | 1.9365 | 1.4811
11.425 | 83.3166 | 83.6877 | 77.3003 | 1.9684 | 1.937 | 1.4812
11.4292 | 83.3092 | 83.6829 | 77.2993 | 1.9688 | 1.9378 | 1.4814
11.4333 | 83.3029 | 83.6766 | 77.2994 | 1.9693 | 1.9385 | 1.4815
11.4375 | 83.2939 | 83.6647 | 77.2925 | 1.9697 | 1.939 | 1.4816
11.4417 | 83.2839 | 83.6522 | 77.2859 | 1.97 | 1.9394 | 1.4817
11.4458 | 83.2855 | 83.6682 | 77.2901 | 1.9704 | 1.94 | 1.4818
11.45 | 83.283 | 83.6801 | 77.2926 | 1.9709 | 1.9406 | 1.4819
11.4542 | 83.2709 | 83.659 | 77.2863 | 1.9713 | 1.9412 | 1.4821
11.4583 | 83.248 | 83.6392 | 77.2812 | 1.9718 | 1.9419 | 1.4823
11.4625 | 83.2395 | 83.6429 | 77.2791 | 1.9723 | 1.9422 | 1.4823
11.4667 | 83.2356 | 83.6436 | 77.2771 | 1.9728 | 1.9427 | 1.4824
11.4708 | 83.2255 | 83.6493 | 77.2816 | 1.9733 | 1.9433 | 1.4825
11.475 | 83.2158 | 83.6544 | 77.285 | 1.974 | 1.944 | 1.4826
11.4792 | 83.2076 | 83.6251 | 77.2741 | 1.9745 | 1.9445 | 1.4828
11.4833 | 83.1981 | 83.6005 | 77.2641 | 1.975 | 1.945 | 1.4829
11.4875 | 83.204 | 83.619 | 77.2685 | 1.9755 | 1.9454 | 1.4829
11.4917 | 83.2129 | 83.632 | 77.2726 | 1.9762 | 1.9458 | 1.4829
11.4958 | 83.2073 | 83.6344 | 77.2725 | 1.9767 | 1.9465 | 1.4831
11.5 | 83.2021 | 83.6394 | 77.2724 | 1.9773 | 1.9471 | 1.4833
11.5042 | 83.1915 | 83.6192 | 77.2643 | 1.9777 | 1.9474 | 1.4833
11.5083 | 83.1904 | 83.6053 | 77.2564 | 1.9782 | 1.9478 | 1.4833
11.5125 | 83.1822 | 83.6158 | 77.2635 | 1.9788 | 1.9483 | 1.4834
11.5167 | 83.1739 | 83.6201 | 77.2701 | 1.9794 | 1.9487 | 1.4835
11.5208 | 83.1603 | 83.6048 | 77.2632 | 1.98 | 1.9493 | 1.4836
11.525 | 83.1459 | 83.5921 | 77.2574 | 1.9806 | 1.9498 | 1.4837
11.5292 | 83.1474 | 83.5861 | 77.2562 | 1.9811 | 1.9501 | 1.4837
11.5333 | 83.1568 | 83.5833 | 77.2543 | 1.9816 | 1.9505 | 1.4837
11.5375 | 83.1573 | 83.5854 | 77.2579 | 1.9822 | 1.9511 | 1.4839
11.5417 | 83.1525 | 83.5848 | 77.2611 | 1.9829 | 1.9517 | 1.484
11.5458 | 83.1442 | 83.5671 | 77.2529 | 1.9834 | 1.9521 | 1.484
11.55 | 83.1385 | 83.5521 | 77.2464 | 1.9838 | 1.9526 | 1.4841
11.5542 | 83.1422 | 83.5561 | 77.252 | 1.9843 | 1.9531 | 1.4841
11.5583 | 83.1501 | 83.5595 | 77.2562 | 1.9849 | 1.9535 | 1.4841
11.5625 | 83.1466 | 83.5454 | 77.2524 | 1.9854 | 1.9542 | 1.4843
11.5667 | 83.14 | 83.5317 | 77.2488 | 1.9859 | 1.9548 | 1.4844
11.5708 | 83.1349 | 83.5207 | 77.2446 | 1.9863 | 1.9552 | 1.4844
11.575 | 83.1338 | 83.5089 | 77.2419 | 1.9868 | 1.9557 | 1.4844
11.5792 | 83.1334 | 83.5163 | 77.2487 | 1.9872 | 1.9563 | 1.4845
11.5833 | 83.1268 | 83.5208 | 77.2537 | 1.9878 | 1.9569 | 1.4845
11.5875 | 83.1183 | 83.4978 | 77.2449 | 1.9882 | 1.9575 | 1.4846
11.5917 | 83.1042 | 83.4791 | 77.2367 | 1.9887 | 1.9581 | 1.4847
11.5958 | 83.1012 | 83.4804 | 77.2391 | 1.9892 | 1.9585 | 1.4847
11.6 | 83.0989 | 83.479 | 77.2425 | 1.9897 | 1.959 | 1.4847
11.6042 | 83.0877 | 83.4803 | 77.2456 | 1.9902 | 1.9597 | 1.4848
11.6083 | 83.0822 | 83.4808 | 77.2472 | 1.9908 | 1.9604 | 1.4849
11.6125 | 83.0658 | 83.4574 | 77.2384 | 1.9914 | 1.9609 | 1.4849
11.6167 | 83.0632 | 83.4386 | 77.2306 | 1.9919 | 1.9615 | 1.4849
11.6208 | 83.0595 | 83.4479 | 77.2372 | 1.9925 | 1.962 | 1.4849
11.625 | 83.0553 | 83.4515 | 77.2442 | 1.9931 | 1.9625 | 1.4849
11.6292 | 83.0462 | 83.4421 | 77.2418 | 1.9937 | 1.9633 | 1.485
11.6333 | 83.0363 | 83.4351 | 77.2387 | 1.9943 | 1.9639 | 1.4851
11.6375 | 83.0312 | 83.4189 | 77.2345 | 1.9948 | 1.9644 | 1.4851
11.6417 | 83.0297 | 83.4061 | 77.2311 | 1.9954 | 1.9649 | 1.4851
11.6458 | 83.0278 | 83.4157 | 77.2374 | 1.996 | 1.9655 | 1.4851
11.65 | 83.0147 | 83.4198 | 77.2439 | 1.9967 | 1.9661 | 1.4852
11.6542 | 83.0056 | 83.4032 | 77.2387 | 1.9973 | 1.9668 | 1.4852
11.6583 | 82.9918 | 83.3903 | 77.2335 | 1.9979 | 1.9674 | 1.4853
11.6625 | 82.9932 | 83.3846 | 77.2354 | 1.9985 | 1.9679 | 1.4852
11.6667 | 82.9889 | 83.3776 | 77.2379 | 1.9992 | 1.9684 | 1.4852
11.6708 | 82.9838 | 83.3816 | 77.2417 | 1.9998 | 1.9691 | 1.4853
11.675 | 82.9676 | 83.3812 | 77.2455 | 2.0006 | 1.9697 | 1.4853
11.6792 | 82.9568 | 83.3646 | 77.2429 | 2.0011 | 1.9703 | 1.4853
11.6833 | 82.9494 | 83.3525 | 77.2405 | 2.0018 | 1.9709 | 1.4852
11.6875 | 82.9481 | 83.3528 | 77.2472 | 2.0025 | 1.9714 | 1.4852
11.6917 | 82.9443 | 83.3511 | 77.2551 | 2.0032 | 1.9719 | 1.4852
11.6958 | 82.9229 | 83.3404 | 77.2584 | 2.004 | 1.9726 | 1.4851
11.7 | 82.9064 | 83.33 | 77.2623 | 2.0048 | 1.9733 | 1.4851
11.7042 | 82.8852 | 83.3118 | 77.268 | 2.0055 | 1.9739 | 1.485
11.7083 | 82.8815 | 83.2967 | 77.274 | 2.0062 | 1.9745 | 1.4848
11.7125 | 82.963 | 83.3847 | 77.2688 | 2.0064 | 1.9744 | 1.4849
11.7167 | 83.0488 | 83.4709 | 77.2629 | 2.0065 | 1.9744 | 1.4849
11.7208 | 83.032 | 83.4659 | 77.2643 | 2.0074 | 1.975 | 1.4847
11.725 | 83.0292 | 83.4664 | 77.2672 | 2.0082 | 1.9757 | 1.4845
11.7292 | 82.8747 | 83.3541 | 77.2981 | 2.0089 | 1.9758 | 1.4844
11.7333 | 82.7635 | 83.2434 | 77.3329 | 2.0092 | 1.976 | 1.4842
11.7375 | 82.7958 | 83.3494 | 77.3335 | 2.0099 | 1.9758 | 1.4841
11.7417 | 82.8917 | 83.4516 | 77.3334 | 2.0098 | 1.9756 | 1.4839
11.7458 | 83.0958 | 83.6695 | 77.3119 | 2.0099 | 1.9748 | 1.4838
11.75 | 83.3149 | 83.8978 | 77.2869 | 2.0093 | 1.9739 | 1.4836
11.7542 | 83.6766 | 84.1501 | 77.2573 | 2.0078 | 1.9708 | 1.4838
11.7583 | 83.9479 | 84.4163 | 77.2223 | 2.0052 | 1.9679 | 1.484
11.7625 | 84.1124 | 84.4741 | 77.2001 | 2.0037 | 1.9651 | 1.4841
11.7667 | 84.1821 | 84.5472 | 77.1755 | 2.0013 | 1.9624 | 1.4843
11.7708 | 84.122 | 84.3661 | 77.1834 | 1.9979 | 1.9593 | 1.4846
11.775 | 83.9666 | 84.1986 | 77.193 | 1.9947 | 1.9562 | 1.4849
11.7792 | 83.9117 | 84.047 | 77.1991 | 1.9927 | 1.9547 | 1.4851
11.7833 | 83.8213 | 83.8867 | 77.2062 | 1.9909 | 1.9532 | 1.4853
11.7875 | 83.5709 | 83.6748 | 77.22 | 1.9904 | 1.9537 | 1.4853
11.7917 | 83.3834 | 83.4477 | 77.2367 | 1.9903 | 1.9539 | 1.4853
11.7958 | 83.2947 | 83.3648 | 77.2463 | 1.9895 | 1.9545 | 1.4853
11.8 | 83.1597 | 83.2646 | 77.257 | 1.9891 | 1.9549 | 1.4854
11.8042 | 83.1044 | 83.2996 | 77.2552 | 1.99 | 1.9568 | 1.4853
11.8083 | 83.0948 | 83.3135 | 77.2532 | 1.991 | 1.9584 | 1.4852
11.8125 | 82.9912 | 83.3355 | 77.2536 | 1.9908 | 1.9593 | 1.4852
11.8167 | 82.9645 | 83.3513 | 77.2542 | 1.9916 | 1.9602 | 1.4852
11.8208 | 83.0497 | 83.4466 | 77.2489 | 1.9922 | 1.9607 | 1.4852
11.825 | 83.0613 | 83.5415 | 77.2422 | 1.993 | 1.9614 | 1.4851
11.8292 | 83.01 | 83.5602 | 77.2418 | 1.9941 | 1.9618 | 1.4851
11.8333 | 83.0415 | 83.5835 | 77.2418 | 1.9947 | 1.9623 | 1.4851
11.8375 | 83.0713 | 83.6076 | 77.2379 | 1.9943 | 1.9618 | 1.4852
11.8417 | 83.1654 | 83.6418 | 77.2336 | 1.9942 | 1.9614 | 1.4853
11.8458 | 83.2281 | 83.636 | 77.2346 | 1.9951 | 1.9617 | 1.4852
11.85 | 83.2595 | 83.6359 | 77.2355 | 1.9957 | 1.962 | 1.4852
11.8542 | 83.1768 | 83.5941 | 77.2379 | 1.996 | 1.9617 | 1.4853
11.8583 | 83.1426 | 83.5558 | 77.2413 | 1.9959 | 1.9614 | 1.4853
11.8625 | 83.2081 | 83.5867 | 77.2354 | 1.9952 | 1.9614 | 1.4853
11.8667 | 83.2871 | 83.6175 | 77.2283 | 1.9949 | 1.9615 | 1.4853
11.8708 | 83.3414 | 83.5551 | 77.236 | 1.9957 | 1.962 | 1.4853
11.875 | 83.3207 | 83.493 | 77.2448 | 1.9964 | 1.9625 | 1.4853
11.8792 | 83.281 | 83.5175 | 77.2398 | 1.9964 | 1.9622 | 1.4854
11.8833 | 83.2203 | 83.538 | 77.2345 | 1.996 | 1.9618 | 1.4855
11.8875 | 83.2651 | 83.56 | 77.2339 | 1.9953 | 1.9626 | 1.4854
11.8917 | 83.2736 | 83.58 | 77.2324 | 1.9952 | 1.9633 | 1.4853
11.8958 | 83.3149 | 83.5132 | 77.2423 | 1.9959 | 1.9633 | 1.4853
11.9 | 83.271 | 83.4494 | 77.2539 | 1.9963 | 1.9633 | 1.4854
11.9042 | 83.2165 | 83.5221 | 77.2286 | 1.9964 | 1.9633 | 1.4855
11.9083 | 83.1695 | 83.5894 | 77.2023 | 1.9961 | 1.9632 | 1.4856
11.9125 | 83.1934 | 83.5435 | 77.2138 | 1.9956 | 1.9641 | 1.4855
11.9167 | 83.177 | 83.5013 | 77.2258 | 1.9957 | 1.9649 | 1.4853
11.9208 | 83.208 | 83.5103 | 77.2603 | 1.9961 | 1.9642 | 1.4854
11.925 | 83.1767 | 83.5194 | 77.2941 | 1.9962 | 1.9635 | 1.4854
11.9292 | 83.1553 | 83.5717 | 77.2548 | 1.9963 | 1.9643 | 1.4855
11.9333 | 83.1068 | 83.6206 | 77.2153 | 1.9964 | 1.965 | 1.4856
11.9375 | 83.1066 | 83.4673 | 77.1772 | 1.9966 | 1.9654 | 1.4857
11.9417 | 83.0659 | 83.3242 | 77.1424 | 1.9971 | 1.9659 | 1.4858
11.9458 | 83.0424 | 83.4173 | 77.1549 | 1.9974 | 1.9654 | 1.486
11.95 | 83.0559 | 83.5002 | 77.1651 | 1.9977 | 1.965 | 1.4863
11.9542 | 83.0903 | 83.5436 | 77.1944 | 1.9976 | 1.9662 | 1.4863
11.9583 | 83.1466 | 83.5862 | 77.2231 | 1.9979 | 1.9674 | 1.4863
11.9625 | 83.1219 | 83.4546 | 77.2118 | 1.9986 | 1.9672 | 1.4865
11.9667 | 83.0942 | 83.3334 | 77.2024 | 1.9989 | 1.9671 | 1.4868
11.9708 | 83.0046 | 83.3943 | 77.1376 | 1.9993 | 1.9675 | 1.4871
11.975 | 82.9597 | 83.4426 | 77.0718 | 1.9995 | 1.9679 | 1.4874
11.9792 | 82.9485 | 83.3101 | 77.0251 | 2.0003 | 1.9697 | 1.488
11.9833 | 82.9051 | 83.188 | 76.9829 | 2.0012 | 1.9715 | 1.4885
11.9875 | 82.8444 | 83.1186 | 76.9297 | 2.0027 | 1.9718 | 1.4896
11.9917 | 82.7857 | 83.0486 | 76.879 | 2.0037 | 1.9722 | 1.4906
11.9958 | 82.7862 | 83.1577 | 76.8607 | 2.0044 | 1.9741 | 1.4914
12 | 82.8012 | 83.248 | 76.8397 | 2.0054 | 1.9757 | 1.4921
12.0042 | 82.8674 | 83.1554 | 76.8719 | 2.0066 | 1.9772 | 1.4929
12.0083 | 82.8845 | 83.0742 | 76.9052 | 2.0078 | 1.9786 | 1.4937
12.0125 | 82.8559 | 83.1579 | 76.8937 | 2.0086 | 1.9787 | 1.4944
12.0167 | 82.867 | 83.2299 | 76.8805 | 2.0092 | 1.9788 | 1.4952
12.0208 | 82.9151 | 83.2818 | 76.8996 | 2.0094 | 1.9804 | 1.4954
12.025 | 82.9509 | 83.3297 | 76.9163 | 2.01 | 1.9819 | 1.4955
12.0292 | 82.9647 | 83.2294 | 76.9264 | 2.0109 | 1.982 | 1.4961
12.0333 | 82.9552 | 83.1471 | 76.9395 | 2.0115 | 1.9822 | 1.4966
12.0375 | 82.9063 | 83.2462 | 76.9051 | 2.0116 | 1.9825 | 1.4969
12.0417 | 82.9028 | 83.3315 | 76.87 | 2.0119 | 1.9827 | 1.4971
12.0458 | 82.947 | 83.2679 | 76.8833 | 2.0122 | 1.9841 | 1.4973
12.05 | 82.9395 | 83.2102 | 76.8965 | 2.0128 | 1.9853 | 1.4975
12.0542 | 82.9062 | 83.1633 | 76.8798 | 2.0136 | 1.985 | 1.4981
12.0583 | 82.8864 | 83.1199 | 76.8659 | 2.014 | 1.9848 | 1.4986
12.0625 | 82.8654 | 83.1984 | 76.8436 | 2.0141 | 1.9858 | 1.4988
12.0667 | 82.876 | 83.2609 | 76.8196 | 2.0147 | 1.9867 | 1.499
12.0708 | 82.9117 | 83.1567 | 76.8396 | 2.0153 | 1.9875 | 1.4993
12.075 | 82.9005 | 83.0641 | 76.8601 | 2.0159 | 1.9882 | 1.4996
12.0792 | 82.8615 | 83.1085 | 76.8427 | 2.0164 | 1.988 | 1.5
12.0833 | 82.8673 | 83.1456 | 76.8262 | 2.0167 | 1.9879 | 1.5004
12.0875 | 82.8804 | 83.1582 | 76.8222 | 2.0169 | 1.9892 | 1.5005
12.0917 | 82.8837 | 83.168 | 76.8164 | 2.0175 | 1.9904 | 1.5006
12.0958 | 82.8945 | 83.0728 | 76.8255 | 2.0182 | 1.9905 | 1.501
12.1 | 82.8796 | 82.9923 | 76.8352 | 2.0186 | 1.9906 | 1.5013
12.1042 | 82.8487 | 83.068 | 76.8083 | 2.0188 | 1.991 | 1.5016
12.1083 | 82.8673 | 83.1299 | 76.782 | 2.0192 | 1.9913 | 1.5019
12.1125 | 82.8911 | 83.0762 | 76.7909 | 2.0195 | 1.9924 | 1.502
12.1167 | 82.8825 | 83.0269 | 76.8 | 2.02 | 1.9934 | 1.5021
12.1208 | 82.8629 | 83.0101 | 76.8035 | 2.0206 | 1.9932 | 1.5025
12.125 | 82.856 | 82.9936 | 76.8079 | 2.0209 | 1.993 | 1.5028
12.1292 | 82.8364 | 83.0602 | 76.7955 | 2.0211 | 1.9938 | 1.5029
12.1333 | 82.837 | 83.1166 | 76.7816 | 2.0216 | 1.9946 | 1.503
12.1375 | 82.8549 | 83.0144 | 76.7869 | 2.0222 | 1.9951 | 1.5032
12.1417 | 82.8277 | 82.9307 | 76.7925 | 2.0226 | 1.9957 | 1.5034
12.1458 | 82.8052 | 82.9615 | 76.7814 | 2.0231 | 1.9956 | 1.5036
12.15 | 82.8256 | 82.9857 | 76.7711 | 2.0234 | 1.9955 | 1.5038
12.1542 | 82.8349 | 82.9923 | 76.7684 | 2.0237 | 1.9967 | 1.5039
12.1583 | 82.8433 | 82.9956 | 76.7656 | 2.0242 | 1.9977 | 1.5041
12.1625 | 82.8603 | 82.9194 | 76.7671 | 2.0247 | 1.9978 | 1.5043
12.1667 | 82.8405 | 82.8534 | 76.7691 | 2.0249 | 1.9979 | 1.5045
12.1708 | 82.8282 | 82.9249 | 76.7655 | 2.0252 | 1.9983 | 1.5046
12.175 | 82.8422 | 82.9815 | 76.7609 | 2.0255 | 1.9986 | 1.5047
12.1792 | 82.8431 | 82.9221 | 76.7539 | 2.0258 | 1.9996 | 1.5049
12.1833 | 82.8173 | 82.8716 | 76.7481 | 2.0264 | 2.0005 | 1.5051
12.1875 | 82.8063 | 82.852 | 76.7501 | 2.0268 | 2.0003 | 1.5052
12.1917 | 82.8023 | 82.8313 | 76.7529 | 2.027 | 2.0002 | 1.5053
12.1958 | 82.7985 | 82.8875 | 76.7514 | 2.0273 | 2.0011 | 1.5055
12.2 | 82.8165 | 82.9321 | 76.7495 | 2.0278 | 2.0018 | 1.5056
12.2042 | 82.8216 | 82.8425 | 76.7399 | 2.0282 | 2.0024 | 1.5057
12.2083 | 82.7986 | 82.7695 | 76.7309 | 2.0285 | 2.0029 | 1.5058
12.2125 | 82.7903 | 82.8056 | 76.7403 | 2.0289 | 2.0029 | 1.5059
12.2167 | 82.8121 | 82.8311 | 76.7478 | 2.029 | 2.0029 | 1.506
12.2208 | 82.8121 | 82.8314 | 76.7378 | 2.0293 | 2.004 | 1.5062
12.225 | 82.8042 | 82.8313 | 76.7289 | 2.0299 | 2.0049 | 1.5064
12.2292 | 82.8021 | 82.7652 | 76.7257 | 2.0303 | 2.005 | 1.5064
12.2333 | 82.7799 | 82.7105 | 76.723 | 2.0304 | 2.0051 | 1.5064
12.2375 | 82.7679 | 82.7667 | 76.7284 | 2.0307 | 2.0055 | 1.5066
12.2417 | 82.781 | 82.8085 | 76.7319 | 2.0312 | 2.006 | 1.5068
12.2458 | 82.7712 | 82.754 | 76.7162 | 2.0316 | 2.0068 | 1.5069
12.25 | 82.7194 | 82.7108 | 76.7033 | 2.0324 | 2.0076 | 1.507
12.2542 | 82.7141 | 82.6985 | 76.7127 | 2.0327 | 2.0075 | 1.507
12.2583 | 82.7151 | 82.6865 | 76.7214 | 2.0331 | 2.0076 | 1.5071
12.2625 | 82.7076 | 82.7225 | 76.7181 | 2.0335 | 2.0084 | 1.5073
12.2667 | 82.7303 | 82.7491 | 76.7135 | 2.0344 | 2.0091 | 1.5075
12.2708 | 82.7197 | 82.6737 | 76.7029 | 2.0348 | 2.0096 | 1.5075
12.275 | 82.6799 | 82.6125 | 76.6947 | 2.0354 | 2.0101 | 1.5075
12.2792 | 82.6802 | 82.6409 | 76.7059 | 2.0358 | 2.0103 | 1.5076
12.2833 | 82.72 | 82.6593 | 76.7156 | 2.0361 | 2.0104 | 1.5078
12.2875 | 82.723 | 82.6557 | 76.7055 | 2.0366 | 2.0114 | 1.5079
12.2917 | 82.733 | 82.6545 | 76.6957 | 2.0373 | 2.0122 | 1.508
12.2958 | 82.7383 | 82.6028 | 76.6942 | 2.0376 | 2.0124 | 1.508
12.3 | 82.7126 | 82.5616 | 76.6934 | 2.0377 | 2.0126 | 1.5081
12.3042 | 82.7186 | 82.6076 | 76.6982 | 2.0381 | 2.013 | 1.5082
12.3083 | 82.7601 | 82.6391 | 76.7016 | 2.0383 | 2.0134 | 1.5083
12.3125 | 82.7508 | 82.6059 | 76.6926 | 2.0386 | 2.0141 | 1.5084
12.3167 | 82.7242 | 82.5802 | 76.6853 | 2.0391 | 2.0147 | 1.5085
12.3208 | 82.7218 | 82.5648 | 76.6888 | 2.0394 | 2.0148 | 1.5085
12.325 | 82.7068 | 82.549 | 76.6914 | 2.0394 | 2.0149 | 1.5086
12.3292 | 82.7072 | 82.5767 | 76.6897 | 2.0398 | 2.0155 | 1.5087
12.3333 | 82.7266 | 82.5937 | 76.6874 | 2.0403 | 2.016 | 1.5088
12.3375 | 82.7124 | 82.5504 | 76.6828 | 2.0406 | 2.0164 | 1.5088
12.3417 | 82.6698 | 82.5158 | 76.6803 | 2.041 | 2.0168 | 1.5089
12.3458 | 82.6622 | 82.532 | 76.6843 | 2.0414 | 2.0169 | 1.5089
12.35 | 82.6719 | 82.541 | 76.6868 | 2.0416 | 2.0171 | 1.509
12.3542 | 82.6642 | 82.5336 | 76.6826 | 2.0421 | 2.0178 | 1.5091
12.3583 | 82.6611 | 82.527 | 76.6785 | 2.0428 | 2.0184 | 1.5091
12.3625 | 82.6571 | 82.4905 | 76.676 | 2.0432 | 2.0186 | 1.5092
12.3667 | 82.6275 | 82.4591 | 76.6748 | 2.0436 | 2.0188 | 1.5092
12.3708 | 82.6346 | 82.4955 | 76.6782 | 2.044 | 2.0191 | 1.5093
12.375 | 82.6659 | 82.521 | 76.6803 | 2.0444 | 2.0194 | 1.5093
12.3792 | 82.6618 | 82.495 | 76.6764 | 2.0448 | 2.02 | 1.5094
12.3833 | 82.646 | 82.48 | 76.6729 | 2.0454 | 2.0205 | 1.5095
12.3875 | 82.6385 | 82.4625 | 76.6715 | 2.0458 | 2.0205 | 1.5095
12.3917 | 82.6283 | 82.4453 | 76.6704 | 2.046 | 2.0207 | 1.5095
12.3958 | 82.621 | 82.4695 | 76.674 | 2.0464 | 2.0211 | 1.5096
12.4 | 82.6328 | 82.4844 | 76.6768 | 2.047 | 2.0215 | 1.5096
12.4042 | 82.6262 | 82.4438 | 76.6718 | 2.0474 | 2.0219 | 1.5097
12.4083 | 82.5988 | 82.4164 | 76.6672 | 2.0479 | 2.0223 | 1.5098
12.4125 | 82.6 | 82.4189 | 76.6671 | 2.0483 | 2.0224 | 1.5098
12.4167 | 82.616 | 82.4153 | 76.6666 | 2.0486 | 2.0226 | 1.5098
12.4208 | 82.6114 | 82.4213 | 76.6692 | 2.049 | 2.0231 | 1.5098
12.425 | 82.6094 | 82.4239 | 76.6722 | 2.0497 | 2.0236 | 1.5099
12.4292 | 82.6067 | 82.3881 | 76.6669 | 2.05 | 2.0239 | 1.5099
12.4333 | 82.5903 | 82.3632 | 76.6617 | 2.0503 | 2.0242 | 1.51
12.4375 | 82.5948 | 82.3751 | 76.6644 | 2.0507 | 2.0245 | 1.51
12.4417 | 82.6162 | 82.3787 | 76.6662 | 2.0511 | 2.0248 | 1.51
12.4458 | 82.6106 | 82.3629 | 76.6656 | 2.0514 | 2.0253 | 1.5101
12.45 | 82.5952 | 82.3495 | 76.6661 | 2.0519 | 2.0258 | 1.5101
12.4542 | 82.5918 | 82.3299 | 76.6625 | 2.0522 | 2.026 | 1.5101
12.4583 | 82.5911 | 82.3132 | 76.6585 | 2.0524 | 2.0263 | 1.5102
12.4625 | 82.5906 | 82.3228 | 76.6624 | 2.0528 | 2.0268 | 1.5102
12.4667 | 82.5933 | 82.3252 | 76.6654 | 2.0533 | 2.0272 | 1.5102
12.4708 | 82.5879 | 82.2982 | 76.6611 | 2.0537 | 2.0277 | 1.5103
12.475 | 82.5579 | 82.2775 | 76.6583 | 2.054 | 2.0281 | 1.5103
12.4792 | 82.558 | 82.277 | 76.6594 | 2.0544 | 2.0284 | 1.5103
12.4833 | 82.5644 | 82.2737 | 76.6594 | 2.0547 | 2.0287 | 1.5103
12.4875 | 82.557 | 82.2704 | 76.6612 | 2.0552 | 2.0292 | 1.5104
12.4917 | 82.5505 | 82.2659 | 76.6627 | 2.0558 | 2.0297 | 1.5104
12.4958 | 82.5402 | 82.2402 | 76.6572 | 2.0562 | 2.0301 | 1.5104
12.5 | 82.5222 | 82.2196 | 76.6532 | 2.0565 | 2.0304 | 1.5104
12.5042 | 82.5221 | 82.2298 | 76.6585 | 2.057 | 2.0308 | 1.5104
12.5083 | 82.5333 | 82.2332 | 76.6626 | 2.0575 | 2.0312 | 1.5104
12.5125 | 82.5253 | 82.214 | 76.66 | 2.058 | 2.0317 | 1.5105
12.5167 | 82.5132 | 82.1999 | 76.6578 | 2.0585 | 2.0322 | 1.5106
12.5208 | 82.5063 | 82.1859 | 76.6552 | 2.0589 | 2.0325 | 1.5105
12.525 | 82.4995 | 82.173 | 76.6535 | 2.0593 | 2.0328 | 1.5105
12.5292 | 82.4996 | 82.1822 | 76.6598 | 2.0598 | 2.0333 | 1.5105
12.5333 | 82.4988 | 82.1855 | 76.6651 | 2.0603 | 2.0337 | 1.5106
12.5375 | 82.492 | 82.1569 | 76.6593 | 2.0608 | 2.0342 | 1.5106
12.5417 | 82.4724 | 82.1361 | 76.6545 | 2.0613 | 2.0346 | 1.5106
12.5458 | 82.4698 | 82.134 | 76.6581 | 2.0618 | 2.0349 | 1.5106
12.55 | 82.4637 | 82.1259 | 76.6618 | 2.0623 | 2.0352 | 1.5105
12.5542 | 82.4619 | 82.125 | 76.6664 | 2.0628 | 2.0358 | 1.5106
12.5583 | 82.4525 | 82.1219 | 76.6701 | 2.0634 | 2.0363 | 1.5106
12.5625 | 82.479 | 82.126 | 76.6598 | 2.0637 | 2.0364 | 1.5106
12.5667 | 82.4973 | 82.1375 | 76.6504 | 2.064 | 2.0366 | 1.5106
12.5708 | 82.4588 | 82.1092 | 76.6645 | 2.0648 | 2.0372 | 1.5105
12.575 | 82.4155 | 82.0736 | 76.6797 | 2.0658 | 2.0379 | 1.5104
12.5792 | 82.3596 | 82.0248 | 76.6886 | 2.0662 | 2.0383 | 1.5104
12.5833 | 82.3125 | 81.9783 | 76.698 | 2.0667 | 2.0387 | 1.5104
12.5875 | 82.3988 | 82.0598 | 76.6846 | 2.067 | 2.0387 | 1.5103
12.5917 | 82.499 | 82.1405 | 76.6701 | 2.0674 | 2.0388 | 1.5102
12.5958 | 82.5696 | 82.2089 | 76.6704 | 2.0676 | 2.0389 | 1.5102
12.6 | 82.6278 | 82.2747 | 76.6698 | 2.0679 | 2.0389 | 1.5102
12.6042 | 82.6102 | 82.22 | 76.6729 | 2.0684 | 2.0388 | 1.5102
12.6083 | 82.6065 | 82.1793 | 76.6776 | 2.0686 | 2.0387 | 1.5102
12.6125 | 82.4305 | 82.1146 | 76.697 | 2.0694 | 2.0388 | 1.51
12.6167 | 82.3564 | 82.0393 | 76.7192 | 2.07 | 2.0391 | 1.5098
12.6208 | 82.3177 | 82.1418 | 76.7214 | 2.0699 | 2.0385 | 1.5098
12.625 | 82.3756 | 82.2266 | 76.7227 | 2.0693 | 2.0379 | 1.5097
12.6292 | 82.567 | 82.4193 | 76.6998 | 2.0698 | 2.037 | 1.5096
12.6333 | 82.7981 | 82.6133 | 76.674 | 2.0692 | 2.0362 | 1.5095
12.6375 | 83.0041 | 82.7588 | 76.6635 | 2.0685 | 2.0339 | 1.5096
12.6417 | 83.1574 | 82.9106 | 76.6505 | 2.0669 | 2.0319 | 1.5097
12.6458 | 83.3495 | 82.9605 | 76.6343 | 2.0653 | 2.0296 | 1.5099
12.65 | 83.4136 | 83.0431 | 76.616 | 2.0631 | 2.0274 | 1.5101
12.6542 | 83.4006 | 82.9164 | 76.6191 | 2.0612 | 2.0258 | 1.5102
12.6583 | 83.3346 | 82.8197 | 76.6233 | 2.0592 | 2.0242 | 1.5103
12.6625 | 83.2639 | 82.6882 | 76.6332 | 2.057 | 2.0234 | 1.5105
12.6667 | 83.175 | 82.5584 | 76.6442 | 2.0554 | 2.0222 | 1.5107
12.6708 | 83.0784 | 82.4126 | 76.6488 | 2.0546 | 2.0232 | 1.5107
12.675 | 82.9218 | 82.2644 | 76.655 | 2.0546 | 2.0238 | 1.5106
12.6792 | 82.8105 | 82.1837 | 76.6668 | 2.0541 | 2.0246 | 1.5106
12.6833 | 82.6824 | 82.0751 | 76.6803 | 2.0538 | 2.0252 | 1.5106
12.6875 | 82.6231 | 82.136 | 76.6754 | 2.0539 | 2.0265 | 1.5106
12.6917 | 82.6015 | 82.164 | 76.6694 | 2.0542 | 2.0276 | 1.5106
12.6958 | 82.5294 | 82.1619 | 76.6705 | 2.0548 | 2.0287 | 1.5105
12.7 | 82.4168 | 82.1508 | 76.6723 | 2.0557 | 2.0298 | 1.5104
12.7042 | 82.4398 | 82.2377 | 76.6709 | 2.0561 | 2.0296 | 1.5104
12.7083 | 82.4534 | 82.3109 | 76.6686 | 2.0564 | 2.0295 | 1.5105
12.7125 | 82.4733 | 82.3623 | 76.6607 | 2.0572 | 2.03 | 1.5105
12.7167 | 82.5485 | 82.4208 | 76.6518 | 2.0583 | 2.0306 | 1.5104
12.7208 | 82.5568 | 82.3705 | 76.658 | 2.0584 | 2.0301 | 1.5104
12.725 | 82.5247 | 82.3391 | 76.6654 | 2.0587 | 2.0298 | 1.5104
12.7292 | 82.5702 | 82.3944 | 76.6602 | 2.0589 | 2.0295 | 1.5105
12.7333 | 82.6266 | 82.4503 | 76.6537 | 2.0589 | 2.0292 | 1.5106
12.7375 | 82.5855 | 82.393 | 76.6555 | 2.0594 | 2.0296 | 1.5105
12.7417 | 82.5924 | 82.3494 | 76.658 | 2.0598 | 2.03 | 1.5105
12.7458 | 82.6127 | 82.3209 | 76.662 | 2.0595 | 2.0295 | 1.5105
12.75 | 82.6329 | 82.295 | 76.6665 | 2.059 | 2.029 | 1.5106
12.7542 | 82.6541 | 82.3317 | 76.6552 | 2.0593 | 2.0295 | 1.5106
12.7583 | 82.7187 | 82.359 | 76.6431 | 2.0595 | 2.03 | 1.5106
12.7625 | 82.6716 | 82.3022 | 76.6564 | 2.0598 | 2.0301 | 1.5105
12.7667 | 82.6695 | 82.2499 | 76.6704 | 2.0601 | 2.0303 | 1.5105
12.7708 | 82.6712 | 82.2955 | 76.6775 | 2.0595 | 2.0301 | 1.5105
12.775 | 82.7407 | 82.3336 | 76.6836 | 2.0591 | 2.0299 | 1.5106
12.7792 | 82.773 | 82.3114 | 76.6556 | 2.0594 | 2.0307 | 1.5106
12.7833 | 82.7898 | 82.2874 | 76.629 | 2.0598 | 2.0314 | 1.5107
12.7875 | 82.7286 | 82.2514 | 76.6262 | 2.0602 | 2.0311 | 1.5107
12.7917 | 82.7204 | 82.2188 | 76.6238 | 2.06 | 2.0308 | 1.5107
12.7958 | 82.6955 | 82.2987 | 76.6578 | 2.0593 | 2.031 | 1.5107
12.8 | 82.7455 | 82.3715 | 76.6896 | 2.059 | 2.0312 | 1.5106
12.8042 | 82.7882 | 82.3316 | 76.694 | 2.0592 | 2.0315 | 1.5106
12.8083 | 82.7934 | 82.2979 | 76.6999 | 2.0598 | 2.0318 | 1.5106
12.8125 | 82.7044 | 82.2566 | 76.653 | 2.0601 | 2.0316 | 1.5107
12.8167 | 82.6209 | 82.2209 | 76.6069 | 2.0602 | 2.0315 | 1.5108
12.8208 | 82.5933 | 82.22 | 76.5918 | 2.0596 | 2.0321 | 1.5109
12.825 | 82.5618 | 82.2149 | 76.5768 | 2.0595 | 2.0326 | 1.511
12.8292 | 82.5708 | 82.2132 | 76.5985 | 2.0598 | 2.0327 | 1.5112
12.8334 | 82.5994 | 82.2099 | 76.621 | 2.0602 | 2.0328 | 1.5114
12.8375 | 82.5568 | 82.2247 | 76.6179 | 2.0604 | 2.0331 | 1.5116
12.8417 | 82.5309 | 82.2427 | 76.6139 | 2.0605 | 2.0335 | 1.5117
12.8458 | 82.5345 | 82.2012 | 76.6129 | 2.0608 | 2.0338 | 1.5117
12.85 | 82.5387 | 82.1618 | 76.6116 | 2.0609 | 2.0342 | 1.5117
12.8542 | 82.4913 | 82.1313 | 76.5816 | 2.0617 | 2.0346 | 1.5121
12.8583 | 82.4592 | 82.104 | 76.5531 | 2.0624 | 2.0349 | 1.5125
12.8625 | 82.4059 | 82.0335 | 76.5005 | 2.0629 | 2.036 | 1.5129
12.8667 | 82.3454 | 81.9729 | 76.4503 | 2.0635 | 2.037 | 1.5133
12.8708 | 82.3524 | 81.9353 | 76.4371 | 2.0645 | 2.0377 | 1.5138
12.875 | 82.344 | 81.8878 | 76.4243 | 2.0653 | 2.0383 | 1.5144
12.8792 | 82.3342 | 81.9193 | 76.4133 | 2.0663 | 2.0394 | 1.515
12.8833 | 82.3303 | 81.9429 | 76.4025 | 2.0672 | 2.0404 | 1.5157
12.8875 | 82.3615 | 81.908 | 76.4082 | 2.0678 | 2.0413 | 1.5161
12.8917 | 82.372 | 81.8756 | 76.4139 | 2.0685 | 2.0423 | 1.5164
12.8959 | 82.3971 | 81.9265 | 76.4307 | 2.0692 | 2.0424 | 1.5168
12.9 | 82.4273 | 81.9592 | 76.4453 | 2.0698 | 2.0426 | 1.5173
12.9042 | 82.4344 | 81.9765 | 76.4482 | 2.07 | 2.0435 | 1.5174
12.9083 | 82.4519 | 82.0036 | 76.4516 | 2.0704 | 2.0443 | 1.5176
12.9125 | 82.4639 | 81.9474 | 76.4535 | 2.0707 | 2.0443 | 1.5178
12.9167 | 82.4636 | 81.9047 | 76.4563 | 2.071 | 2.0446 | 1.518
12.9208 | 82.4426 | 81.9653 | 76.4481 | 2.0713 | 2.0446 | 1.5182
12.925 | 82.44 | 82.0141 | 76.4388 | 2.0715 | 2.0447 | 1.5183
12.9292 | 82.4463 | 81.9635 | 76.436 | 2.0717 | 2.0455 | 1.5185
12.9333 | 82.4377 | 81.931 | 76.4348 | 2.072 | 2.0463 | 1.5186
12.9375 | 82.4189 | 81.9013 | 76.4218 | 2.0726 | 2.046 | 1.5189
12.9417 | 82.4 | 81.8666 | 76.4093 | 2.0729 | 2.0459 | 1.5191
12.9459 | 82.3865 | 81.9245 | 76.4026 | 2.0731 | 2.0465 | 1.5193
12.95 | 82.3936 | 81.969 | 76.3946 | 2.0734 | 2.047 | 1.5194
12.9542 | 82.4152 | 81.8907 | 76.4011 | 2.0739 | 2.0475 | 1.5196
12.9584 | 82.413 | 81.8288 | 76.4096 | 2.0744 | 2.0481 | 1.5199
12.9625 | 82.3846 | 81.8691 | 76.3997 | 2.0748 | 2.0478 | 1.5201
12.9667 | 82.3789 | 81.8911 | 76.389 | 2.0751 | 2.0476 | 1.5203
12.9708 | 82.3921 | 81.9043 | 76.3929 | 2.0752 | 2.0486 | 1.5203
12.975 | 82.4003 | 81.9224 | 76.3955 | 2.0756 | 2.0494 | 1.5204
12.9792 | 82.4111 | 81.8426 | 76.3952 | 2.0761 | 2.0493 | 1.5206
12.9833 | 82.3952 | 81.7782 | 76.3965 | 2.0765 | 2.0494 | 1.5209
12.9875 | 82.3706 | 81.8468 | 76.3772 | 2.0767 | 2.0496 | 1.521
12.9917 | 82.3764 | 81.8936 | 76.3575 | 2.0769 | 2.0497 | 1.5212
12.9958 | 82.4043 | 81.853 | 76.3729 | 2.0771 | 2.0506 | 1.5212
13 | 82.4103 | 81.8257 | 76.3887 | 2.0774 | 2.0513 | 1.5212
13.0042 | 82.389 | 81.8097 | 76.3849 | 2.078 | 2.0509 | 1.5215
13.0084 | 82.3702 | 81.7897 | 76.3818 | 2.0782 | 2.0508 | 1.5218
13.0125 | 82.3559 | 81.8495 | 76.3698 | 2.0783 | 2.0513 | 1.5218
13.0167 | 82.3569 | 81.898 | 76.3561 | 2.0786 | 2.0518 | 1.5217
13.0209 | 82.3769 | 81.811 | 76.372 | 2.0791 | 2.0522 | 1.5219
13.025 | 82.3709 | 81.7491 | 76.389 | 2.0795 | 2.0526 | 1.522
13.0292 | 82.3333 | 81.7804 | 76.3671 | 2.0799 | 2.0524 | 1.5222
13.0333 | 82.3378 | 81.7957 | 76.3464 | 2.0801 | 2.0522 | 1.5224
13.0375 | 82.3594 | 81.8092 | 76.3533 | 2.0802 | 2.0531 | 1.5223
13.0417 | 82.3734 | 81.8238 | 76.3587 | 2.0805 | 2.0538 | 1.5222
13.0458 | 82.3906 | 81.7529 | 76.3651 | 2.0811 | 2.0538 | 1.5225
13.05 | 82.3763 | 81.6964 | 76.3725 | 2.0813 | 2.0539 | 1.5228
13.0542 | 82.3451 | 81.7632 | 76.3516 | 2.0815 | 2.054 | 1.5228
13.0583 | 82.3469 | 81.8074 | 76.3301 | 2.0816 | 2.0541 | 1.5228
13.0625 | 82.3692 | 81.7629 | 76.3475 | 2.0818 | 2.0549 | 1.5229
13.0667 | 82.3623 | 81.7333 | 76.3647 | 2.0822 | 2.0557 | 1.5229
13.0709 | 82.346 | 81.7135 | 76.3545 | 2.0826 | 2.0553 | 1.5231
13.075 | 82.3318 | 81.6909 | 76.3467 | 2.0828 | 2.0552 | 1.5233
13.0792 | 82.3217 | 81.7486 | 76.3405 | 2.0829 | 2.0558 | 1.5233
13.0834 | 82.336 | 81.7922 | 76.3326 | 2.0832 | 2.0562 | 1.5232
13.0875 | 82.3589 | 81.7097 | 76.3441 | 2.0836 | 2.0567 | 1.5234
13.0917 | 82.345 | 81.6499 | 76.3556 | 2.084 | 2.0571 | 1.5235
13.0958 | 82.319 | 81.688 | 76.3425 | 2.0843 | 2.0568 | 1.5236
13.1 | 82.3171 | 81.7087 | 76.3304 | 2.0844 | 2.0567 | 1.5237
13.1042 | 82.3314 | 81.7184 | 76.3351 | 2.0844 | 2.0576 | 1.5237
13.1083 | 82.3442 | 81.7305 | 76.3383 | 2.0848 | 2.0583 | 1.5237
13.1125 | 82.3464 | 81.6592 | 76.3378 | 2.0853 | 2.0582 | 1.5238
13.1167 | 82.3233 | 81.6033 | 76.338 | 2.0856 | 2.0583 | 1.524
13.1209 | 82.2933 | 81.6696 | 76.3294 | 2.0857 | 2.0585 | 1.524
13.125 | 82.2832 | 81.7135 | 76.321 | 2.086 | 2.0586 | 1.524
13.1292 | 82.3027 | 81.6658 | 76.326 | 2.0863 | 2.0594 | 1.5241
13.1334 | 82.2883 | 81.6365 | 76.331 | 2.0868 | 2.0601 | 1.5242
13.1375 | 82.2742 | 81.6208 | 76.3289 | 2.0873 | 2.0598 | 1.5242
13.1417 | 82.2647 | 81.6037 | 76.327 | 2.0877 | 2.0596 | 1.5243
13.1459 | 82.252 | 81.6518 | 76.3226 | 2.0878 | 2.0603 | 1.5244
13.15 | 82.2556 | 81.6859 | 76.3175 | 2.0884 | 2.0608 | 1.5244
13.1542 | 82.2691 | 81.6088 | 76.3196 | 2.0888 | 2.0612 | 1.5245
13.1583 | 82.2607 | 81.5537 | 76.3228 | 2.0893 | 2.0615 | 1.5245
13.1625 | 82.2409 | 81.5941 | 76.3231 | 2.0897 | 2.0614 | 1.5246
13.1667 | 82.2645 | 81.6174 | 76.3228 | 2.0899 | 2.0613 | 1.5246
13.1708 | 82.2771 | 81.6143 | 76.3171 | 2.0901 | 2.0622 | 1.5247
13.175 | 82.2771 | 81.6162 | 76.311 | 2.0905 | 2.0629 | 1.5248
13.1792 | 82.2908 | 81.5611 | 76.3139 | 2.0909 | 2.0628 | 1.5248
13.1834 | 82.2842 | 81.5188 | 76.3176 | 2.091 | 2.0628 | 1.5248
13.1875 | 82.267 | 81.5869 | 76.3174 | 2.0912 | 2.0631 | 1.5249
13.1917 | 82.2923 | 81.6316 | 76.3164 | 2.0914 | 2.0632 | 1.525
13.1959 | 82.3016 | 81.5815 | 76.3108 | 2.0916 | 2.0639 | 1.525
13.2 | 82.2724 | 81.5498 | 76.3057 | 2.0919 | 2.0645 | 1.525
13.2042 | 82.2699 | 81.5401 | 76.3107 | 2.0922 | 2.0642 | 1.5251
13.2084 | 82.2642 | 81.5256 | 76.3155 | 2.0922 | 2.064 | 1.5251
13.2125 | 82.2543 | 81.5735 | 76.311 | 2.0924 | 2.0646 | 1.5252
13.2167 | 82.2632 | 81.6049 | 76.3063 | 2.0928 | 2.065 | 1.5253
13.2208 | 82.265 | 81.5429 | 76.3056 | 2.0931 | 2.0653 | 1.5252
13.225 | 82.2282 | 81.5017 | 76.3057 | 2.0934 | 2.0655 | 1.5252
13.2292 | 82.2113 | 81.5319 | 76.3097 | 2.0938 | 2.0654 | 1.5253
13.2334 | 82.2285 | 81.547 | 76.3124 | 2.094 | 2.0654 | 1.5254
13.2375 | 82.2213 | 81.5434 | 76.3048 | 2.0942 | 2.0661 | 1.5254
13.2417 | 82.2133 | 81.5401 | 76.2981 | 2.0949 | 2.0666 | 1.5254
13.2459 | 82.2176 | 81.5005 | 76.3026 | 2.0953 | 2.0665 | 1.5254
13.25 | 82.1965 | 81.4713 | 76.3075 | 2.0954 | 2.0665 | 1.5254
13.2542 | 82.1955 | 81.5209 | 76.3069 | 2.0958 | 2.0667 | 1.5255
13.2584 | 82.2305 | 81.5545 | 76.3048 | 2.0961 | 2.0669 | 1.5256
13.2625 | 82.2336 | 81.5139 | 76.2993 | 2.0964 | 2.0674 | 1.5256
13.2667 | 82.2069 | 81.4886 | 76.2953 | 2.0969 | 2.0678 | 1.5256
13.2709 | 82.2014 | 81.4865 | 76.3018 | 2.0972 | 2.0676 | 1.5256
13.275 | 82.1949 | 81.4804 | 76.308 | 2.0973 | 2.0675 | 1.5257
13.2792 | 82.1879 | 81.5093 | 76.3037 | 2.0976 | 2.068 | 1.5257
13.2833 | 82.2064 | 81.5303 | 76.2982 | 2.0981 | 2.0684 | 1.5258
13.2875 | 82.2085 | 81.4742 | 76.2965 | 2.0984 | 2.0686 | 1.5257
13.2917 | 82.1739 | 81.4364 | 76.296 | 2.0988 | 2.0688 | 1.5257
13.2959 | 82.1682 | 81.4664 | 76.3002 | 2.0991 | 2.0687 | 1.5258
13.3 | 82.1895 | 81.4801 | 76.3038 | 2.0993 | 2.0688 | 1.5258
13.3042 | 82.187 | 81.4766 | 76.2992 | 2.0995 | 2.0694 | 1.5259
13.3084 | 82.1844 | 81.4776 | 76.2944 | 2.1001 | 2.0698 | 1.5259
13.3125 | 82.1901 | 81.4359 | 76.2953 | 2.1004 | 2.0698 | 1.5259
13.3167 | 82.1656 | 81.406 | 76.2968 | 2.1005 | 2.0699 | 1.5259
13.3209 | 82.1617 | 81.4456 | 76.2982 | 2.1008 | 2.0701 | 1.5259
13.325 | 82.1944 | 81.4668 | 76.299 | 2.1011 | 2.0703 | 1.526
13.3292 | 82.1903 | 81.4347 | 76.2962 | 2.1014 | 2.0708 | 1.526
13.3334 | 82.1716 | 81.4163 | 76.2937 | 2.1018 | 2.0712 | 1.526
13.3375 | 82.167 | 81.4033 | 76.2948 | 2.1021 | 2.0711 | 1.526
13.3417 | 82.1666 | 81.3892 | 76.2956 | 2.1021 | 2.0712 | 1.526
13.3458 | 82.1574 | 81.4165 | 76.2954 | 2.1024 | 2.0716 | 1.526
13.35 | 82.1717 | 81.4313 | 76.2953 | 2.1028 | 2.0719 | 1.5261
13.3542 | 82.1683 | 81.3899 | 76.2941 | 2.1031 | 2.0722 | 1.5261
13.3584 | 82.1345 | 81.3644 | 76.2934 | 2.1034 | 2.0725 | 1.5261
13.3625 | 82.1291 | 81.3775 | 76.2941 | 2.1037 | 2.0726 | 1.5261
13.3667 | 82.1452 | 81.3807 | 76.294 | 2.1039 | 2.0727 | 1.5261
13.3709 | 82.1376 | 81.3835 | 76.2935 | 2.1042 | 2.0732 | 1.5261
13.375 | 82.1291 | 81.3851 | 76.2936 | 2.1048 | 2.0736 | 1.5261
13.3792 | 82.1274 | 81.3532 | 76.2931 | 2.1052 | 2.0737 | 1.5261
13.3834 | 82.1059 | 81.3316 | 76.2928 | 2.1054 | 2.0739 | 1.5262
13.3875 | 82.0997 | 81.3548 | 76.2938 | 2.1057 | 2.0741 | 1.5262
13.3917 | 82.1298 | 81.3653 | 76.2938 | 2.1061 | 2.0743 | 1.5262
13.3959 | 82.1171 | 81.3439 | 76.2933 | 2.1065 | 2.0747 | 1.5262
13.4 | 82.0954 | 81.3305 | 76.2936 | 2.107 | 2.0751 | 1.5262
13.4042 | 82.0939 | 81.3213 | 76.2935 | 2.1073 | 2.0752 | 1.5262
13.4084 | 82.0928 | 81.3134 | 76.2931 | 2.1074 | 2.0753 | 1.5262
13.4125 | 82.1001 | 81.3397 | 76.2926 | 2.1078 | 2.0756 | 1.5262
13.4167 | 82.1228 | 81.358 | 76.2917 | 2.1082 | 2.0758 | 1.5262
13.4209 | 82.0885 | 81.3007 | 76.2949 | 2.1089 | 2.0763 | 1.5262
13.425 | 82.0276 | 81.254 | 76.2998 | 2.1094 | 2.0768 | 1.5262
13.4292 | 82.0281 | 81.269 | 76.3017 | 2.1096 | 2.0767 | 1.5262
13.4334 | 82.0464 | 81.2747 | 76.3025 | 2.1097 | 2.0767 | 1.5262
13.4375 | 82.0975 | 81.3244 | 76.2954 | 2.1101 | 2.0771 | 1.5262
13.4417 | 82.1456 | 81.3728 | 76.2877 | 2.1107 | 2.0774 | 1.5262
13.4459 | 82.1274 | 81.3271 | 76.2892 | 2.111 | 2.0775 | 1.5262
13.45 | 82.0803 | 81.2928 | 76.2925 | 2.1113 | 2.0777 | 1.5262
13.4542 | 82.006 | 81.2559 | 76.3064 | 2.1118 | 2.078 | 1.5261
13.4584 | 81.9636 | 81.2089 | 76.3205 | 2.1123 | 2.0783 | 1.5261
13.4625 | 81.9313 | 81.2035 | 76.3219 | 2.113 | 2.0787 | 1.526
13.4667 | 81.9091 | 81.1958 | 76.3242 | 2.1137 | 2.0791 | 1.526
13.4709 | 82.0089 | 81.3006 | 76.3099 | 2.1139 | 2.0787 | 1.526
13.475 | 82.097 | 81.4027 | 76.2939 | 2.1139 | 2.0784 | 1.526
13.4792 | 82.1856 | 81.4361 | 76.2958 | 2.1141 | 2.0786 | 1.5259
13.4834 | 82.2451 | 81.4716 | 76.2968 | 2.1144 | 2.0787 | 1.5259
13.4875 | 82.2776 | 81.3901 | 76.3027 | 2.1147 | 2.0782 | 1.5259
13.4917 | 82.2501 | 81.3241 | 76.3112 | 2.1147 | 2.0778 | 1.5259
13.4959 | 82.1272 | 81.3291 | 76.3185 | 2.1157 | 2.0778 | 1.5258
13.5 | 82.0763 | 81.319 | 76.3262 | 2.1159 | 2.0778 | 1.5257
13.5042 | 81.9805 | 81.3687 | 76.3308 | 2.1156 | 2.0776 | 1.5257
13.5084 | 82.0061 | 81.4001 | 76.3352 | 2.1151 | 2.0774 | 1.5256
13.5125 | 82.1569 | 81.5215 | 76.3173 | 2.1152 | 2.0764 | 1.5256
13.5167 | 82.326 | 81.6409 | 76.2979 | 2.1146 | 2.0755 | 1.5256
13.5209 | 82.4608 | 81.7303 | 76.2931 | 2.1146 | 2.0744 | 1.5256
13.525 | 82.5614 | 81.8242 | 76.2864 | 2.114 | 2.0734 | 1.5256
13.5292 | 82.7083 | 81.8239 | 76.2786 | 2.1125 | 2.0718 | 1.5258
13.5334 | 82.7957 | 81.859 | 76.27 | 2.1107 | 2.0702 | 1.526
13.5375 | 82.8255 | 81.792 | 76.2657 | 2.1095 | 2.0694 | 1.5261
13.5417 | 82.8331 | 81.7563 | 76.2616 | 2.1083 | 2.0685 | 1.5261
13.5459 | 82.7515 | 81.6242 | 76.2771 | 2.1065 | 2.0684 | 1.5262
13.55 | 82.6411 | 81.5018 | 76.2939 | 2.1052 | 2.0679 | 1.5263
13.5542 | 82.6166 | 81.4267 | 76.2918 | 2.1042 | 2.0684 | 1.5263
13.5584 | 82.5893 | 81.3519 | 76.2907 | 2.1033 | 2.0685 | 1.5264
13.5625 | 82.4712 | 81.3103 | 76.2979 | 2.1033 | 2.0696 | 1.5263
13.5667 | 82.3988 | 81.2379 | 76.306 | 2.1036 | 2.0705 | 1.5261
13.5709 | 82.3137 | 81.2557 | 76.3098 | 2.1033 | 2.0712 | 1.5262
13.575 | 82.2052 | 81.2438 | 76.3136 | 2.1033 | 2.0717 | 1.5262
13.5792 | 82.1289 | 81.3032 | 76.3044 | 2.1036 | 2.0724 | 1.5262
13.5834 | 82.1085 | 81.3473 | 76.2948 | 2.1042 | 2.0732 | 1.5261
13.5875 | 82.0364 | 81.3828 | 76.3006 | 2.1042 | 2.0733 | 1.526
13.5917 | 82.0423 | 81.4025 | 76.3063 | 2.1049 | 2.0735 | 1.526
13.5959 | 82.0935 | 81.4408 | 76.2993 | 2.1053 | 2.0733 | 1.5261
13.6 | 82.1341 | 81.492 | 76.2916 | 2.1057 | 2.0733 | 1.5262
13.6042 | 82.1142 | 81.4806 | 76.2891 | 2.1063 | 2.0732 | 1.5261
13.6084 | 82.1191 | 81.4831 | 76.2873 | 2.1069 | 2.0733 | 1.5261
13.6125 | 82.1285 | 81.4854 | 76.2967 | 2.1068 | 2.0728 | 1.5261
13.6167 | 82.1407 | 81.4917 | 76.3056 | 2.1067 | 2.0724 | 1.5261
13.6209 | 82.1901 | 81.4691 | 76.2996 | 2.107 | 2.0726 | 1.5261
13.625 | 82.2035 | 81.4662 | 76.2936 | 2.1074 | 2.0728 | 1.5262
13.6292 | 82.2002 | 81.4257 | 76.2859 | 2.1075 | 2.0727 | 1.5262
13.6334 | 82.1424 | 81.3811 | 76.2794 | 2.1077 | 2.0726 | 1.5262
13.6375 | 82.1639 | 81.4134 | 76.2865 | 2.1075 | 2.0727 | 1.5262
13.6417 | 82.1898 | 81.4387 | 76.2921 | 2.1075 | 2.0726 | 1.5262
13.6459 | 82.2045 | 81.4209 | 76.3108 | 2.1078 | 2.073 | 1.5261
13.65 | 82.1989 | 81.4098 | 76.3298 | 2.1081 | 2.0733 | 1.526
13.6542 | 82.2095 | 81.4094 | 76.3139 | 2.108 | 2.0731 | 1.5261
13.6584 | 82.1819 | 81.395 | 76.2986 | 2.1079 | 2.073 | 1.5262
13.6625 | 82.221 | 81.388 | 76.2676 | 2.1078 | 2.0735 | 1.5263
13.6667 | 82.2243 | 81.3846 | 76.2364 | 2.1079 | 2.0739 | 1.5263
13.6709 | 82.243 | 81.3743 | 76.2666 | 2.1082 | 2.0737 | 1.5262
13.675 | 82.2145 | 81.364 | 76.2969 | 2.1083 | 2.0737 | 1.5262
13.6792 | 82.2381 | 81.433 | 76.3177 | 2.108 | 2.0737 | 1.5262
13.6834 | 82.2796 | 81.4902 | 76.3373 | 2.1075 | 2.0736 | 1.5263
13.6875 | 82.3482 | 81.4254 | 76.3106 | 2.1075 | 2.074 | 1.5263
13.6917 | 82.3902 | 81.3815 | 76.2849 | 2.1079 | 2.0745 | 1.5262
13.6959 | 82.3585 | 81.3547 | 76.2732 | 2.1082 | 2.0741 | 1.5263
13.7 | 82.2997 | 81.3236 | 76.2619 | 2.1086 | 2.0738 | 1.5263
13.7042 | 82.2737 | 81.3655 | 76.2505 | 2.1082 | 2.0744 | 1.5265
13.7084 | 82.2486 | 81.4002 | 76.2392 | 2.1076 | 2.0748 | 1.5267
13.7125 | 82.252 | 81.3353 | 76.2399 | 2.1078 | 2.0751 | 1.5268
13.7167 | 82.2669 | 81.2854 | 76.2417 | 2.1081 | 2.0754 | 1.5268
13.7209 | 82.2192 | 81.3333 | 76.2554 | 2.1083 | 2.0752 | 1.527
13.725 | 82.171 | 81.366 | 76.2669 | 2.1085 | 2.075 | 1.5271
13.7292 | 82.1375 | 81.354 | 76.2576 | 2.1084 | 2.0758 | 1.5272
13.7334 | 82.1579 | 81.3515 | 76.2488 | 2.1084 | 2.0765 | 1.5273
13.7375 | 82.0925 | 81.2658 | 76.2281 | 2.1088 | 2.0765 | 1.5275
13.7417 | 82.0562 | 81.195 | 76.2091 | 2.1096 | 2.0766 | 1.5277
13.7459 | 82.0153 | 81.2266 | 76.1831 | 2.1101 | 2.0771 | 1.528
13.75 | 81.9513 | 81.2435 | 76.1566 | 2.1103 | 2.0775 | 1.5283
13.7542 | 81.9576 | 81.1877 | 76.1458 | 2.1111 | 2.0785 | 1.5286
13.7584 | 81.9878 | 81.1418 | 76.137 | 2.1118 | 2.0794 | 1.5289
13.7625 | 81.9788 | 81.1359 | 76.1305 | 2.1127 | 2.0795 | 1.5293
13.7667 | 81.941 | 81.1222 | 76.1238 | 2.1136 | 2.0797 | 1.5298
13.7709 | 81.9749 | 81.18 | 76.1291 | 2.114 | 2.0805 | 1.53
13.775 | 81.9955 | 81.2192 | 76.1327 | 2.1142 | 2.0812 | 1.5302
13.7792 | 82.0319 | 81.1846 | 76.15 | 2.1147 | 2.0815 | 1.5304
13.7834 | 82.0829 | 81.1585 | 76.168 | 2.1154 | 2.0819 | 1.5306
13.7875 | 82.0684 | 81.1909 | 76.1614 | 2.1156 | 2.0818 | 1.5308
13.7917 | 82.0383 | 81.2196 | 76.1542 | 2.1158 | 2.0818 | 1.5309
13.7959 | 82.0654 | 81.2237 | 76.1616 | 2.1158 | 2.0823 | 1.5309
13.8 | 82.1014 | 81.2316 | 76.1684 | 2.1158 | 2.0827 | 1.5309
13.8042 | 82.0903 | 81.2003 | 76.1676 | 2.1161 | 2.0826 | 1.5311
13.8084 | 82.0795 | 81.1797 | 76.1681 | 2.1166 | 2.0825 | 1.5313
13.8125 | 82.0543 | 81.1986 | 76.1521 | 2.1166 | 2.0828 | 1.5313
13.8167 | 82.0157 | 81.2152 | 76.1359 | 2.1166 | 2.083 | 1.5314
13.8209 | 82.0318 | 81.1847 | 76.1392 | 2.1169 | 2.0833 | 1.5315
13.825 | 82.054 | 81.1565 | 76.1423 | 2.1172 | 2.0836 | 1.5316
13.8292 | 82.0319 | 81.1583 | 76.1347 | 2.1176 | 2.0836 | 1.5318
13.8334 | 82.0058 | 81.1578 | 76.1279 | 2.118 | 2.0836 | 1.5319
13.8375 | 82.0111 | 81.1627 | 76.1232 | 2.1181 | 2.084 | 1.532
13.8417 | 82.0121 | 81.1632 | 76.1188 | 2.1182 | 2.0845 | 1.5321
13.8459 | 82.0189 | 81.153 | 76.1299 | 2.1186 | 2.0845 | 1.5322
13.85 | 82.0361 | 81.1404 | 76.1404 | 2.1191 | 2.0845 | 1.5323
13.8542 | 82.0201 | 81.1534 | 76.1313 | 2.1192 | 2.0848 | 1.5324
13.8584 | 81.9943 | 81.1691 | 76.1219 | 2.1195 | 2.085 | 1.5326
13.8625 | 82.0138 | 81.1404 | 76.1189 | 2.1197 | 2.0852 | 1.5326
13.8667 | 82.0241 | 81.1161 | 76.1161 | 2.1198 | 2.0855 | 1.5326
13.8709 | 82.0149 | 81.1267 | 76.119 | 2.1202 | 2.0855 | 1.5327
13.875 | 82.0218 | 81.1312 | 76.1221 | 2.1205 | 2.0855 | 1.5329
13.8792 | 82.0183 | 81.1327 | 76.1158 | 2.1206 | 2.0859 | 1.533
13.8834 | 82.0062 | 81.1367 | 76.1101 | 2.1207 | 2.0863 | 1.533
13.8875 | 82.0146 | 81.1214 | 76.1169 | 2.121 | 2.0863 | 1.533
13.8917 | 82.0185 | 81.104 | 76.1227 | 2.1213 | 2.0863 | 1.5331
13.8959 | 81.998 | 81.1256 | 76.1166 | 2.1215 | 2.0865 | 1.5332
13.9 | 81.9856 | 81.1453 | 76.1102 | 2.1218 | 2.0866 | 1.5333
13.9042 | 81.9881 | 81.112 | 76.1096 | 2.122 | 2.087 | 1.5333
13.9084 | 81.9859 | 81.0898 | 76.1098 | 2.1222 | 2.0873 | 1.5333
13.9125 | 81.9794 | 81.0957 | 76.1096 | 2.1226 | 2.0872 | 1.5334
13.9167 | 81.9899 | 81.0926 | 76.1093 | 2.1228 | 2.0871 | 1.5336
13.9209 | 81.9949 | 81.1043 | 76.1051 | 2.1229 | 2.0876 | 1.5336
13.925 | 81.9926 | 81.1188 | 76.1011 | 2.1231 | 2.0879 | 1.5336
13.9292 | 82.0063 | 81.0797 | 76.1057 | 2.1234 | 2.088 | 1.5337
13.9334 | 82.007 | 81.0474 | 76.1101 | 2.1235 | 2.0882 | 1.5338
13.9375 | 81.9885 | 81.078 | 76.1012 | 2.1237 | 2.0882 | 1.5338
13.9417 | 81.9828 | 81.0945 | 76.0919 | 2.1239 | 2.0882 | 1.5339
13.9459 | 81.9948 | 81.0803 | 76.099 | 2.124 | 2.0887 | 1.5339
13.95 | 81.9854 | 81.0758 | 76.107 | 2.1242 | 2.0891 | 1.5338
13.9542 | 81.9812 | 81.0566 | 76.1028 | 2.1246 | 2.089 | 1.534
13.9584 | 81.9808 | 81.0348 | 76.0988 | 2.1248 | 2.089 | 1.5342
13.9625 | 81.969 | 81.0679 | 76.0926 | 2.1249 | 2.0893 | 1.5341
13.9667 | 81.9628 | 81.0926 | 76.0854 | 2.1251 | 2.0895 | 1.5341
13.9709 | 81.9833 | 81.0496 | 76.0968 | 2.1253 | 2.0898 | 1.5342
13.975 | 81.9729 | 81.0217 | 76.1092 | 2.1256 | 2.0902 | 1.5342
13.9792 | 81.9574 | 81.0382 | 76.0961 | 2.1259 | 2.09 | 1.5343
13.9834 | 81.966 | 81.0423 | 76.0831 | 2.1261 | 2.0899 | 1.5344
13.9875 | 81.9716 | 81.0536 | 76.0893 | 2.1261 | 2.0904 | 1.5343
13.9917 | 81.9732 | 81.068 | 76.0939 | 2.1263 | 2.0908 | 1.5343
13.9959 | 81.9761 | 81.0179 | 76.0942 | 2.1267 | 2.0908 | 1.5344
14 | 81.9554 | 80.9782 | 76.0961 | 2.1269 | 2.091 | 1.5346
14.0042 | 81.9293 | 81.0227 | 76.0847 | 2.1271 | 2.091 | 1.5346
14.0084 | 81.9289 | 81.05 | 76.0734 | 2.1273 | 2.091 | 1.5345
14.0125 | 81.9478 | 81.0251 | 76.087 | 2.1275 | 2.0915 | 1.5346
14.0167 | 81.9401 | 81.0157 | 76.0995 | 2.1279 | 2.092 | 1.5346
14.0209 | 81.9282 | 80.9929 | 76.0884 | 2.1283 | 2.0918 | 1.5347
14.025 | 81.9095 | 80.9687 | 76.0786 | 2.1287 | 2.0917 | 1.5348
14.0292 | 81.8987 | 81.0131 | 76.0785 | 2.1287 | 2.0921 | 1.5348
14.0334 | 81.9106 | 81.0448 | 76.0775 | 2.1291 | 2.0923 | 1.5347
14.0375 | 81.9237 | 80.9915 | 76.0867 | 2.1294 | 2.0927 | 1.5348
14.0417 | 81.9278 | 80.9575 | 76.096 | 2.1298 | 2.093 | 1.5349
14.0459 | 81.9046 | 80.9766 | 76.0825 | 2.1301 | 2.0928 | 1.5349
14.05 | 81.9072 | 80.982 | 76.0693 | 2.1303 | 2.0927 | 1.535
14.0542 | 81.9251 | 80.9923 | 76.0768 | 2.1303 | 2.0933 | 1.5349
14.0584 | 81.941 | 81.005 | 76.0833 | 2.1306 | 2.0937 | 1.5349
14.0625 | 81.9443 | 80.9605 | 76.0832 | 2.1309 | 2.0937 | 1.535
14.0667 | 81.9457 | 80.927 | 76.0846 | 2.1311 | 2.0937 | 1.5351
14.0709 | 81.9212 | 80.9784 | 76.0773 | 2.1311 | 2.0938 | 1.5351
14.075 | 81.9244 | 81.0108 | 76.0693 | 2.1312 | 2.0938 | 1.5351
14.0792 | 81.9464 | 80.973 | 76.0767 | 2.1313 | 2.0943 | 1.5351
14.0834 | 81.9403 | 80.952 | 76.0834 | 2.1316 | 2.0948 | 1.5351
14.0875 | 81.9254 | 80.9434 | 76.0783 | 2.1319 | 2.0945 | 1.5352
14.0917 | 81.9126 | 80.9275 | 76.0746 | 2.132 | 2.0943 | 1.5352
14.0959 | 81.9037 | 80.9757 | 76.0739 | 2.132 | 2.0947 | 1.5352
14.1 | 81.9024 | 81.0108 | 76.0721 | 2.1322 | 2.095 | 1.5352
14.1042 | 81.9164 | 80.9488 | 76.076 | 2.1325 | 2.0952 | 1.5353
14.1084 | 81.9032 | 80.91 | 76.08 | 2.1328 | 2.0955 | 1.5353
14.1125 | 81.8728 | 80.9398 | 76.0749 | 2.1331 | 2.0952 | 1.5353
14.1167 | 81.8686 | 80.9498 | 76.0703 | 2.1333 | 2.095 | 1.5353
14.1209 | 81.8736 | 80.9569 | 76.072 | 2.1335 | 2.0956 | 1.5353
14.125 | 81.8724 | 80.9661 | 76.0732 | 2.1339 | 2.0961 | 1.5353
14.1292 | 81.8806 | 80.919 | 76.0745 | 2.1343 | 2.0959 | 1.5354
14.1334 | 81.8779 | 80.8864 | 76.0762 | 2.1345 | 2.0959 | 1.5354
14.1375 | 81.8615 | 80.9386 | 76.0719 | 2.1347 | 2.096 | 1.5354
14.1417 | 81.8737 | 80.9693 | 76.0674 | 2.1349 | 2.096 | 1.5355
14.1459 | 81.8896 | 80.9357 | 76.07 | 2.1351 | 2.0965 | 1.5355
14.15 | 81.8781 | 80.9186 | 76.073 | 2.1355 | 2.0969 | 1.5355
14.1542 | 81.8669 | 80.9106 | 76.0739 | 2.1358 | 2.0966 | 1.5355
14.1584 | 81.8666 | 80.9012 | 76.0744 | 2.136 | 2.0964 | 1.5355
14.1625 | 81.8558 | 80.9346 | 76.07 | 2.136 | 2.0968 | 1.5355
14.1667 | 81.8648 | 80.9573 | 76.0651 | 2.1364 | 2.0971 | 1.5355
14.1709 | 81.8743 | 80.9048 | 76.0687 | 2.1367 | 2.0972 | 1.5355
14.175 | 81.8585 | 80.871 | 76.0733 | 2.1369 | 2.0974 | 1.5355
14.1792 | 81.8398 | 80.9024 | 76.0727 | 2.1372 | 2.0972 | 1.5356
14.1834 | 81.852 | 80.9176 | 76.0713 | 2.1373 | 2.0972 | 1.5356
14.1875 | 81.858 | 80.9126 | 76.0674 | 2.1375 | 2.0977 | 1.5356
14.1917 | 81.8534 | 80.9132 | 76.0635 | 2.1379 | 2.0981 | 1.5356
14.1959 | 81.8617 | 80.8766 | 76.0683 | 2.1382 | 2.098 | 1.5356
14.2 | 81.8469 | 80.8495 | 76.074 | 2.1383 | 2.0979 | 1.5356
14.2042 | 81.8339 | 80.8951 | 76.0712 | 2.1385 | 2.0981 | 1.5357
14.2084 | 81.8576 | 80.9219 | 76.0674 | 2.1387 | 2.0982 | 1.5357
14.2125 | 81.8658 | 80.8815 | 76.0658 | 2.1388 | 2.0986 | 1.5357
14.2167 | 81.85 | 80.8589 | 76.0647 | 2.1392 | 2.099 | 1.5357
14.2209 | 81.8422 | 80.858 | 76.0686 | 2.1394 | 2.0988 | 1.5357
14.225 | 81.839 | 80.8502 | 76.0729 | 2.1395 | 2.0987 | 1.5357
14.2292 | 81.8294 | 80.88 | 76.0687 | 2.1396 | 2.0991 | 1.5357
14.2334 | 81.8421 | 80.8998 | 76.0639 | 2.1399 | 2.0994 | 1.5357
14.2375 | 81.847 | 80.8484 | 76.0655 | 2.1402 | 2.0996 | 1.5357
14.2417 | 81.8199 | 80.8169 | 76.0675 | 2.1404 | 2.0998 | 1.5357
14.2459 | 81.8043 | 80.8471 | 76.0688 | 2.1407 | 2.0997 | 1.5357
14.25 | 81.8136 | 80.8594 | 76.0698 | 2.1409 | 2.0996 | 1.5358
14.2542 | 81.8173 | 80.8583 | 76.0665 | 2.141 | 2.1002 | 1.5358
14.2584 | 81.8103 | 80.8621 | 76.0631 | 2.1415 | 2.1005 | 1.5358
14.2625 | 81.8177 | 80.8282 | 76.0656 | 2.1418 | 2.1004 | 1.5358
14.2667 | 81.8026 | 80.8053 | 76.0685 | 2.1419 | 2.1005 | 1.5358
14.2709 | 81.7723 | 80.8319 | 76.0695 | 2.1423 | 2.1007 | 1.5358
14.275 | 81.7842 | 80.839 | 76.0704 | 2.1427 | 2.1009 | 1.5358
14.2792 | 81.7984 | 80.8221 | 76.0678 | 2.1428 | 2.1012 | 1.5358
14.2834 | 81.7946 | 80.8207 | 76.065 | 2.1431 | 2.1013 | 1.5358
14.2875 | 81.8094 | 80.8298 | 76.0644 | 2.1435 | 2.1012 | 1.5358
14.2917 | 81.8241 | 80.8369 | 76.0637 | 2.1436 | 2.1013 | 1.5358
14.2959 | 81.7852 | 80.8329 | 76.0661 | 2.1438 | 2.1017 | 1.5358
14.3 | 81.7618 | 80.8201 | 76.0693 | 2.1443 | 2.1019 | 1.5358
14.3042 | 81.7408 | 80.7627 | 76.0748 | 2.1447 | 2.1022 | 1.5358
14.3084 | 81.6935 | 80.7204 | 76.0807 | 2.1451 | 2.1025 | 1.5357
14.3125 | 81.7256 | 80.784 | 76.0754 | 2.1453 | 2.1023 | 1.5358
14.3167 | 81.784 | 80.8293 | 76.0691 | 2.1454 | 2.1022 | 1.5358
14.3209 | 81.8385 | 80.8705 | 76.0608 | 2.1455 | 2.1025 | 1.5358
14.325 | 81.8706 | 80.9176 | 76.0521 | 2.1459 | 2.1027 | 1.5358
14.3292 | 81.8466 | 80.8181 | 76.0651 | 2.1465 | 2.1028 | 1.5357
14.3334 | 81.783 | 80.7349 | 76.0798 | 2.1469 | 2.103 | 1.5357
14.3375 | 81.6794 | 80.7382 | 76.085 | 2.1471 | 2.103 | 1.5357
14.3417 | 81.6732 | 80.7201 | 76.0906 | 2.1475 | 2.1029 | 1.5357
14.3459 | 81.6231 | 80.7572 | 76.0857 | 2.148 | 2.1034 | 1.5356
14.35 | 81.6178 | 80.795 | 76.0807 | 2.1488 | 2.1039 | 1.5355
14.3542 | 81.6736 | 80.8433 | 76.077 | 2.1493 | 2.1034 | 1.5356
14.3584 | 81.749 | 80.89 | 76.0722 | 2.1491 | 2.103 | 1.5356
14.3625 | 81.8272 | 80.9285 | 76.0675 | 2.1492 | 2.1029 | 1.5356
14.3667 | 81.9102 | 80.9673 | 76.0623 | 2.1494 | 2.1028 | 1.5356
14.3709 | 81.9709 | 80.887 | 76.0711 | 2.1494 | 2.1027 | 1.5356
14.375 | 81.9568 | 80.826 | 76.0819 | 2.1498 | 2.1026 | 1.5355
14.3792 | 81.8857 | 80.8494 | 76.0848 | 2.1504 | 2.1021 | 1.5355
14.3834 | 81.8532 | 80.8551 | 76.0872 | 2.1502 | 2.1017 | 1.5355
14.3875 | 81.7443 | 80.8907 | 76.0865 | 2.1501 | 2.1019 | 1.5355
14.3917 | 81.7429 | 80.9128 | 76.0859 | 2.1501 | 2.1021 | 1.5354
14.3959 | 81.8171 | 80.9541 | 76.0817 | 2.1495 | 2.1011 | 1.5354
14.4 | 81.9105 | 80.9966 | 76.0771 | 2.1493 | 2.1004 | 1.5355
14.4042 | 82.0292 | 81.0938 | 76.0674 | 2.1495 | 2.0997 | 1.5355
14.4084 | 82.1548 | 81.1886 | 76.0555 | 2.1491 | 2.099 | 1.5355
14.4125 | 82.2352 | 81.1474 | 76.0541 | 2.1483 | 2.0984 | 1.5356
14.4167 | 82.3138 | 81.1402 | 76.0531 | 2.1475 | 2.0976 | 1.5356
14.4209 | 82.3653 | 81.0919 | 76.0518 | 2.1464 | 2.0968 | 1.5357
14.425 | 82.3481 | 81.0708 | 76.0502 | 2.1453 | 2.0959 | 1.5358
14.4292 | 82.3131 | 81.0029 | 76.0565 | 2.1443 | 2.0964 | 1.5358
14.4334 | 82.2759 | 80.9416 | 76.0631 | 2.1433 | 2.0964 | 1.5358
14.4375 | 82.2636 | 80.8561 | 76.0668 | 2.1421 | 2.0967 | 1.5358
14.4417 | 82.2495 | 80.7742 | 76.0721 | 2.1414 | 2.0967 | 1.5359
14.4459 | 82.2331 | 80.7799 | 76.0731 | 2.1409 | 2.0975 | 1.5358
14.45 | 82.1454 | 80.7572 | 76.0738 | 2.1411 | 2.0981 | 1.5358
14.4542 | 82.064 | 80.7642 | 76.0779 | 2.1407 | 2.0988 | 1.5358
14.4584 | 81.9556 | 80.7441 | 76.0825 | 2.1407 | 2.0994 | 1.5357
14.4625 | 81.9124 | 80.7944 | 76.0782 | 2.1407 | 2.0995 | 1.5357
14.4667 | 81.8516 | 80.8309 | 76.0735 | 2.1405 | 2.0998 | 1.5357
14.4709 | 81.8305 | 80.8673 | 76.0732 | 2.1409 | 2.1 | 1.5357
14.475 | 81.7768 | 80.8911 | 76.0724 | 2.1411 | 2.1005 | 1.5356
14.4792 | 81.7753 | 80.8979 | 76.0662 | 2.1414 | 2.1001 | 1.5357
14.4834 | 81.7782 | 80.9155 | 76.0603 | 2.1417 | 2.0999 | 1.5358
14.4875 | 81.774 | 80.9391 | 76.0652 | 2.1421 | 2.0997 | 1.5357
14.4917 | 81.7989 | 80.9749 | 76.0692 | 2.1425 | 2.0997 | 1.5356
14.4959 | 81.8015 | 80.9456 | 76.0799 | 2.1427 | 2.0995 | 1.5356
14.5 | 81.8112 | 80.9257 | 76.0909 | 2.1428 | 2.0994 | 1.5357
14.5042 | 81.8465 | 80.9041 | 76.067 | 2.143 | 2.0993 | 1.5358
14.5084 | 81.8547 | 80.8975 | 76.044 | 2.1431 | 2.0991 | 1.5359
14.5125 | 81.8408 | 80.8836 | 76.0449 | 2.1434 | 2.0993 | 1.5358
14.5167 | 81.8343 | 80.8654 | 76.0455 | 2.1435 | 2.0995 | 1.5357
14.5209 | 81.8264 | 80.8779 | 76.0772 | 2.1434 | 2.0994 | 1.5357
14.525 | 81.8426 | 80.8854 | 76.1081 | 2.1432 | 2.0992 | 1.5357
14.5292 | 81.8665 | 80.8942 | 76.0966 | 2.1434 | 2.0995 | 1.5357
14.5334 | 81.8984 | 80.9055 | 76.0854 | 2.1435 | 2.0997 | 1.5357
14.5375 | 81.8687 | 80.8618 | 76.061 | 2.1438 | 2.0998 | 1.5357
14.5417 | 81.8616 | 80.8102 | 76.0375 | 2.144 | 2.1 | 1.5357
14.5459 | 81.8268 | 80.8365 | 76.0417 | 2.1438 | 2.0999 | 1.5358
14.55 | 81.8198 | 80.8602 | 76.0451 | 2.1439 | 2.0998 | 1.5358
14.5542 | 81.818 | 80.8811 | 76.0616 | 2.144 | 2.1001 | 1.5358
14.5584 | 81.8202 | 80.9001 | 76.0783 | 2.1442 | 2.1004 | 1.5358
14.5625 | 81.8183 | 80.8856 | 76.0824 | 2.1443 | 2.1002 | 1.5358
14.5667 | 81.8405 | 80.8704 | 76.0861 | 2.1442 | 2.1001 | 1.5358
14.5709 | 81.8667 | 80.8711 | 76.0732 | 2.1441 | 2.1002 | 1.5358
14.575 | 81.912 | 80.8822 | 76.0597 | 2.144 | 2.1003 | 1.5358
14.5792 | 81.9319 | 80.8551 | 76.0514 | 2.1442 | 2.1004 | 1.5359
14.5834 | 81.9439 | 80.826 | 76.0448 | 2.1446 | 2.1006 | 1.5359
14.5875 | 81.9337 | 80.8232 | 76.033 | 2.1446 | 2.1007 | 1.5361
14.5917 | 81.9051 | 80.821 | 76.0211 | 2.1445 | 2.1007 | 1.5362
14.5959 | 81.9419 | 80.8204 | 76.0228 | 2.1442 | 2.101 | 1.5363
14.6 | 81.9387 | 80.8236 | 76.0241 | 2.144 | 2.1013 | 1.5363
14.6042 | 81.9688 | 80.828 | 76.0392 | 2.1444 | 2.1013 | 1.5364
14.6084 | 81.9607 | 80.8236 | 76.0542 | 2.1446 | 2.1013 | 1.5365
14.6125 | 81.9081 | 80.8148 | 76.0376 | 2.1449 | 2.1017 | 1.5366
14.6167 | 81.8792 | 80.8177 | 76.0207 | 2.1449 | 2.1019 | 1.5368
14.6209 | 81.8212 | 80.7815 | 76.0139 | 2.1447 | 2.1021 | 1.5368
14.625 | 81.7919 | 80.7486 | 76.0079 | 2.1449 | 2.1024 | 1.5368
14.6292 | 81.7537 | 80.7534 | 75.998 | 2.1453 | 2.1027 | 1.5371
14.6334 | 81.7125 | 80.7509 | 75.9887 | 2.1457 | 2.1028 | 1.5374
14.6375 | 81.6746 | 80.7191 | 75.9672 | 2.1462 | 2.1035 | 1.5376
14.6417 | 81.668 | 80.7002 | 75.9466 | 2.1467 | 2.104 | 1.5377
14.6459 | 81.681 | 80.7055 | 75.9579 | 2.1472 | 2.1041 | 1.5379
14.65 | 81.6714 | 80.6936 | 75.9686 | 2.1478 | 2.1043 | 1.5381
14.6542 | 81.6971 | 80.7332 | 75.9692 | 2.1484 | 2.1047 | 1.5384
14.6584 | 81.7163 | 80.7632 | 75.9693 | 2.1487 | 2.1051 | 1.5386
14.6625 | 81.7273 | 80.7296 | 75.9718 | 2.1489 | 2.1053 | 1.5386
14.6667 | 81.7607 | 80.7088 | 75.9747 | 2.1493 | 2.1056 | 1.5386
14.6709 | 81.7783 | 80.7451 | 75.985 | 2.1494 | 2.1054 | 1.5387
14.675 | 81.7687 | 80.7659 | 75.9941 | 2.1496 | 2.1053 | 1.5389
14.6792 | 81.7746 | 80.7693 | 75.99 | 2.1497 | 2.1057 | 1.5389
14.6834 | 81.8047 | 80.785 | 75.9865 | 2.1496 | 2.106 | 1.5389
14.6875 | 81.7899 | 80.741 | 75.9856 | 2.1497 | 2.1059 | 1.5389
14.6917 | 81.7859 | 80.7083 | 75.9855 | 2.1501 | 2.1058 | 1.5389
14.6959 | 81.7641 | 80.7514 | 75.9819 | 2.1501 | 2.1058 | 1.539
14.7 | 81.7417 | 80.7807 | 75.977 | 2.1501 | 2.1058 | 1.5391
14.7042 | 81.7346 | 80.7384 | 75.9699 | 2.1502 | 2.1063 | 1.5391
14.7084 | 81.7601 | 80.7136 | 75.964 | 2.1504 | 2.1067 | 1.5392
14.7125 | 81.7457 | 80.7046 | 75.9622 | 2.1507 | 2.1064 | 1.5393
14.7167 | 81.7172 | 80.6868 | 75.961 | 2.1511 | 2.1062 | 1.5394
14.7209 | 81.7163 | 80.7317 | 75.9618 | 2.1513 | 2.1066 | 1.5395
14.725 | 81.7228 | 80.7637 | 75.9617 | 2.1512 | 2.1069 | 1.5395
14.7292 | 81.7332 | 80.7137 | 75.9648 | 2.1515 | 2.1071 | 1.5396
14.7334 | 81.7455 | 80.6798 | 75.9687 | 2.1519 | 2.1073 | 1.5396
14.7375 | 81.7364 | 80.707 | 75.9648 | 2.1521 | 2.1071 | 1.5397
14.7417 | 81.6984 | 80.7224 | 75.9599 | 2.1523 | 2.1069 | 1.5398
14.7459 | 81.7128 | 80.7206 | 75.9569 | 2.1524 | 2.1075 | 1.5398
14.75 | 81.7437 | 80.7239 | 75.9542 | 2.1524 | 2.1079 | 1.5398
14.7542 | 81.7402 | 80.6884 | 75.9588 | 2.1527 | 2.1077 | 1.5399
14.7584 | 81.7379 | 80.6596 | 75.9646 | 2.1532 | 2.1077 | 1.5399
14.7625 | 81.7279 | 80.7061 | 75.9575 | 2.1532 | 2.1078 | 1.54
14.7667 | 81.7106 | 80.7368 | 75.9494 | 2.1531 | 2.1078 | 1.5401
14.7709 | 81.7243 | 80.7066 | 75.9554 | 2.1533 | 2.1082 | 1.5401
14.775 | 81.7516 | 80.6887 | 75.9612 | 2.1535 | 2.1085 | 1.54
14.7792 | 81.7242 | 80.6835 | 75.9591 | 2.1538 | 2.1082 | 1.5401
14.7834 | 81.696 | 80.6771 | 75.9572 | 2.1541 | 2.1081 | 1.5403
14.7875 | 81.6912 | 80.7003 | 75.95 | 2.1541 | 2.1084 | 1.5402
14.7917 | 81.6965 | 80.7173 | 75.9427 | 2.154 | 2.1087 | 1.5402
14.7959 | 81.7112 | 80.6813 | 75.9534 | 2.1544 | 2.1088 | 1.5402
14.8 | 81.7309 | 80.6564 | 75.9647 | 2.1547 | 2.1089 | 1.5403
14.8042 | 81.7159 | 80.6759 | 75.9529 | 2.1549 | 2.1088 | 1.5404
14.8084 | 81.6928 | 80.688 | 75.9409 | 2.155 | 2.1088 | 1.5405
14.8125 | 81.7089 | 80.6815 | 75.9445 | 2.1551 | 2.1092 | 1.5404
14.8167 | 81.7256 | 80.6766 | 75.9475 | 2.1551 | 2.1095 | 1.5403
14.8209 | 81.7219 | 80.6606 | 75.9519 | 2.1554 | 2.1094 | 1.5405
14.825 | 81.7139 | 80.647 | 75.9572 | 2.1557 | 2.1093 | 1.5406
14.8292 | 81.7012 | 80.6718 | 75.9463 | 2.1557 | 2.1095 | 1.5406
14.8334 | 81.6922 | 80.6893 | 75.9354 | 2.1557 | 2.1097 | 1.5406
14.8375 | 81.7037 | 80.6644 | 75.9449 | 2.1559 | 2.1099 | 1.5406
14.8417 | 81.7181 | 80.645 | 75.9536 | 2.1561 | 2.1101 | 1.5406
14.8459 | 81.7005 | 80.6498 | 75.9468 | 2.1563 | 2.11 | 1.5407
14.85 | 81.6721 | 80.6517 | 75.9411 | 2.1566 | 2.1099 | 1.5408
14.8542 | 81.6809 | 80.6603 | 75.9416 | 2.1566 | 2.1102 | 1.5407
14.8584 | 81.6892 | 80.6683 | 75.9418 | 2.1566 | 2.1105 | 1.5407
14.8625 | 81.6979 | 80.6469 | 75.9463 | 2.1569 | 2.1105 | 1.5408
14.8667 | 81.7075 | 80.6297 | 75.95 | 2.1572 | 2.1106 | 1.5409
14.8709 | 81.6919 | 80.6443 | 75.9414 | 2.1573 | 2.1106 | 1.5408
14.875 | 81.6667 | 80.6553 | 75.9334 | 2.1574 | 2.1107 | 1.5408
14.8792 | 81.6764 | 80.6418 | 75.9396 | 2.1576 | 2.1109 | 1.5408
14.8834 | 81.6874 | 80.6316 | 75.9458 | 2.1577 | 2.1112 | 1.5409
14.8875 | 81.6752 | 80.6301 | 75.942 | 2.158 | 2.1111 | 1.5409
14.8917 | 81.6665 | 80.6275 | 75.9381 | 2.1583 | 2.1111 | 1.541
14.8959 | 81.6647 | 80.6346 | 75.9373 | 2.1584 | 2.1113 | 1.541
14.9 | 81.6443 | 80.6429 | 75.9364 | 2.1585 | 2.1115 | 1.5409
14.9042 | 81.6547 | 80.6222 | 75.9383 | 2.1588 | 2.1116 | 1.541
14.9084 | 81.6617 | 80.6034 | 75.9405 | 2.1591 | 2.1117 | 1.5411
14.9125 | 81.645 | 80.6228 | 75.937 | 2.1593 | 2.1117 | 1.5411
14.9167 | 81.641 | 80.6368 | 75.9334 | 2.1596 | 2.1117 | 1.5411
14.9209 | 81.6475 | 80.6222 | 75.9377 | 2.1597 | 2.1121 | 1.5411
14.925 | 81.6504 | 80.6146 | 75.9416 | 2.1599 | 2.1123 | 1.5411
14.9292 | 81.6518 | 80.6039 | 75.936 | 2.1602 | 2.1123 | 1.5412
14.9334 | 81.6619 | 80.5902 | 75.9306 | 2.1604 | 2.1122 | 1.5412
14.9375 | 81.6599 | 80.6133 | 75.9338 | 2.1604 | 2.1124 | 1.5412
14.9417 | 81.664 | 80.6324 | 75.9368 | 2.1606 | 2.1126 | 1.5411
14.9459 | 81.6699 | 80.6074 | 75.9376 | 2.1607 | 2.1127 | 1.5412
14.95 | 81.6779 | 80.5907 | 75.9387 | 2.1608 | 2.1129 | 1.5413
14.9542 | 81.6643 | 80.6015 | 75.9325 | 2.1609 | 2.1128 | 1.5413
14.9584 | 81.6649 | 80.6054 | 75.9261 | 2.1611 | 2.1127 | 1.5412
14.9625 | 81.6695 | 80.6058 | 75.9333 | 2.1611 | 2.1131 | 1.5412
14.9667 | 81.6619 | 80.6082 | 75.9405 | 2.1612 | 2.1133 | 1.5412
14.9709 | 81.6592 | 80.5926 | 75.935 | 2.1614 | 2.1133 | 1.5413
14.975 | 81.6498 | 80.5766 | 75.9301 | 2.1616 | 2.1133 | 1.5414
14.9792 | 81.6426 | 80.6022 | 75.9303 | 2.1616 | 2.1133 | 1.5413
14.9834 | 81.6385 | 80.6217 | 75.9294 | 2.1618 | 2.1134 | 1.5413
14.9875 | 81.6438 | 80.5949 | 75.9339 | 2.162 | 2.1136 | 1.5413
14.9917 | 81.6359 | 80.5775 | 75.9387 | 2.1622 | 2.1139 | 1.5414
14.9959 | 81.6172 | 80.5844 | 75.9316 | 2.1625 | 2.1137 | 1.5414
15 | 81.6076 | 80.5818 | 75.9249 | 2.1627 | 2.1136 | 1.5414
15.0042 | 81.613 | 80.5944 | 75.9307 | 2.1628 | 2.1139 | 1.5414
15.0084 | 81.6193 | 80.6089 | 75.9351 | 2.163 | 2.1141 | 1.5414
15.0125 | 81.6258 | 80.5747 | 75.9328 | 2.1634 | 2.1141 | 1.5414
15.0167 | 81.6253 | 80.549 | 75.9317 | 2.1636 | 2.1142 | 1.5415
15.0209 | 81.6137 | 80.5818 | 75.9284 | 2.1638 | 2.1141 | 1.5415
15.025 | 81.6094 | 80.6 | 75.9252 | 2.1639 | 2.1141 | 1.5414
15.0292 | 81.6268 | 80.5855 | 75.9317 | 2.164 | 2.1145 | 1.5414
15.0334 | 81.6283 | 80.5832 | 75.9372 | 2.1642 | 2.1147 | 1.5415
15.0375 | 81.6202 | 80.5653 | 75.931 | 2.1645 | 2.1145 | 1.5415
15.0417 | 81.6133 | 80.5477 | 75.9258 | 2.1647 | 2.1145 | 1.5415
15.0459 | 81.605 | 80.581 | 75.9276 | 2.1647 | 2.1146 | 1.5415
15.05 | 81.6059 | 80.6036 | 75.9288 | 2.1649 | 2.1147 | 1.5415
15.0542 | 81.6163 | 80.5664 | 75.932 | 2.1651 | 2.1149 | 1.5415
15.0584 | 81.6163 | 80.5451 | 75.9351 | 2.1653 | 2.1152 | 1.5415
15.0625 | 81.5988 | 80.5575 | 75.9288 | 2.1656 | 2.1149 | 1.5415
15.0667 | 81.5931 | 80.5588 | 75.923 | 2.1657 | 2.1148 | 1.5415
15.0709 | 81.6014 | 80.5694 | 75.9274 | 2.1658 | 2.1152 | 1.5415
15.075 | 81.602 | 80.5803 | 75.9314 | 2.166 | 2.1155 | 1.5415
15.0792 | 81.6082 | 80.5457 | 75.9313 | 2.1662 | 2.1154 | 1.5416
15.0834 | 81.6086 | 80.5218 | 75.9316 | 2.1664 | 2.1155 | 1.5416
15.0875 | 81.5929 | 80.5539 | 75.9277 | 2.1665 | 2.1155 | 1.5416
15.0917 | 81.5956 | 80.5712 | 75.9233 | 2.1667 | 2.1155 | 1.5416
15.0959 | 81.6081 | 80.5502 | 75.9277 | 2.1668 | 2.1159 | 1.5416
15.1 | 81.6055 | 80.5403 | 75.9322 | 2.1669 | 2.1161 | 1.5416
15.1042 | 81.597 | 80.5325 | 75.9302 | 2.1672 | 2.1159 | 1.5416
15.1084 | 81.5967 | 80.5224 | 75.9285 | 2.1673 | 2.1158 | 1.5416
15.1125 | 81.5865 | 80.5486 | 75.9268 | 2.1674 | 2.1161 | 1.5416
15.1167 | 81.5861 | 80.5661 | 75.9243 | 2.1675 | 2.1163 | 1.5416
15.1209 | 81.5898 | 80.5229 | 75.9288 | 2.1678 | 2.1165 | 1.5416
15.125 | 81.573 | 80.4944 | 75.9339 | 2.168 | 2.1167 | 1.5416
15.1292 | 81.5675 | 80.5276 | 75.9294 | 2.1682 | 2.1165 | 1.5416
15.1334 | 81.5762 | 80.5474 | 75.9246 | 2.1683 | 2.1163 | 1.5417
15.1375 | 81.5844 | 80.5463 | 75.9245 | 2.1685 | 2.1168 | 1.5416
15.1417 | 81.5766 | 80.5499 | 75.9242 | 2.1688 | 2.1172 | 1.5416
15.1459 | 81.5607 | 80.5023 | 75.9296 | 2.1691 | 2.117 | 1.5416
15.15 | 81.5351 | 80.463 | 75.9362 | 2.1693 | 2.117 | 1.5416
15.1542 | 81.5173 | 80.5048 | 75.9329 | 2.1695 | 2.1171 | 1.5416
15.1584 | 81.5382 | 80.5288 | 75.9286 | 2.1698 | 2.1172 | 1.5416
15.1625 | 81.5816 | 80.5307 | 75.9253 | 2.1698 | 2.1174 | 1.5416
15.1667 | 81.6075 | 80.5471 | 75.9216 | 2.1699 | 2.1175 | 1.5416
15.1709 | 81.6014 | 80.5348 | 75.9232 | 2.1704 | 2.1174 | 1.5416
15.175 | 81.5889 | 80.5223 | 75.9256 | 2.1706 | 2.1174 | 1.5417
15.1792 | 81.5184 | 80.4923 | 75.9324 | 2.1708 | 2.1178 | 1.5416
15.1834 | 81.4693 | 80.4544 | 75.9397 | 2.1711 | 2.1181 | 1.5416
15.1875 | 81.4778 | 80.4491 | 75.9384 | 2.1714 | 2.1181 | 1.5416
15.1917 | 81.4835 | 80.453 | 75.937 | 2.1716 | 2.1181 | 1.5416
15.1959 | 81.5095 | 80.5268 | 75.9292 | 2.1721 | 2.1181 | 1.5416
15.2 | 81.5424 | 80.584 | 75.9206 | 2.1725 | 2.1181 | 1.5416
15.2042 | 81.5972 | 80.566 | 75.9213 | 2.1721 | 2.1183 | 1.5416
15.2084 | 81.5947 | 80.5611 | 75.9219 | 2.1723 | 2.1183 | 1.5416
15.2125 | 81.6315 | 80.4886 | 75.9308 | 2.1728 | 2.1183 | 1.5416
15.2167 | 81.5781 | 80.4276 | 75.9411 | 2.1731 | 2.1184 | 1.5416
15.2209 | 81.4898 | 80.4548 | 75.9427 | 2.1736 | 2.1185 | 1.5416
15.225 | 81.4264 | 80.4566 | 75.9447 | 2.1737 | 2.1185 | 1.5416
15.2292 | 81.4003 | 80.4902 | 75.94 | 2.1741 | 2.1187 | 1.5415
15.2334 | 81.3944 | 80.5302 | 75.9344 | 2.1745 | 2.1189 | 1.5415
15.2375 | 81.4464 | 80.5494 | 75.9336 | 2.1753 | 2.1186 | 1.5415
15.2417 | 81.4624 | 80.5652 | 75.933 | 2.1756 | 2.1184 | 1.5415
15.2459 | 81.533 | 80.5993 | 75.9285 | 2.1756 | 2.1182 | 1.5415
15.25 | 81.602 | 80.6328 | 75.9235 | 2.1754 | 2.1178 | 1.5415
15.2542 | 81.6898 | 80.5795 | 75.9292 | 2.1753 | 2.1179 | 1.5415
15.2584 | 81.7192 | 80.5477 | 75.9354 | 2.1758 | 2.1179 | 1.5414
15.2625 | 81.7219 | 80.5507 | 75.9389 | 2.1763 | 2.1174 | 1.5415
15.2667 | 81.6586 | 80.5349 | 75.9429 | 2.1766 | 2.117 | 1.5415
15.2709 | 81.5787 | 80.5725 | 75.9391 | 2.1767 | 2.1172 | 1.5414
15.275 | 81.5265 | 80.604 | 75.9347 | 2.1764 | 2.1173 | 1.5414
15.2792 | 81.5597 | 80.609 | 75.9366 | 2.1759 | 2.1168 | 1.5414
15.2834 | 81.5943 | 80.6167 | 75.9384 | 2.1755 | 2.1165 | 1.5414
15.2875 | 81.6961 | 80.6917 | 75.929 | 2.1755 | 2.1158 | 1.5414
15.2917 | 81.8048 | 80.7581 | 75.9183 | 2.1753 | 2.1152 | 1.5415
15.2959 | 81.8756 | 80.7218 | 75.9176 | 2.1751 | 2.1151 | 1.5415
15.3 | 81.8899 | 80.7194 | 75.917 | 2.1748 | 2.1149 | 1.5415
15.3042 | 81.9649 | 80.6715 | 75.9203 | 2.1743 | 2.1142 | 1.5416
15.3084 | 81.9686 | 80.6405 | 75.9239 | 2.1733 | 2.1135 | 1.5417
15.3125 | 81.9625 | 80.6245 | 75.9222 | 2.1727 | 2.1139 | 1.5417
15.3167 | 82.0043 | 80.6109 | 75.9203 | 2.1721 | 2.114 | 1.5416
15.3209 | 82.0123 | 80.5159 | 75.9271 | 2.171 | 2.1145 | 1.5416
15.325 | 81.9778 | 80.4314 | 75.9355 | 2.1703 | 2.1147 | 1.5416
15.3292 | 81.9546 | 80.4627 | 75.9336 | 2.1701 | 2.1149 | 1.5417
15.3334 | 81.9629 | 80.4618 | 75.9314 | 2.1692 | 2.115 | 1.5417
15.3375 | 81.8638 | 80.4836 | 75.9365 | 2.169 | 2.1159 | 1.5416
15.3417 | 81.833 | 80.4863 | 75.9415 | 2.1689 | 2.1166 | 1.5415
15.3459 | 81.8057 | 80.4845 | 75.9412 | 2.1686 | 2.1165 | 1.5415
15.35 | 81.7471 | 80.4761 | 75.9414 | 2.1687 | 2.1165 | 1.5416
15.3542 | 81.7165 | 80.5449 | 75.926 | 2.169 | 2.1166 | 1.5416
15.3584 | 81.6598 | 80.5954 | 75.9098 | 2.1689 | 2.1168 | 1.5416
15.3625 | 81.5974 | 80.5794 | 75.9208 | 2.1689 | 2.1167 | 1.5415
15.3667 | 81.5678 | 80.5792 | 75.932 | 2.1688 | 2.1168 | 1.5415
15.3709 | 81.5566 | 80.5987 | 75.9441 | 2.1687 | 2.1162 | 1.5415
15.375 | 81.5978 | 80.6283 | 75.9555 | 2.1691 | 2.1158 | 1.5415
15.3792 | 81.593 | 80.614 | 75.9366 | 2.1693 | 2.1161 | 1.5416
15.3834 | 81.5745 | 80.6066 | 75.9183 | 2.1695 | 2.1163 | 1.5416
15.3875 | 81.5621 | 80.5484 | 75.9079 | 2.1696 | 2.1161 | 1.5416
15.3917 | 81.57 | 80.5074 | 75.8984 | 2.1696 | 2.1158 | 1.5416
15.3959 | 81.5743 | 80.5537 | 75.9199 | 2.1697 | 2.1158 | 1.5416
15.4 | 81.5751 | 80.5887 | 75.9399 | 2.1701 | 2.1158 | 1.5416
15.4042 | 81.591 | 80.5751 | 75.9508 | 2.1701 | 2.1161 | 1.5416
15.4084 | 81.5716 | 80.5614 | 75.9626 | 2.1702 | 2.1163 | 1.5416
15.4125 | 81.6052 | 80.5375 | 75.9417 | 2.17 | 2.1161 | 1.5416
15.4167 | 81.6406 | 80.5184 | 75.9208 | 2.1701 | 2.116 | 1.5416
15.4209 | 81.6648 | 80.534 | 75.914 | 2.1703 | 2.1163 | 1.5416
15.425 | 81.6562 | 80.535 | 75.9067 | 2.1706 | 2.1165 | 1.5415
15.4292 | 81.6363 | 80.531 | 75.9159 | 2.1708 | 2.1165 | 1.5416
15.4334 | 81.5958 | 80.5284 | 75.926 | 2.1707 | 2.1165 | 1.5417
15.4375 | 81.5855 | 80.547 | 75.9259 | 2.1705 | 2.1165 | 1.5417
15.4417 | 81.5869 | 80.5655 | 75.925 | 2.1706 | 2.1166 | 1.5417
15.4459 | 81.5923 | 80.5597 | 75.9332 | 2.1707 | 2.1167 | 1.5416
15.45 | 81.5779 | 80.551 | 75.941 | 2.1709 | 2.1167 | 1.5416
15.4542 | 81.5625 | 80.5445 | 75.9358 | 2.1711 | 2.1166 | 1.5416
15.4584 | 81.5765 | 80.5484 | 75.9311 | 2.1709 | 2.1165 | 1.5417
15.4625 | 81.5729 | 80.5326 | 75.9125 | 2.171 | 2.1168 | 1.5417
15.4667 | 81.6016 | 80.5175 | 75.8946 | 2.1711 | 2.117 | 1.5418
15.4709 | 81.5889 | 80.5065 | 75.8984 | 2.1714 | 2.117 | 1.5418
15.475 | 81.5809 | 80.493 | 75.9023 | 2.1716 | 2.117 | 1.5419
15.4792 | 81.584 | 80.5108 | 75.9017 | 2.1713 | 2.1172 | 1.542
15.4834 | 81.6203 | 80.5313 | 75.9009 | 2.1712 | 2.1173 | 1.5422
15.4875 | 81.6804 | 80.5127 | 75.9018 | 2.1711 | 2.1175 | 1.5421
15.4917 | 81.6968 | 80.4924 | 75.9028 | 2.1713 | 2.1177 | 1.5421
15.4959 | 81.7086 | 80.4965 | 75.9046 | 2.1718 | 2.1177 | 1.5422
15.5 | 81.6877 | 80.5021 | 75.9058 | 2.1719 | 2.1176 | 1.5423
15.5042 | 81.6436 | 80.4944 | 75.8949 | 2.1719 | 2.118 | 1.5424
15.5084 | 81.6233 | 80.4907 | 75.8848 | 2.1718 | 2.1183 | 1.5424
15.5125 | 81.5899 | 80.4585 | 75.8783 | 2.1718 | 2.1185 | 1.5426
15.5167 | 81.5456 | 80.4275 | 75.8726 | 2.1721 | 2.1186 | 1.5427
15.5209 | 81.4899 | 80.4433 | 75.864 | 2.1723 | 2.1188 | 1.5429
15.525 | 81.475 | 80.4577 | 75.8549 | 2.1727 | 2.119 | 1.543
15.5292 | 81.4673 | 80.4538 | 75.8597 | 2.1727 | 2.1193 | 1.5431
15.5334 | 81.4754 | 80.4424 | 75.8651 | 2.1732 | 2.1197 | 1.5432
15.5375 | 81.4887 | 80.4449 | 75.8659 | 2.1738 | 2.1197 | 1.5433
15.5417 | 81.4931 | 80.4444 | 75.8664 | 2.1741 | 2.1197 | 1.5435
15.5459 | 81.4871 | 80.4645 | 75.868 | 2.1743 | 2.1199 | 1.5435
15.55 | 81.5149 | 80.4841 | 75.8689 | 2.1745 | 2.1201 | 1.5435
15.5542 | 81.555 | 80.4763 | 75.8783 | 2.1745 | 2.1201 | 1.5435
15.5584 | 81.5579 | 80.4656 | 75.8882 | 2.1748 | 2.1202 | 1.5436
15.5625 | 81.5712 | 80.4715 | 75.8814 | 2.175 | 2.1201 | 1.5436
15.5667 | 81.5578 | 80.4853 | 75.8748 | 2.1749 | 2.1201 | 1.5436
15.5709 | 81.5555 | 80.4803 | 75.8773 | 2.1748 | 2.1202 | 1.5436
15.575 | 81.5584 | 80.4778 | 75.8795 | 2.1748 | 2.1204 | 1.5436
15.5792 | 81.5603 | 80.4695 | 75.8782 | 2.175 | 2.1203 | 1.5436
15.5834 | 81.5433 | 80.4607 | 75.8769 | 2.1751 | 2.1202 | 1.5437
15.5875 | 81.5191 | 80.4537 | 75.8646 | 2.1753 | 2.1204 | 1.5438
15.5917 | 81.516 | 80.4551 | 75.8527 | 2.1753 | 2.1206 | 1.5438
15.5959 | 81.5129 | 80.4504 | 75.8594 | 2.1754 | 2.1206 | 1.5438
15.6 | 81.5145 | 80.4352 | 75.8662 | 2.1756 | 2.1207 | 1.5438
15.6042 | 81.5115 | 80.4511 | 75.8668 | 2.1759 | 2.1208 | 1.5439
15.6084 | 81.5056 | 80.4633 | 75.867 | 2.176 | 2.1208 | 1.544
15.6125 | 81.502 | 80.4477 | 75.8613 | 2.1761 | 2.121 | 1.544
15.6167 | 81.5028 | 80.4402 | 75.8557 | 2.1763 | 2.1212 | 1.544
15.6209 | 81.514 | 80.4469 | 75.8636 | 2.1765 | 2.1211 | 1.544
15.625 | 81.5031 | 80.4438 | 75.871 | 2.1767 | 2.121 | 1.5441
15.6292 | 81.502 | 80.4451 | 75.8628 | 2.1768 | 2.1213 | 1.5442
15.6334 | 81.5092 | 80.4542 | 75.8553 | 2.1769 | 2.1214 | 1.5442
15.6375 | 81.5154 | 80.435 | 75.8569 | 2.1769 | 2.1214 | 1.5442
15.6417 | 81.5156 | 80.417 | 75.859 | 2.1772 | 2.1215 | 1.5441
15.6459 | 81.5219 | 80.4451 | 75.8639 | 2.1773 | 2.1215 | 1.5442
15.65 | 81.5121 | 80.4617 | 75.8677 | 2.1773 | 2.1214 | 1.5443
15.6542 | 81.5053 | 80.44 | 75.8587 | 2.1774 | 2.1217 | 1.5443
15.6584 | 81.5146 | 80.4328 | 75.8503 | 2.1775 | 2.122 | 1.5443
15.6625 | 81.5061 | 80.4283 | 75.8576 | 2.1777 | 2.1217 | 1.5443
15.6667 | 81.4876 | 80.4166 | 75.8648 | 2.1779 | 2.1216 | 1.5443
15.6709 | 81.4866 | 80.4415 | 75.8604 | 2.1781 | 2.1219 | 1.5444
15.675 | 81.4911 | 80.4624 | 75.8562 | 2.178 | 2.122 | 1.5445
15.6792 | 81.4948 | 80.4255 | 75.855 | 2.1782 | 2.1221 | 1.5444
15.6834 | 81.5085 | 80.4032 | 75.8544 | 2.1784 | 2.1223 | 1.5444
15.6875 | 81.505 | 80.422 | 75.8571 | 2.1786 | 2.1221 | 1.5444
15.6917 | 81.4829 | 80.4266 | 75.8588 | 2.1787 | 2.122 | 1.5445
15.6959 | 81.4909 | 80.4292 | 75.8538 | 2.1787 | 2.1224 | 1.5445
15.7 | 81.5049 | 80.4372 | 75.8494 | 2.1787 | 2.1226 | 1.5445
15.7042 | 81.5053 | 80.4115 | 75.8554 | 2.1789 | 2.1225 | 1.5445
15.7084 | 81.505 | 80.3908 | 75.8617 | 2.1791 | 2.1225 | 1.5445
15.7125 | 81.4946 | 80.4233 | 75.8554 | 2.1792 | 2.1225 | 1.5446
15.7167 | 81.4826 | 80.4416 | 75.8481 | 2.1792 | 2.1225 | 1.5447
15.7209 | 81.487 | 80.4163 | 75.8503 | 2.1793 | 2.1228 | 1.5446
15.725 | 81.4995 | 80.4042 | 75.8535 | 2.1794 | 2.1231 | 1.5445
15.7292 | 81.4872 | 80.4027 | 75.8551 | 2.1797 | 2.1228 | 1.5446
15.7334 | 81.4702 | 80.3957 | 75.857 | 2.1799 | 2.1227 | 1.5447
15.7375 | 81.4727 | 80.4207 | 75.8513 | 2.1799 | 2.123 | 1.5447
15.7417 | 81.4806 | 80.4404 | 75.8446 | 2.1799 | 2.1231 | 1.5447
15.7459 | 81.4894 | 80.4022 | 75.8519 | 2.18 | 2.1232 | 1.5447
15.75 | 81.4958 | 80.3779 | 75.8596 | 2.1804 | 2.1234 | 1.5447
15.7542 | 81.4764 | 80.4 | 75.8521 | 2.1805 | 2.1232 | 1.5448
15.7584 | 81.458 | 80.4089 | 75.845 | 2.1805 | 2.1231 | 1.5448
15.7625 | 81.465 | 80.4108 | 75.8481 | 2.1806 | 2.1235 | 1.5447
15.7667 | 81.4851 | 80.4174 | 75.8507 | 2.1806 | 2.1237 | 1.5447
15.7709 | 81.4789 | 80.3877 | 75.8527 | 2.1809 | 2.1236 | 1.5448
15.775 | 81.4617 | 80.3656 | 75.8551 | 2.1813 | 2.1236 | 1.5449
15.7792 | 81.4527 | 80.3971 | 75.8467 | 2.1813 | 2.1237 | 1.5448
15.7834 | 81.4378 | 80.4157 | 75.8382 | 2.1813 | 2.1237 | 1.5448
15.7875 | 81.4526 | 80.3968 | 75.8481 | 2.1815 | 2.1239 | 1.5448
15.7917 | 81.4724 | 80.3881 | 75.8577 | 2.1818 | 2.1242 | 1.5448
15.7959 | 81.4545 | 80.3835 | 75.8515 | 2.182 | 2.124 | 1.5449
15.8 | 81.4333 | 80.3773 | 75.8455 | 2.1823 | 2.1239 | 1.545
15.8042 | 81.4394 | 80.394 | 75.8445 | 2.1822 | 2.1241 | 1.5449
15.8084 | 81.4507 | 80.4056 | 75.8428 | 2.1823 | 2.1243 | 1.5448
15.8125 | 81.4635 | 80.3784 | 75.8492 | 2.1825 | 2.1243 | 1.5449
15.8167 | 81.475 | 80.3591 | 75.8559 | 2.1828 | 2.1244 | 1.545
15.8209 | 81.4608 | 80.3819 | 75.8478 | 2.1828 | 2.1243 | 1.545
15.825 | 81.4468 | 80.3962 | 75.8399 | 2.1829 | 2.1243 | 1.545
15.8292 | 81.4585 | 80.3891 | 75.8452 | 2.1829 | 2.1246 | 1.5449
15.8334 | 81.4873 | 80.3878 | 75.8498 | 2.1829 | 2.1248 | 1.5449
15.8375 | 81.4767 | 80.3701 | 75.8483 | 2.1831 | 2.1247 | 1.545
15.8417 | 81.4744 | 80.3539 | 75.8477 | 2.1834 | 2.1246 | 1.545
15.8459 | 81.4562 | 80.3827 | 75.8449 | 2.1833 | 2.1247 | 1.545
15.85 | 81.4479 | 80.4017 | 75.842 | 2.1833 | 2.1248 | 1.545
15.8542 | 81.4569 | 80.3777 | 75.8464 | 2.1833 | 2.125 | 1.545
15.8584 | 81.471 | 80.3635 | 75.8504 | 2.1835 | 2.1251 | 1.545
15.8625 | 81.4557 | 80.3692 | 75.8457 | 2.1837 | 2.1249 | 1.545
15.8667 | 81.434 | 80.3695 | 75.8416 | 2.1839 | 2.1248 | 1.545
15.8709 | 81.428 | 80.382 | 75.8445 | 2.1839 | 2.1251 | 1.545
15.875 | 81.4245 | 80.3912 | 75.847 | 2.184 | 2.1253 | 1.545
15.8792 | 81.4286 | 80.3658 | 75.8467 | 2.1842 | 2.1252 | 1.5451
15.8834 | 81.4315 | 80.3482 | 75.8462 | 2.1845 | 2.1253 | 1.5451
15.8875 | 81.422 | 80.3674 | 75.8439 | 2.1847 | 2.1252 | 1.5451
15.8917 | 81.412 | 80.3793 | 75.8418 | 2.1848 | 2.1252 | 1.545
15.8959 | 81.422 | 80.3703 | 75.8447 | 2.1849 | 2.1255 | 1.5451
15.9 | 81.4327 | 80.3644 | 75.8477 | 2.1851 | 2.1256 | 1.5451
15.9042 | 81.4329 | 80.359 | 75.8452 | 2.1853 | 2.1255 | 1.5451
15.9084 | 81.4268 | 80.3545 | 75.8425 | 2.1855 | 2.1254 | 1.5451
15.9125 | 81.4288 | 80.3683 | 75.8438 | 2.1855 | 2.1256 | 1.5451
15.9167 | 81.4227 | 80.3798 | 75.8449 | 2.1856 | 2.1257 | 1.5451
15.9209 | 81.4304 | 80.3597 | 75.8444 | 2.1858 | 2.1258 | 1.5451
15.925 | 81.4343 | 80.3444 | 75.8445 | 2.1859 | 2.1258 | 1.5451
15.9292 | 81.4229 | 80.3582 | 75.8441 | 2.186 | 2.1257 | 1.5451
15.9334 | 81.417 | 80.3675 | 75.8432 | 2.1862 | 2.1257 | 1.5451
15.9375 | 81.4177 | 80.3609 | 75.8444 | 2.1862 | 2.1259 | 1.5451
15.9417 | 81.4207 | 80.3581 | 75.8456 | 2.1864 | 2.1261 | 1.5451
15.9459 | 81.4171 | 80.3476 | 75.843 | 2.1865 | 2.126 | 1.5451
15.95 | 81.413 | 80.3365 | 75.8411 | 2.1867 | 2.126 | 1.5451
15.9542 | 81.4101 | 80.3555 | 75.8439 | 2.1868 | 2.1261 | 1.5451
15.9584 | 81.4113 | 80.3707 | 75.8459 | 2.1869 | 2.1262 | 1.5451
15.9625 | 81.4147 | 80.3472 | 75.8444 | 2.187 | 2.1263 | 1.5452
15.9667 | 81.4218 | 80.3312 | 75.8432 | 2.1872 | 2.1265 | 1.5452
15.9709 | 81.4108 | 80.3394 | 75.8423 | 2.1873 | 2.1263 | 1.5452
15.975 | 81.4032 | 80.3408 | 75.8417 | 2.1875 | 2.1263 | 1.5451
15.9792 | 81.4132 | 80.3514 | 75.8441 | 2.1875 | 2.1265 | 1.5452
15.9834 | 81.4263 | 80.3638 | 75.8459 | 2.1875 | 2.1266 | 1.5452
15.9875 | 81.4155 | 80.3375 | 75.8428 | 2.1878 | 2.1267 | 1.5452
15.9917 | 81.4127 | 80.3154 | 75.8404 | 2.188 | 2.1267 | 1.5452
15.9959 | 81.3925 | 80.3308 | 75.8433 | 2.1881 | 2.1267 | 1.5452
16 | 81.3789 | 80.3378 | 75.8458 | 2.1881 | 2.1267 | 1.5451
16.0042 | 81.3943 | 80.3326 | 75.8459 | 2.1883 | 2.1269 | 1.5452
16.0084 | 81.4063 | 80.3341 | 75.8456 | 2.1884 | 2.1272 | 1.5452
16.0125 | 81.4154 | 80.3428 | 75.8398 | 2.1886 | 2.1269 | 1.5452
16.0167 | 81.4115 | 80.3492 | 75.8342 | 2.1887 | 2.1268 | 1.5452
16.0209 | 81.398 | 80.3416 | 75.8409 | 2.1889 | 2.1271 | 1.5452
16.025 | 81.3635 | 80.3332 | 75.8477 | 2.1891 | 2.1274 | 1.5451
16.0292 | 81.3442 | 80.2925 | 75.8502 | 2.1894 | 2.1274 | 1.5452
16.0334 | 81.3312 | 80.2573 | 75.8533 | 2.1896 | 2.1275 | 1.5452
16.0375 | 81.3534 | 80.3201 | 75.8444 | 2.1897 | 2.1273 | 1.5452
16.0417 | 81.3937 | 80.3709 | 75.8344 | 2.1898 | 2.1272 | 1.5452
16.0459 | 81.4239 | 80.3693 | 75.8367 | 2.1899 | 2.1275 | 1.5452
16.05 | 81.4288 | 80.3767 | 75.8389 | 2.1902 | 2.1278 | 1.5452
16.0542 | 81.4241 | 80.3212 | 75.8424 | 2.1903 | 2.1276 | 1.5452
16.0584 | 81.395 | 80.2721 | 75.847 | 2.1904 | 2.1275 | 1.5452
16.0625 | 81.3378 | 80.2792 | 75.8503 | 2.1907 | 2.1278 | 1.5452
16.0667 | 81.312 | 80.2738 | 75.8534 | 2.1911 | 2.128 | 1.5451
16.0709 | 81.2924 | 80.2958 | 75.8505 | 2.1912 | 2.128 | 1.5451
16.075 | 81.3088 | 80.3203 | 75.8473 | 2.1913 | 2.128 | 1.5452
16.0792 | 81.3282 | 80.3553 | 75.8404 | 2.1919 | 2.1279 | 1.5452
16.0834 | 81.3774 | 80.3871 | 75.8328 | 2.192 | 2.1279 | 1.5451
16.0875 | 81.3933 | 80.3554 | 75.8392 | 2.1921 | 2.128 | 1.5451
16.0917 | 81.4219 | 80.3309 | 75.8459 | 2.1922 | 2.1281 | 1.5451
16.0959 | 81.4236 | 80.2985 | 75.848 | 2.1923 | 2.128 | 1.5452
16.1 | 81.4269 | 80.2725 | 75.8511 | 2.1924 | 2.1279 | 1.5452
16.1042 | 81.3549 | 80.2942 | 75.852 | 2.193 | 2.1281 | 1.5451
16.1084 | 81.3004 | 80.298 | 75.8528 | 2.1933 | 2.1283 | 1.5451
16.1125 | 81.2546 | 80.3157 | 75.8521 | 2.1936 | 2.1283 | 1.5451
16.1167 | 81.2333 | 80.3353 | 75.8509 | 2.1938 | 2.1282 | 1.5451
16.1209 | 81.2352 | 80.3591 | 75.8463 | 2.1944 | 2.128 | 1.5451
16.125 | 81.2543 | 80.3825 | 75.8419 | 2.1949 | 2.128 | 1.5451
16.1292 | 81.2946 | 80.3947 | 75.8426 | 2.1952 | 2.1278 | 1.5451
16.1334 | 81.3502 | 80.4066 | 75.843 | 2.195 | 2.1275 | 1.5451
16.1375 | 81.4208 | 80.3794 | 75.8441 | 2.195 | 2.1274 | 1.5451
16.1417 | 81.5054 | 80.3685 | 75.8455 | 2.195 | 2.1273 | 1.5451
16.1459 | 81.5235 | 80.36 | 75.8481 | 2.1954 | 2.1272 | 1.5451
16.15 | 81.5056 | 80.3399 | 75.8515 | 2.196 | 2.127 | 1.5451
16.1542 | 81.4476 | 80.3667 | 75.8508 | 2.1962 | 2.127 | 1.5451
16.1584 | 81.4001 | 80.3878 | 75.8494 | 2.1959 | 2.1268 | 1.5451
16.1625 | 81.3598 | 80.3946 | 75.848 | 2.1956 | 2.1267 | 1.545
16.1667 | 81.408 | 80.4041 | 75.8468 | 2.1951 | 2.1267 | 1.545
16.1709 | 81.4391 | 80.4335 | 75.8428 | 2.1949 | 2.1262 | 1.5451
16.175 | 81.5097 | 80.4564 | 75.8386 | 2.1952 | 2.1257 | 1.5451
16.1792 | 81.552 | 80.4524 | 75.8371 | 2.1953 | 2.1257 | 1.5451
16.1834 | 81.5919 | 80.4726 | 75.8347 | 2.1952 | 2.1255 | 1.5451
16.1875 | 81.6389 | 80.4264 | 75.8396 | 2.195 | 2.1253 | 1.5451
16.1917 | 81.6903 | 80.3928 | 75.8452 | 2.1946 | 2.125 | 1.5452
16.1959 | 81.7353 | 80.3784 | 75.8408 | 2.1941 | 2.1251 | 1.5452
16.2 | 81.7545 | 80.3655 | 75.8363 | 2.1936 | 2.125 | 1.5452
16.2042 | 81.7646 | 80.3147 | 75.8381 | 2.193 | 2.1255 | 1.5452
16.2084 | 81.7411 | 80.2714 | 75.8405 | 2.1924 | 2.1259 | 1.5452
16.2125 | 81.7251 | 80.2852 | 75.8496 | 2.1918 | 2.1259 | 1.5452
16.2167 | 81.7329 | 80.2717 | 75.8588 | 2.1913 | 2.1259 | 1.5452
16.2209 | 81.704 | 80.3035 | 75.8581 | 2.1909 | 2.1265 | 1.5451
16.225 | 81.7102 | 80.3232 | 75.8567 | 2.1905 | 2.127 | 1.5451
16.2292 | 81.7078 | 80.3014 | 75.845 | 2.1902 | 2.127 | 1.5451
16.2334 | 81.6594 | 80.2753 | 75.8342 | 2.19 | 2.1272 | 1.5452
16.2375 | 81.6478 | 80.3394 | 75.8325 | 2.19 | 2.127 | 1.5451
16.2417 | 81.6031 | 80.3848 | 75.8297 | 2.19 | 2.1268 | 1.5451
16.2459 | 81.5711 | 80.3897 | 75.8504 | 2.1899 | 2.127 | 1.5451
16.25 | 81.5359 | 80.4125 | 75.8706 | 2.1898 | 2.1272 | 1.545
16.2542 | 81.5311 | 80.3897 | 75.8629 | 2.1897 | 2.1267 | 1.5451
16.2584 | 81.5195 | 80.3758 | 75.8561 | 2.1896 | 2.1263 | 1.5452
16.2625 | 81.513 | 80.3813 | 75.8328 | 2.1897 | 2.1265 | 1.5452
16.2667 | 81.4991 | 80.3905 | 75.8091 | 2.1899 | 2.1265 | 1.5451
16.2709 | 81.4644 | 80.3467 | 75.8251 | 2.1899 | 2.1265 | 1.5451
16.275 | 81.4399 | 80.3187 | 75.8415 | 2.1899 | 2.1265 | 1.5451
16.2792 | 81.412 | 80.3574 | 75.8531 | 2.1898 | 2.1263 | 1.5452
16.2834 | 81.3959 | 80.3827 | 75.8644 | 2.1899 | 2.126 | 1.5452
16.2875 | 81.3924 | 80.367 | 75.8561 | 2.19 | 2.1265 | 1.5452
16.2917 | 81.3821 | 80.3561 | 75.8476 | 2.19 | 2.1269 | 1.5451
16.2959 | 81.3871 | 80.3227 | 75.8462 | 2.1901 | 2.1266 | 1.5451
16.3 | 81.4154 | 80.2914 | 75.8452 | 2.19 | 2.1264 | 1.5451
16.3042 | 81.4352 | 80.342 | 75.8381 | 2.19 | 2.1266 | 1.5451
16.3084 | 81.4479 | 80.3744 | 75.8307 | 2.1902 | 2.1267 | 1.5452
16.3125 | 81.4482 | 80.3376 | 75.8306 | 2.1904 | 2.127 | 1.5452
16.3167 | 81.4338 | 80.3114 | 75.8313 | 2.1905 | 2.1272 | 1.5452
16.3209 | 81.4217 | 80.3334 | 75.8416 | 2.1904 | 2.1268 | 1.5452
16.325 | 81.4151 | 80.3489 | 75.8508 | 2.1903 | 2.1265 | 1.5452
16.3292 | 81.4277 | 80.3704 | 75.8498 | 2.1902 | 2.1269 | 1.5452
16.3334 | 81.4225 | 80.3892 | 75.8487 | 2.1903 | 2.1272 | 1.5452
16.3375 | 81.4312 | 80.3351 | 75.8436 | 2.1905 | 2.1271 | 1.5452
16.3417 | 81.4032 | 80.2987 | 75.8393 | 2.1906 | 2.127 | 1.5452
16.3459 | 81.3885 | 80.3287 | 75.8315 | 2.1907 | 2.1269 | 1.5453
16.35 | 81.3698 | 80.3478 | 75.823 | 2.1907 | 2.1269 | 1.5453
16.3542 | 81.3527 | 80.3306 | 75.8227 | 2.1909 | 2.1273 | 1.5454
16.3584 | 81.3542 | 80.3175 | 75.8233 | 2.1911 | 2.1276 | 1.5454
16.3625 | 81.3437 | 80.3028 | 75.8233 | 2.1914 | 2.1274 | 1.5455
16.3667 | 81.3526 | 80.2943 | 75.8229 | 2.1915 | 2.1272 | 1.5456
16.3709 | 81.3956 | 80.326 | 75.8226 | 2.1914 | 2.1275 | 1.5456
16.375 | 81.4242 | 80.3445 | 75.8215 | 2.1913 | 2.1277 | 1.5456
16.3792 | 81.472 | 80.3157 | 75.8275 | 2.1914 | 2.1278 | 1.5456
16.3834 | 81.4873 | 80.2964 | 75.8343 | 2.1916 | 2.1279 | 1.5457
16.3875 | 81.5034 | 80.2959 | 75.8215 | 2.1918 | 2.1279 | 1.5458
16.3917 | 81.4761 | 80.2979 | 75.8086 | 2.1919 | 2.1279 | 1.5459
16.3959 | 81.4699 | 80.2966 | 75.8071 | 2.1919 | 2.1282 | 1.5458
16.4 | 81.432 | 80.2897 | 75.8058 | 2.1919 | 2.1285 | 1.5458
16.4042 | 81.4104 | 80.2764 | 75.8057 | 2.192 | 2.1285 | 1.546
16.4084 | 81.3703 | 80.2683 | 75.8063 | 2.1921 | 2.1285 | 1.5462
16.4125 | 81.3612 | 80.2828 | 75.7997 | 2.1922 | 2.1287 | 1.5462
16.4167 | 81.3404 | 80.2897 | 75.7931 | 2.1923 | 2.1289 | 1.5462
16.4209 | 81.3233 | 80.2876 | 75.8022 | 2.1925 | 2.129 | 1.5463
16.425 | 81.3318 | 80.2814 | 75.8107 | 2.1928 | 2.1291 | 1.5463
16.4292 | 81.3279 | 80.2915 | 75.8099 | 2.193 | 2.1291 | 1.5464
16.4334 | 81.3463 | 80.3043 | 75.809 | 2.1931 | 2.1291 | 1.5464
16.4375 | 81.3629 | 80.3038 | 75.8093 | 2.1932 | 2.1292 | 1.5464
16.4417 | 81.3788 | 80.3005 | 75.8102 | 2.1933 | 2.1293 | 1.5464
16.4459 | 81.3834 | 80.3003 | 75.8156 | 2.1934 | 2.1292 | 1.5464
16.45 | 81.3844 | 80.3032 | 75.8207 | 2.1935 | 2.1291 | 1.5464
16.4542 | 81.3848 | 80.3082 | 75.8163 | 2.1934 | 2.1292 | 1.5464
16.4584 | 81.3868 | 80.3177 | 75.8118 | 2.1934 | 2.1293 | 1.5464
16.4625 | 81.3887 | 80.2951 | 75.8082 | 2.1935 | 2.1293 | 1.5464
16.4667 | 81.3824 | 80.2747 | 75.805 | 2.1936 | 2.1293 | 1.5464
16.4709 | 81.3644 | 80.2832 | 75.8039 | 2.1937 | 2.1293 | 1.5465
16.475 | 81.3519 | 80.2919 | 75.8027 | 2.1937 | 2.1292 | 1.5465
16.4792 | 81.353 | 80.2895 | 75.8013 | 2.1938 | 2.1295 | 1.5466
16.4834 | 81.3537 | 80.2832 | 75.8004 | 2.1938 | 2.1297 | 1.5466
16.4875 | 81.353 | 80.2784 | 75.8031 | 2.1941 | 2.1296 | 1.5466
16.4917 | 81.3448 | 80.2716 | 75.8054 | 2.1943 | 2.1295 | 1.5466
16.4959 | 81.3348 | 80.2861 | 75.8035 | 2.1943 | 2.1296 | 1.5467
16.5 | 81.3324 | 80.3011 | 75.8008 | 2.1944 | 2.1297 | 1.5467
16.5042 | 81.3421 | 80.2839 | 75.8019 | 2.1945 | 2.1298 | 1.5467
16.5084 | 81.3506 | 80.2666 | 75.8036 | 2.1947 | 2.1299 | 1.5467
16.5125 | 81.3419 | 80.2735 | 75.803 | 2.1949 | 2.1299 | 1.5467
16.5167 | 81.3396 | 80.2812 | 75.8025 | 2.195 | 2.1298 | 1.5468
16.5209 | 81.3448 | 80.2855 | 75.8005 | 2.195 | 2.1299 | 1.5468
16.525 | 81.3574 | 80.2891 | 75.7987 | 2.195 | 2.1301 | 1.5468
16.5292 | 81.3609 | 80.2772 | 75.8031 | 2.1951 | 2.1301 | 1.5468
16.5334 | 81.3618 | 80.2651 | 75.8073 | 2.1953 | 2.13 | 1.5468
16.5375 | 81.3418 | 80.2741 | 75.8007 | 2.1954 | 2.1301 | 1.5469
16.5417 | 81.3304 | 80.2853 | 75.7939 | 2.1954 | 2.1301 | 1.5469
16.5459 | 81.3403 | 80.2798 | 75.7987 | 2.1954 | 2.1302 | 1.5468
16.55 | 81.3436 | 80.2716 | 75.8041 | 2.1955 | 2.1303 | 1.5468
16.5542 | 81.3375 | 80.2718 | 75.8039 | 2.1957 | 2.1303 | 1.5469
16.5584 | 81.3357 | 80.2735 | 75.8036 | 2.1959 | 2.1302 | 1.547
16.5625 | 81.3302 | 80.2714 | 75.7962 | 2.1959 | 2.1303 | 1.5469
16.5667 | 81.3285 | 80.2727 | 75.7888 | 2.1959 | 2.1305 | 1.5469
16.5709 | 81.3424 | 80.2686 | 75.7987 | 2.1961 | 2.1305 | 1.5469
16.575 | 81.3431 | 80.2592 | 75.8087 | 2.1962 | 2.1305 | 1.5469
16.5792 | 81.3331 | 80.2653 | 75.8008 | 2.1963 | 2.1305 | 1.547
16.5834 | 81.3337 | 80.2752 | 75.7933 | 2.1964 | 2.1306 | 1.5471
16.5875 | 81.3418 | 80.2673 | 75.7951 | 2.1963 | 2.1306 | 1.547
16.5917 | 81.3403 | 80.2595 | 75.7963 | 2.1964 | 2.1308 | 1.5469
16.5959 | 81.3426 | 80.2637 | 75.8003 | 2.1966 | 2.1307 | 1.547
16.6 | 81.3334 | 80.2622 | 75.8045 | 2.1967 | 2.1307 | 1.5471
16.6042 | 81.3193 | 80.2606 | 75.7955 | 2.1967 | 2.1308 | 1.547
16.6084 | 81.3202 | 80.2655 | 75.7873 | 2.1968 | 2.1309 | 1.547
16.6125 | 81.3314 | 80.2615 | 75.7967 | 2.1968 | 2.1309 | 1.547
16.6167 | 81.3261 | 80.2533 | 75.8052 | 2.197 | 2.1309 | 1.547
16.6209 | 81.3264 | 80.2602 | 75.7993 | 2.1972 | 2.131 | 1.5471
16.625 | 81.3205 | 80.267 | 75.7936 | 2.1972 | 2.131 | 1.5472
16.6292 | 81.318 | 80.2547 | 75.7926 | 2.1972 | 2.1311 | 1.5471
16.6334 | 81.3227 | 80.2487 | 75.7923 | 2.1974 | 2.1312 | 1.547
16.6375 | 81.3273 | 80.2572 | 75.7985 | 2.1975 | 2.1311 | 1.5471
16.6417 | 81.3211 | 80.2567 | 75.8041 | 2.1976 | 2.1311 | 1.5471
16.6459 | 81.3154 | 80.2556 | 75.7956 | 2.1977 | 2.1313 | 1.5471
16.65 | 81.3147 | 80.2615 | 75.7874 | 2.1978 | 2.1314 | 1.5471
16.6542 | 81.3178 | 80.2454 | 75.793 | 2.1979 | 2.1314 | 1.5471
16.6584 | 81.3086 | 80.2311 | 75.7987 | 2.1981 | 2.1314 | 1.5471
16.6625 | 81.3104 | 80.2523 | 75.7967 | 2.1982 | 2.1314 | 1.5471
16.6667 | 81.3004 | 80.2634 | 75.7946 | 2.1983 | 2.1314 | 1.5472
16.6709 | 81.2968 | 80.2512 | 75.7932 | 2.1983 | 2.1316 | 1.5472
16.675 | 81.3068 | 80.251 | 75.7919 | 2.1985 | 2.1317 | 1.5471
16.6792 | 81.3025 | 80.2422 | 75.7952 | 2.1986 | 2.1316 | 1.5472
16.6834 | 81.2986 | 80.2292 | 75.7983 | 2.1989 | 2.1316 | 1.5472
16.6875 | 81.2964 | 80.2483 | 75.7935 | 2.1989 | 2.1317 | 1.5472
16.6917 | 81.3026 | 80.2612 | 75.7889 | 2.199 | 2.1317 | 1.5472
16.6959 | 81.3076 | 80.2414 | 75.7937 | 2.199 | 2.1318 | 1.5472
16.7 | 81.3123 | 80.2317 | 75.7986 | 2.1993 | 2.132 | 1.5472
16.7042 | 81.3106 | 80.2415 | 75.7952 | 2.1993 | 2.1318 | 1.5472
16.7084 | 81.3007 | 80.2428 | 75.7913 | 2.1994 | 2.1317 | 1.5473
16.7125 | 81.3092 | 80.2464 | 75.7914 | 2.1994 | 2.132 | 1.5472
16.7167 | 81.3216 | 80.2532 | 75.7917 | 2.1994 | 2.1321 | 1.5472
16.7209 | 81.3238 | 80.2347 | 75.7951 | 2.1995 | 2.132 | 1.5472
16.725 | 81.3168 | 80.2195 | 75.7987 | 2.1997 | 2.1321 | 1.5473
16.7292 | 81.306 | 80.2423 | 75.7929 | 2.1997 | 2.132 | 1.5473
16.7334 | 81.3018 | 80.2556 | 75.7865 | 2.1996 | 2.132 | 1.5472
16.7375 | 81.3099 | 80.2402 | 75.7916 | 2.1997 | 2.1322 | 1.5472
16.7417 | 81.3194 | 80.2344 | 75.797 | 2.1998 | 2.1324 | 1.5472
16.7459 | 81.3071 | 80.2328 | 75.7946 | 2.2 | 2.1322 | 1.5473
16.75 | 81.2866 | 80.2254 | 75.7926 | 2.2001 | 2.1321 | 1.5473
16.7542 | 81.2744 | 80.2443 | 75.7913 | 2.2001 | 2.1323 | 1.5473
16.7584 | 81.2811 | 80.2598 | 75.7892 | 2.2002 | 2.1323 | 1.5472
16.7625 | 81.2863 | 80.2306 | 75.7934 | 2.2003 | 2.1324 | 1.5473
16.7667 | 81.2922 | 80.2127 | 75.7979 | 2.2006 | 2.1325 | 1.5473
16.7709 | 81.2768 | 80.2313 | 75.7924 | 2.2008 | 2.1324 | 1.5473
16.775 | 81.2652 | 80.2378 | 75.7873 | 2.2008 | 2.1322 | 1.5473
16.7792 | 81.2712 | 80.2392 | 75.7915 | 2.2009 | 2.1325 | 1.5473
16.7834 | 81.2908 | 80.2457 | 75.7949 | 2.2009 | 2.1327 | 1.5472
16.7875 | 81.2966 | 80.223 | 75.7938 | 2.2012 | 2.1326 | 1.5473
16.7917 | 81.2874 | 80.2059 | 75.7933 | 2.2014 | 2.1325 | 1.5473
16.7959 | 81.2798 | 80.2345 | 75.7905 | 2.2014 | 2.1325 | 1.5473
16.8 | 81.2726 | 80.2514 | 75.7877 | 2.2014 | 2.1325 | 1.5473
16.8042 | 81.286 | 80.2318 | 75.7929 | 2.2014 | 2.1327 | 1.5473
16.8084 | 81.3014 | 80.2239 | 75.7975 | 2.2016 | 2.1329 | 1.5473
16.8125 | 81.295 | 80.2204 | 75.7929 | 2.2018 | 2.1327 | 1.5473
16.8167 | 81.2747 | 80.2137 | 75.7886 | 2.2019 | 2.1326 | 1.5473
16.8209 | 81.27 | 80.2326 | 75.7902 | 2.2019 | 2.1328 | 1.5473
16.825 | 81.2706 | 80.246 | 75.7917 | 2.2019 | 2.1329 | 1.5473
16.8292 | 81.2843 | 80.2217 | 75.7931 | 2.202 | 2.1329 | 1.5473
16.8334 | 81.2896 | 80.2079 | 75.7947 | 2.2022 | 2.133 | 1.5474
16.8375 | 81.2765 | 80.2204 | 75.7913 | 2.2024 | 2.1329 | 1.5473
16.8417 | 81.2555 | 80.224 | 75.7882 | 2.2025 | 2.1329 | 1.5473
16.8459 | 81.2603 | 80.2212 | 75.7917 | 2.2025 | 2.1331 | 1.5473
16.85 | 81.27 | 80.2215 | 75.795 | 2.2025 | 2.1332 | 1.5473
16.8542 | 81.2836 | 80.2135 | 75.7928 | 2.2027 | 2.1331 | 1.5473
16.8584 | 81.283 | 80.2086 | 75.7906 | 2.2029 | 2.1331 | 1.5474
16.8625 | 81.2784 | 80.2303 | 75.7893 | 2.2029 | 2.1331 | 1.5473
16.8667 | 81.2731 | 80.245 | 75.7877 | 2.2028 | 2.1331 | 1.5473
16.8709 | 81.2594 | 80.2086 | 75.7923 | 2.203 | 2.1334 | 1.5473
16.875 | 81.2543 | 80.1804 | 75.7975 | 2.2032 | 2.1336 | 1.5473
16.8792 | 81.2448 | 80.1926 | 75.7954 | 2.2033 | 2.1333 | 1.5473
16.8834 | 81.2446 | 80.1981 | 75.7932 | 2.2033 | 2.1332 | 1.5473
16.8875 | 81.2687 | 80.2342 | 75.789 | 2.2034 | 2.1334 | 1.5473
16.8917 | 81.2987 | 80.269 | 75.784 | 2.2034 | 2.1335 | 1.5473
16.8959 | 81.2932 | 80.2257 | 75.7873 | 2.2036 | 2.1335 | 1.5473
16.9 | 81.2789 | 80.192 | 75.7917 | 2.204 | 2.1336 | 1.5473
16.9042 | 81.2442 | 80.1873 | 75.7954 | 2.2041 | 2.1336 | 1.5473
16.9084 | 81.2107 | 80.1748 | 75.7991 | 2.2042 | 2.1335 | 1.5473
16.9125 | 81.2002 | 80.184 | 75.797 | 2.2044 | 2.1338 | 1.5473
16.9167 | 81.2168 | 80.1931 | 75.7946 | 2.2045 | 2.134 | 1.5473
16.9209 | 81.2382 | 80.2242 | 75.7887 | 2.2047 | 2.1337 | 1.5473
16.925 | 81.2692 | 80.2549 | 75.7824 | 2.2048 | 2.1335 | 1.5474
16.9292 | 81.2887 | 80.2449 | 75.7862 | 2.2049 | 2.1338 | 1.5473
16.9334 | 81.2873 | 80.2377 | 75.7897 | 2.2051 | 2.134 | 1.5473
16.9375 | 81.2889 | 80.1798 | 75.7943 | 2.2051 | 2.1339 | 1.5473
16.9417 | 81.2628 | 80.1295 | 75.8002 | 2.2052 | 2.1339 | 1.5474
16.9459 | 81.2212 | 80.1683 | 75.798 | 2.2055 | 2.1339 | 1.5473
16.95 | 81.1901 | 80.194 | 75.7954 | 2.2057 | 2.1339 | 1.5473
16.9542 | 81.1702 | 80.211 | 75.7946 | 2.2058 | 2.1342 | 1.5473
16.9584 | 81.1566 | 80.2274 | 75.7933 | 2.2061 | 2.1344 | 1.5473
16.9625 | 81.2054 | 80.2246 | 75.7894 | 2.2063 | 2.1341 | 1.5473
16.9667 | 81.2303 | 80.2288 | 75.7855 | 2.2065 | 2.1339 | 1.5473
16.9709 | 81.2313 | 80.2271 | 75.7894 | 2.2067 | 2.134 | 1.5473
16.975 | 81.2551 | 80.2236 | 75.7934 | 2.2069 | 2.1341 | 1.5473
16.9792 | 81.2623 | 80.1943 | 75.7957 | 2.2067 | 2.1341 | 1.5473
16.9834 | 81.271 | 80.1704 | 75.7984 | 2.2067 | 2.1341 | 1.5473
16.9875 | 81.2544 | 80.1851 | 75.7971 | 2.2071 | 2.1341 | 1.5473
16.9917 | 81.2257 | 80.1908 | 75.7958 | 2.2075 | 2.1342 | 1.5472
16.9959 | 81.1409 | 80.209 | 75.7976 | 2.2077 | 2.1342 | 1.5472
17 | 81.0937 | 80.221 | 75.7994 | 2.208 | 2.1342 | 1.5473
17.0042 | 81.094 | 80.2365 | 75.7939 | 2.2083 | 2.134 | 1.5473
17.0084 | 81.1101 | 80.2577 | 75.7883 | 2.2087 | 2.1339 | 1.5473
17.0125 | 81.1384 | 80.2624 | 75.7899 | 2.2093 | 2.1338 | 1.5473
17.0167 | 81.1748 | 80.2665 | 75.7915 | 2.2097 | 2.1337 | 1.5472
17.0209 | 81.221 | 80.2487 | 75.7925 | 2.2095 | 2.1335 | 1.5473
17.025 | 81.2636 | 80.2397 | 75.7937 | 2.2094 | 2.1334 | 1.5473
17.0292 | 81.3293 | 80.2364 | 75.7937 | 2.2094 | 2.1333 | 1.5473
17.0334 | 81.3432 | 80.2314 | 75.7938 | 2.2098 | 2.1333 | 1.5472
17.0375 | 81.3504 | 80.2398 | 75.7972 | 2.2102 | 2.1332 | 1.5472
17.0417 | 81.2902 | 80.2397 | 75.8005 | 2.2104 | 2.1331 | 1.5473
17.0459 | 81.2555 | 80.2493 | 75.7942 | 2.2103 | 2.133 | 1.5473
17.05 | 81.23 | 80.2623 | 75.7881 | 2.21 | 2.1329 | 1.5473
17.0542 | 81.234 | 80.2741 | 75.7884 | 2.2098 | 2.1328 | 1.5473
17.0584 | 81.2483 | 80.2833 | 75.7885 | 2.2098 | 2.1326 | 1.5472
17.0625 | 81.27 | 80.2883 | 75.7922 | 2.2099 | 2.1324 | 1.5473
17.0667 | 81.2948 | 80.3043 | 75.7953 | 2.2098 | 2.1322 | 1.5473
17.0709 | 81.3301 | 80.2697 | 75.7912 | 2.2096 | 2.1322 | 1.5473
17.075 | 81.3918 | 80.25 | 75.7876 | 2.2094 | 2.1323 | 1.5473
17.0792 | 81.4726 | 80.2258 | 75.7834 | 2.2093 | 2.1323 | 1.5474
17.0834 | 81.5074 | 80.2 | 75.7794 | 2.2095 | 2.1321 | 1.5474
17.0875 | 81.5011 | 80.1969 | 75.7884 | 2.2093 | 2.1325 | 1.5474
17.0917 | 81.5189 | 80.1942 | 75.7969 | 2.2091 | 2.1326 | 1.5473
17.0959 | 81.5064 | 80.1867 | 75.8062 | 2.2084 | 2.1328 | 1.5473
17.1 | 81.5529 | 80.1663 | 75.8163 | 2.208 | 2.1331 | 1.5473
17.1042 | 81.5646 | 80.1823 | 75.8007 | 2.2078 | 2.1332 | 1.5473
17.1084 | 81.5649 | 80.1853 | 75.7849 | 2.2075 | 2.1333 | 1.5473
17.1125 | 81.5293 | 80.1885 | 75.7785 | 2.2073 | 2.1335 | 1.5473
17.1167 | 81.5098 | 80.1876 | 75.7723 | 2.2068 | 2.1338 | 1.5473
17.1209 | 81.5082 | 80.2232 | 75.7909 | 2.2065 | 2.1335 | 1.5473
17.125 | 81.5097 | 80.2478 | 75.8092 | 2.2063 | 2.1333 | 1.5473
17.1292 | 81.5053 | 80.2651 | 75.8098 | 2.2064 | 2.1333 | 1.5473
17.1334 | 81.4744 | 80.294 | 75.8099 | 2.2063 | 2.1334 | 1.5473
17.1375 | 81.4717 | 80.2497 | 75.7937 | 2.2061 | 2.1332 | 1.5473
17.1417 | 81.4801 | 80.2175 | 75.7785 | 2.2058 | 2.1332 | 1.5473
17.1459 | 81.5111 | 80.2326 | 75.7787 | 2.2057 | 2.133 | 1.5473
17.15 | 81.5258 | 80.2471 | 75.7781 | 2.2058 | 2.1327 | 1.5473
17.1542 | 81.4934 | 80.2367 | 75.7875 | 2.2059 | 2.133 | 1.5473
17.1584 | 81.4631 | 80.237 | 75.7971 | 2.2059 | 2.1332 | 1.5473
17.1625 | 81.4375 | 80.2244 | 75.7977 | 2.2057 | 2.133 | 1.5473
17.1667 | 81.4189 | 80.2067 | 75.7985 | 2.2056 | 2.1328 | 1.5473
17.1709 | 81.4107 | 80.2255 | 75.799 | 2.2056 | 2.133 | 1.5473
17.175 | 81.3954 | 80.2421 | 75.7982 | 2.2057 | 2.1331 | 1.5473
17.1792 | 81.3813 | 80.2132 | 75.7954 | 2.2057 | 2.1332 | 1.5473
17.1834 | 81.3736 | 80.1872 | 75.794 | 2.2056 | 2.1333 | 1.5473
17.1875 | 81.3735 | 80.2071 | 75.7854 | 2.2055 | 2.1332 | 1.5473
17.1917 | 81.3814 | 80.2147 | 75.7767 | 2.2055 | 2.1331 | 1.5474
17.1959 | 81.3797 | 80.2165 | 75.7813 | 2.2056 | 2.1334 | 1.5474
17.2 | 81.377 | 80.2225 | 75.7853 | 2.2056 | 2.1336 | 1.5473
17.2042 | 81.352 | 80.2168 | 75.7931 | 2.2057 | 2.1334 | 1.5474
17.2084 | 81.3576 | 80.2092 | 75.8016 | 2.2056 | 2.1332 | 1.5474
17.2125 | 81.3526 | 80.2315 | 75.7949 | 2.2054 | 2.1333 | 1.5474
17.2167 | 81.3674 | 80.2525 | 75.7873 | 2.2054 | 2.1334 | 1.5474
17.2209 | 81.3874 | 80.2162 | 75.788 | 2.2054 | 2.1335 | 1.5474
17.225 | 81.3766 | 80.1918 | 75.7894 | 2.2056 | 2.1336 | 1.5473
17.2292 | 81.3546 | 80.2068 | 75.7866 | 2.2059 | 2.1334 | 1.5474
17.2334 | 81.3275 | 80.2139 | 75.7842 | 2.2059 | 2.1332 | 1.5475
17.2375 | 81.2813 | 80.2081 | 75.7752 | 2.2058 | 2.1336 | 1.5475
17.2417 | 81.2622 | 80.2086 | 75.7661 | 2.2058 | 2.1339 | 1.5475
17.2459 | 81.2306 | 80.1879 | 75.7749 | 2.2058 | 2.1338 | 1.5475
17.25 | 81.2191 | 80.1686 | 75.7837 | 2.2059 | 2.1337 | 1.5476
17.2542 | 81.2144 | 80.2083 | 75.7814 | 2.2062 | 2.1338 | 1.5476
17.2584 | 81.2287 | 80.2355 | 75.7785 | 2.2061 | 2.1338 | 1.5477
17.2625 | 81.2408 | 80.1992 | 75.7775 | 2.2062 | 2.1341 | 1.5477
17.2667 | 81.2748 | 80.1769 | 75.7769 | 2.2061 | 2.1343 | 1.5476
17.2709 | 81.2906 | 80.1804 | 75.7771 | 2.2063 | 2.134 | 1.5477
17.275 | 81.3201 | 80.1789 | 75.777 | 2.2064 | 2.1339 | 1.5478
17.2792 | 81.3175 | 80.197 | 75.7703 | 2.2064 | 2.1343 | 1.5478
17.2834 | 81.3207 | 80.211 | 75.7637 | 2.2065 | 2.1345 | 1.5478
17.2875 | 81.3243 | 80.1703 | 75.7656 | 2.2065 | 2.1345 | 1.5479
17.2917 | 81.3033 | 80.1404 | 75.7683 | 2.2066 | 2.1346 | 1.5479
17.2959 | 81.2934 | 80.1788 | 75.7665 | 2.2068 | 2.1345 | 1.548
17.3 | 81.2673 | 80.2019 | 75.7636 | 2.2067 | 2.1344 | 1.548
17.3042 | 81.242 | 80.1948 | 75.7662 | 2.2067 | 2.1348 | 1.548
17.3084 | 81.2306 | 80.1914 | 75.7689 | 2.2067 | 2.1351 | 1.548
17.3125 | 81.2313 | 80.1743 | 75.7696 | 2.2067 | 2.1348 | 1.5481
17.3167 | 81.2329 | 80.1619 | 75.7707 | 2.2068 | 2.1347 | 1.5482
17.3209 | 81.2346 | 80.2012 | 75.7714 | 2.207 | 2.1348 | 1.5481
17.325 | 81.2345 | 80.2282 | 75.7714 | 2.207 | 2.1348 | 1.5481
17.3292 | 81.2313 | 80.1984 | 75.776 | 2.207 | 2.1349 | 1.5481
17.3334 | 81.2429 | 80.1812 | 75.7812 | 2.207 | 2.135 | 1.5481
17.3375 | 81.2508 | 80.1867 | 75.7759 | 2.2071 | 2.1348 | 1.5481
17.3417 | 81.2534 | 80.1928 | 75.7702 | 2.2072 | 2.1346 | 1.5481
17.3459 | 81.2463 | 80.1985 | 75.7679 | 2.2073 | 2.1349 | 1.5481
17.35 | 81.2486 | 80.201 | 75.7656 | 2.2073 | 2.1351 | 1.5481
17.3542 | 81.238 | 80.175 | 75.7678 | 2.2073 | 2.135 | 1.5481
17.3584 | 81.2356 | 80.157 | 75.7707 | 2.2074 | 2.1349 | 1.5482
17.3625 | 81.2356 | 80.1812 | 75.766 | 2.2074 | 2.1349 | 1.5482
17.3667 | 81.2277 | 80.1956 | 75.7609 | 2.2074 | 2.135 | 1.5482
17.3709 | 81.226 | 80.1861 | 75.7648 | 2.2075 | 2.1351 | 1.5482
17.375 | 81.2224 | 80.1771 | 75.7684 | 2.2077 | 2.1353 | 1.5482
17.3792 | 81.218 | 80.1733 | 75.7691 | 2.2078 | 2.1351 | 1.5483
17.3834 | 81.2097 | 80.1736 | 75.7694 | 2.2079 | 2.135 | 1.5483
17.3875 | 81.2178 | 80.1842 | 75.7644 | 2.208 | 2.1352 | 1.5483
17.3917 | 81.2158 | 80.1886 | 75.7597 | 2.208 | 2.1353 | 1.5483
17.3959 | 81.2205 | 80.1774 | 75.7667 | 2.2082 | 2.1353 | 1.5483
17.4 | 81.2258 | 80.1705 | 75.7739 | 2.2083 | 2.1353 | 1.5483
17.4042 | 81.2243 | 80.1786 | 75.7685 | 2.2083 | 2.1353 | 1.5483
17.4084 | 81.2308 | 80.187 | 75.7629 | 2.2083 | 2.1353 | 1.5484
17.4125 | 81.2306 | 80.1802 | 75.7629 | 2.2084 | 2.1354 | 1.5483
17.4167 | 81.2299 | 80.1711 | 75.7628 | 2.2084 | 2.1355 | 1.5483
17.4209 | 81.2224 | 80.1726 | 75.7675 | 2.2085 | 2.1354 | 1.5483
17.425 | 81.2172 | 80.1766 | 75.7724 | 2.2086 | 2.1353 | 1.5484
17.4292 | 81.2189 | 80.1809 | 75.7656 | 2.2086 | 2.1355 | 1.5484
17.4334 | 81.2243 | 80.1839 | 75.7592 | 2.2086 | 2.1356 | 1.5484
17.4375 | 81.2223 | 80.1733 | 75.7641 | 2.2088 | 2.1356 | 1.5484
17.4417 | 81.216 | 80.1633 | 75.7685 | 2.2089 | 2.1355 | 1.5483
17.4459 | 81.2098 | 80.1709 | 75.7655 | 2.209 | 2.1355 | 1.5484
17.45 | 81.2088 | 80.1792 | 75.7627 | 2.209 | 2.1356 | 1.5485
17.4542 | 81.2138 | 80.1742 | 75.7627 | 2.209 | 2.1357 | 1.5484
17.4584 | 81.2258 | 80.1677 | 75.763 | 2.2091 | 2.1358 | 1.5484
17.4625 | 81.2207 | 80.1675 | 75.7661 | 2.2092 | 2.1357 | 1.5484
17.4667 | 81.2159 | 80.1683 | 75.7684 | 2.2093 | 2.1356 | 1.5485
17.4709 | 81.218 | 80.1719 | 75.7628 | 2.2093 | 2.1357 | 1.5485
17.475 | 81.2186 | 80.1751 | 75.7576 | 2.2093 | 2.1358 | 1.5484
17.4792 | 81.2187 | 80.1673 | 75.7631 | 2.2094 | 2.1358 | 1.5484
17.4834 | 81.2189 | 80.1579 | 75.7689 | 2.2095 | 2.1358 | 1.5484
17.4875 | 81.2061 | 80.1664 | 75.7651 | 2.2096 | 2.1358 | 1.5485
17.4917 | 81.2002 | 80.176 | 75.7609 | 2.2096 | 2.1358 | 1.5485
17.4959 | 81.2096 | 80.1698 | 75.7615 | 2.2096 | 2.1359 | 1.5485
17.5 | 81.2107 | 80.164 | 75.7622 | 2.2097 | 2.1361 | 1.5484
17.5042 | 81.2085 | 80.1608 | 75.7645 | 2.2099 | 2.136 | 1.5485
17.5084 | 81.2024 | 80.1569 | 75.767 | 2.21 | 2.1359 | 1.5485
17.5125 | 81.1958 | 80.1668 | 75.7618 | 2.21 | 2.136 | 1.5485
17.5167 | 81.2013 | 80.177 | 75.7567 | 2.21 | 2.1361 | 1.5485
17.5209 | 81.2082 | 80.1661 | 75.7632 | 2.2101 | 2.1361 | 1.5485
17.525 | 81.214 | 80.1557 | 75.7694 | 2.2102 | 2.1362 | 1.5485
17.5292 | 81.2021 | 80.1563 | 75.7634 | 2.2104 | 2.1361 | 1.5485
17.5334 | 81.1914 | 80.158 | 75.7577 | 2.2104 | 2.1361 | 1.5486
17.5375 | 81.1995 | 80.1626 | 75.7593 | 2.2104 | 2.1362 | 1.5485
17.5417 | 81.1971 | 80.1652 | 75.761 | 2.2105 | 2.1363 | 1.5484
17.5459 | 81.2038 | 80.1605 | 75.765 | 2.2106 | 2.1363 | 1.5485
17.55 | 81.194 | 80.1559 | 75.7688 | 2.2108 | 2.1363 | 1.5486
17.5542 | 81.1869 | 80.1574 | 75.7605 | 2.2109 | 2.1363 | 1.5486
17.5584 | 81.1813 | 80.1627 | 75.7525 | 2.2109 | 2.1363 | 1.5486
17.5625 | 81.1953 | 80.1593 | 75.7605 | 2.211 | 2.1364 | 1.5485
17.5667 | 81.2007 | 80.152 | 75.7683 | 2.2111 | 2.1365 | 1.5485
17.5709 | 81.1954 | 80.1548 | 75.7645 | 2.2113 | 2.1364 | 1.5486
17.575 | 81.1885 | 80.1572 | 75.7609 | 2.2114 | 2.1364 | 1.5486
17.5792 | 81.1892 | 80.1564 | 75.7587 | 2.2113 | 2.1365 | 1.5486
17.5834 | 81.1928 | 80.1597 | 75.7565 | 2.2113 | 2.1366 | 1.5485
17.5875 | 81.2038 | 80.1562 | 75.7627 | 2.2115 | 2.1365 | 1.5485
17.5917 | 81.2052 | 80.1482 | 75.7689 | 2.2116 | 2.1365 | 1.5486
17.5959 | 81.1986 | 80.1541 | 75.7617 | 2.2116 | 2.1366 | 1.5486
17.6 | 81.192 | 80.1613 | 75.755 | 2.2116 | 2.1366 | 1.5486
17.6042 | 81.1979 | 80.1548 | 75.7597 | 2.2116 | 2.1366 | 1.5486
17.6084 | 81.2033 | 80.1504 | 75.7639 | 2.2116 | 2.1367 | 1.5485
17.6125 | 81.2052 | 80.1525 | 75.7629 | 2.2117 | 2.1367 | 1.5486
17.6167 | 81.1994 | 80.1503 | 75.7621 | 2.2118 | 2.1366 | 1.5487
17.6209 | 81.1957 | 80.1534 | 75.7591 | 2.2118 | 2.1367 | 1.5486
17.625 | 81.1875 | 80.1596 | 75.7566 | 2.2118 | 2.1368 | 1.5486
17.6292 | 81.1886 | 80.1533 | 75.7619 | 2.2119 | 2.1368 | 1.5486
17.6334 | 81.1862 | 80.1455 | 75.7665 | 2.212 | 2.1368 | 1.5486
17.6375 | 81.1782 | 80.1515 | 75.7613 | 2.2121 | 2.1368 | 1.5486
17.6417 | 81.1719 | 80.1563 | 75.7564 | 2.2122 | 2.1367 | 1.5486
17.6459 | 81.172 | 80.1504 | 75.7591 | 2.2123 | 2.1368 | 1.5486
17.65 | 81.1721 | 80.1483 | 75.7622 | 2.2124 | 2.1369 | 1.5486
17.6542 | 81.1713 | 80.1495 | 75.7626 | 2.2126 | 2.1369 | 1.5486
17.6584 | 81.1739 | 80.1457 | 75.7627 | 2.2127 | 2.1368 | 1.5487
17.6625 | 81.1734 | 80.1492 | 75.7595 | 2.2127 | 2.1369 | 1.5486
17.6667 | 81.1729 | 80.1559 | 75.7566 | 2.2128 | 2.137 | 1.5486
17.6709 | 81.1825 | 80.1462 | 75.7604 | 2.2129 | 2.137 | 1.5486
17.675 | 81.1786 | 80.1378 | 75.7645 | 2.213 | 2.137 | 1.5486
17.6792 | 81.1747 | 80.15 | 75.7614 | 2.2131 | 2.137 | 1.5486
17.6834 | 81.177 | 80.1566 | 75.7579 | 2.2131 | 2.1369 | 1.5487
17.6875 | 81.1794 | 80.1465 | 75.7596 | 2.2131 | 2.1371 | 1.5486
17.6917 | 81.178 | 80.1444 | 75.7613 | 2.2132 | 2.1372 | 1.5486
17.6959 | 81.1824 | 80.1412 | 75.7615 | 2.2133 | 2.1371 | 1.5486
17.7 | 81.1738 | 80.134 | 75.7618 | 2.2134 | 2.137 | 1.5487
17.7042 | 81.1705 | 80.151 | 75.7596 | 2.2134 | 2.1371 | 1.5486
17.7084 | 81.1781 | 80.1651 | 75.7571 | 2.2135 | 2.1371 | 1.5486
17.7125 | 81.1826 | 80.144 | 75.7599 | 2.2135 | 2.1372 | 1.5486
17.7167 | 81.1798 | 80.1319 | 75.763 | 2.2136 | 2.1373 | 1.5486
17.7209 | 81.162 | 80.1331 | 75.7616 | 2.2138 | 2.1372 | 1.5486
17.725 | 81.1474 | 80.1252 | 75.7605 | 2.2139 | 2.1372 | 1.5486
17.7292 | 81.1573 | 80.1418 | 75.7607 | 2.2138 | 2.1373 | 1.5486
17.7334 | 81.1794 | 80.1606 | 75.7602 | 2.2137 | 2.1373 | 1.5486
17.7375 | 81.2 | 80.1505 | 75.7586 | 2.2139 | 2.1373 | 1.5486
17.7417 | 81.2057 | 80.1458 | 75.7572 | 2.2142 | 2.1374 | 1.5487
17.7459 | 81.1854 | 80.1411 | 75.7588 | 2.2143 | 2.1374 | 1.5486
17.75 | 81.1578 | 80.1284 | 75.7608 | 2.2144 | 2.1373 | 1.5486
17.7542 | 81.145 | 80.1171 | 75.7646 | 2.2144 | 2.1375 | 1.5486
17.7584 | 81.151 | 80.1123 | 75.768 | 2.2145 | 2.1376 | 1.5486
17.7625 | 81.1563 | 80.133 | 75.7615 | 2.2145 | 2.1375 | 1.5486
17.7667 | 81.1617 | 80.1482 | 75.7549 | 2.2147 | 2.1374 | 1.5487
17.7709 | 81.181 | 80.1705 | 75.754 | 2.2147 | 2.1374 | 1.5487
17.775 | 81.1908 | 80.1918 | 75.7528 | 2.2146 | 2.1374 | 1.5486
17.7792 | 81.1884 | 80.1308 | 75.7606 | 2.2149 | 2.1376 | 1.5486
17.7834 | 81.1711 | 80.0826 | 75.7691 | 2.2152 | 2.1379 | 1.5486
17.7875 | 81.136 | 80.0968 | 75.7662 | 2.2152 | 2.1376 | 1.5486
17.7917 | 81.1106 | 80.0975 | 75.7634 | 2.2153 | 2.1374 | 1.5487
17.7959 | 81.0957 | 80.1389 | 75.7608 | 2.2154 | 2.1377 | 1.5486
17.8 | 81.1228 | 80.1794 | 75.7572 | 2.2156 | 2.1379 | 1.5486
17.8042 | 81.145 | 80.1564 | 75.7573 | 2.2157 | 2.1378 | 1.5486
17.8084 | 81.161 | 80.1422 | 75.7575 | 2.2158 | 2.1377 | 1.5487
17.8125 | 81.1727 | 80.144 | 75.7576 | 2.2159 | 2.1377 | 1.5487
17.8167 | 81.1868 | 80.1415 | 75.7576 | 2.2158 | 2.1376 | 1.5486
17.8209 | 81.1768 | 80.1118 | 75.7632 | 2.216 | 2.1379 | 1.5486
17.825 | 81.1736 | 80.0881 | 75.7694 | 2.2162 | 2.1381 | 1.5486
17.8292 | 81.1412 | 80.1077 | 75.7656 | 2.2163 | 2.1379 | 1.5486
17.8334 | 81.1123 | 80.1188 | 75.7616 | 2.2164 | 2.1377 | 1.5487
17.8375 | 81.0929 | 80.1447 | 75.7604 | 2.2165 | 2.138 | 1.5486
17.8417 | 81.0867 | 80.1664 | 75.7587 | 2.2168 | 2.1381 | 1.5486
17.8459 | 81.1042 | 80.1444 | 75.7596 | 2.2169 | 2.138 | 1.5486
17.85 | 81.1195 | 80.1334 | 75.761 | 2.2171 | 2.1378 | 1.5487
17.8542 | 81.1224 | 80.1479 | 75.7592 | 2.2173 | 2.1378 | 1.5486
17.8584 | 81.1428 | 80.1574 | 75.7572 | 2.2174 | 2.1377 | 1.5486
17.8625 | 81.1639 | 80.1313 | 75.7621 | 2.2172 | 2.1379 | 1.5486
17.8667 | 81.1667 | 80.109 | 75.7672 | 2.2173 | 2.1381 | 1.5486
17.8709 | 81.1713 | 80.1127 | 75.7653 | 2.2176 | 2.1379 | 1.5486
17.875 | 81.1461 | 80.1137 | 75.7636 | 2.2178 | 2.1377 | 1.5486
17.8792 | 81.0751 | 80.1452 | 75.7635 | 2.2181 | 2.1379 | 1.5486
17.8834 | 81.0295 | 80.1659 | 75.763 | 2.2184 | 2.138 | 1.5485
17.8875 | 81.026 | 80.1575 | 75.7623 | 2.2185 | 2.1378 | 1.5486
17.8917 | 81.0272 | 80.1582 | 75.7615 | 2.2188 | 2.1377 | 1.5486
17.8959 | 81.0337 | 80.1694 | 75.7584 | 2.2195 | 2.1375 | 1.5486
17.9 | 81.0636 | 80.1804 | 75.7552 | 2.2199 | 2.1374 | 1.5486
17.9042 | 81.0547 | 80.1713 | 75.7596 | 2.2201 | 2.1374 | 1.5486
17.9084 | 81.0832 | 80.1645 | 75.7639 | 2.22 | 2.1374 | 1.5486
17.9125 | 81.1605 | 80.1539 | 75.7642 | 2.22 | 2.1372 | 1.5486
17.9167 | 81.2182 | 80.1493 | 75.7645 | 2.2199 | 2.1371 | 1.5486
17.9209 | 81.245 | 80.156 | 75.7625 | 2.2203 | 2.1372 | 1.5486
17.925 | 81.2592 | 80.1529 | 75.7606 | 2.2207 | 2.1372 | 1.5486
17.9292 | 81.2395 | 80.1564 | 75.7583 | 2.2207 | 2.1371 | 1.5486
17.9334 | 81.198 | 80.1616 | 75.7558 | 2.2207 | 2.137 | 1.5486
17.9375 | 81.1855 | 80.1769 | 75.7612 | 2.2207 | 2.1369 | 1.5486
17.9417 | 81.1693 | 80.1935 | 75.7662 | 2.2205 | 2.1368 | 1.5485
17.9459 | 81.1497 | 80.1885 | 75.7664 | 2.2206 | 2.1368 | 1.5486
17.95 | 81.1332 | 80.1865 | 75.7669 | 2.2208 | 2.1367 | 1.5486
17.9542 | 81.1523 | 80.1608 | 75.7538 | 2.2204 | 2.1367 | 1.5487
17.9584 | 81.1347 | 80.1493 | 75.7409 | 2.2204 | 2.1366 | 1.5487
17.9625 | 81.1968 | 80.1402 | 75.7487 | 2.2204 | 2.1367 | 1.5487
17.9667 | 81.2054 | 80.127 | 75.7565 | 2.2203 | 2.1368 | 1.5486
17.9709 | 81.2343 | 80.1324 | 75.7702 | 2.2205 | 2.1369 | 1.5486
17.975 | 81.2667 | 80.1349 | 75.7837 | 2.2205 | 2.1369 | 1.5486
17.9792 | 81.2913 | 80.1191 | 75.7733 | 2.2202 | 2.1371 | 1.5486
17.9834 | 81.3297 | 80.1016 | 75.7634 | 2.2202 | 2.1374 | 1.5486
17.9875 | 81.3799 | 80.1054 | 75.7529 | 2.2202 | 2.1374 | 1.5486
17.9917 | 81.3949 | 80.0934 | 75.7426 | 2.22 | 2.1375 | 1.5486
17.9959 | 81.3727 | 80.1239 | 75.7527 | 2.2201 | 2.1375 | 1.5486
18 | 81.3803 | 80.1506 | 75.7622 | 2.2198 | 2.1376 | 1.5486
18.0042 | 81.373 | 80.1585 | 75.7703 | 2.2195 | 2.1375 | 1.5486
18.0084 | 81.3574 | 80.1651 | 75.7789 | 2.2194 | 2.1376 | 1.5486
18.0125 | 81.3703 | 80.1695 | 75.7694 | 2.2195 | 2.1374 | 1.5486
18.0167 | 81.3549 | 80.1778 | 75.7596 | 2.2194 | 2.1373 | 1.5486
18.0209 | 81.3441 | 80.1612 | 75.7558 | 2.2192 | 2.1373 | 1.5486
18.025 | 81.3578 | 80.1572 | 75.7521 | 2.219 | 2.1373 | 1.5486
18.0292 | 81.3908 | 80.1537 | 75.7549 | 2.2188 | 2.1372 | 1.5486
18.0334 | 81.4011 | 80.1495 | 75.7583 | 2.2187 | 2.137 | 1.5487
18.0375 | 81.3934 | 80.1532 | 75.7576 | 2.2188 | 2.1371 | 1.5487
18.0417 | 81.3807 | 80.162 | 75.7565 | 2.2186 | 2.1372 | 1.5487
18.0459 | 81.3626 | 80.1431 | 75.7624 | 2.2184 | 2.1372 | 1.5486
18.05 | 81.3634 | 80.1256 | 75.7685 | 2.2182 | 2.1372 | 1.5486
18.0542 | 81.3757 | 80.1431 | 75.7694 | 2.2182 | 2.1372 | 1.5486
18.0584 | 81.3732 | 80.1533 | 75.7702 | 2.2182 | 2.137 | 1.5486
18.0625 | 81.3562 | 80.1388 | 75.7603 | 2.2182 | 2.1373 | 1.5486
18.0667 | 81.3436 | 80.1286 | 75.7508 | 2.2182 | 2.1376 | 1.5486
18.0709 | 81.3536 | 80.1259 | 75.7529 | 2.218 | 2.1374 | 1.5486
18.075 | 81.3472 | 80.1155 | 75.7552 | 2.2179 | 2.1372 | 1.5486
18.0792 | 81.3578 | 80.143 | 75.7578 | 2.2181 | 2.1374 | 1.5487
18.0834 | 81.3426 | 80.1676 | 75.7598 | 2.2181 | 2.1375 | 1.5487
18.0875 | 81.3175 | 80.1421 | 75.7581 | 2.2182 | 2.1375 | 1.5487
18.0917 | 81.3095 | 80.1236 | 75.7569 | 2.2181 | 2.1376 | 1.5487
18.0959 | 81.3095 | 80.1415 | 75.7612 | 2.2178 | 2.1374 | 1.5487
18.1 | 81.3291 | 80.1532 | 75.7647 | 2.2177 | 2.1372 | 1.5487
18.1042 | 81.3705 | 80.1492 | 75.7606 | 2.2176 | 2.1375 | 1.5487
18.1084 | 81.3888 | 80.1522 | 75.757 | 2.2177 | 2.1377 | 1.5487
18.1125 | 81.3912 | 80.1262 | 75.7535 | 2.2177 | 2.1376 | 1.5487
18.1167 | 81.3827 | 80.1037 | 75.7507 | 2.2177 | 2.1375 | 1.5487
18.1209 | 81.3457 | 80.1285 | 75.7492 | 2.2176 | 2.1375 | 1.5488
18.125 | 81.3339 | 80.1481 | 75.7467 | 2.2176 | 2.1376 | 1.5488
18.1292 | 81.3174 | 80.1301 | 75.7495 | 2.2175 | 2.1378 | 1.5488
18.1334 | 81.2927 | 80.1164 | 75.7531 | 2.2176 | 2.1379 | 1.5488
18.1375 | 81.2756 | 80.122 | 75.7525 | 2.2177 | 2.1378 | 1.5489
18.1417 | 81.2355 | 80.1228 | 75.7517 | 2.2177 | 2.1376 | 1.5489
18.1459 | 81.2162 | 80.131 | 75.7507 | 2.2176 | 2.1379 | 1.5489
18.15 | 81.2041 | 80.141 | 75.7489 | 2.2174 | 2.138 | 1.5489
18.1542 | 81.2062 | 80.1195 | 75.7509 | 2.2173 | 2.138 | 1.5489
18.1584 | 81.2227 | 80.1007 | 75.7538 | 2.2173 | 2.138 | 1.5489
18.1625 | 81.2269 | 80.1177 | 75.7468 | 2.2174 | 2.138 | 1.549
18.1667 | 81.2379 | 80.1306 | 75.7395 | 2.2175 | 2.138 | 1.549
18.1709 | 81.2423 | 80.1181 | 75.7433 | 2.2174 | 2.1382 | 1.549
18.175 | 81.2502 | 80.1094 | 75.747 | 2.2174 | 2.1384 | 1.549
18.1792 | 81.2578 | 80.1145 | 75.7471 | 2.2174 | 2.1382 | 1.5491
18.1834 | 81.253 | 80.1139 | 75.7471 | 2.2176 | 2.1381 | 1.5491
18.1875 | 81.2424 | 80.1234 | 75.7433 | 2.2176 | 2.1383 | 1.5491
18.1917 | 81.2297 | 80.1341 | 75.7391 | 2.2176 | 2.1385 | 1.5491
18.1959 | 81.2226 | 80.1167 | 75.745 | 2.2175 | 2.1384 | 1.5491
18.2 | 81.2182 | 80.1012 | 75.7514 | 2.2175 | 2.1384 | 1.5491
18.2042 | 81.2181 | 80.1287 | 75.7511 | 2.2175 | 2.1383 | 1.5491
18.2084 | 81.2078 | 80.1485 | 75.7504 | 2.2176 | 2.1382 | 1.5492
18.2125 | 81.2021 | 80.1316 | 75.7497 | 2.2176 | 2.1384 | 1.5491
18.2167 | 81.1966 | 80.1249 | 75.7491 | 2.2175 | 2.1386 | 1.5491
18.2209 | 81.2002 | 80.119 | 75.7502 | 2.2175 | 2.1383 | 1.5491
18.225 | 81.2001 | 80.1123 | 75.7512 | 2.2175 | 2.1382 | 1.5491
18.2292 | 81.2002 | 80.1288 | 75.7471 | 2.2176 | 2.1384 | 1.5491
18.2334 | 81.1952 | 80.143 | 75.7427 | 2.2176 | 2.1385 | 1.5492
18.2375 | 81.1854 | 80.1122 | 75.7432 | 2.2176 | 2.1385 | 1.5491
18.2417 | 81.1826 | 80.0892 | 75.7447 | 2.2176 | 2.1386 | 1.5491
18.2459 | 81.1775 | 80.1153 | 75.7457 | 2.2176 | 2.1384 | 1.5492
18.25 | 81.1754 | 80.1301 | 75.7462 | 2.2177 | 2.1383 | 1.5492
18.2542 | 81.1647 | 80.1245 | 75.7438 | 2.2177 | 2.1386 | 1.5492
18.2584 | 81.1597 | 80.123 | 75.7412 | 2.2178 | 2.1388 | 1.5492
18.2625 | 81.1443 | 80.1049 | 75.7442 | 2.2178 | 2.1386 | 1.5492
18.2667 | 81.1332 | 80.0897 | 75.7476 | 2.2178 | 2.1385 | 1.5492
18.2709 | 81.1337 | 80.1229 | 75.7457 | 2.2178 | 2.1385 | 1.5492
18.275 | 81.1328 | 80.146 | 75.7437 | 2.2178 | 2.1386 | 1.5493
18.2792 | 81.1337 | 80.1181 | 75.7444 | 2.2179 | 2.1387 | 1.5492
18.2834 | 81.1407 | 80.1013 | 75.7454 | 2.218 | 2.1389 | 1.5492
18.2875 | 81.1334 | 80.1075 | 75.7458 | 2.218 | 2.1386 | 1.5492
18.2917 | 81.1264 | 80.11 | 75.7458 | 2.2181 | 2.1385 | 1.5493
18.2959 | 81.1331 | 80.1242 | 75.743 | 2.2181 | 2.1387 | 1.5493
18.3 | 81.136 | 80.1342 | 75.7404 | 2.2181 | 2.1389 | 1.5493
18.3042 | 81.1316 | 80.1089 | 75.7454 | 2.2182 | 2.1388 | 1.5492
18.3084 | 81.1344 | 80.0928 | 75.7508 | 2.2183 | 2.1388 | 1.5492
18.3125 | 81.1322 | 80.1148 | 75.7455 | 2.2183 | 2.1387 | 1.5493
18.3167 | 81.1236 | 80.1287 | 75.7395 | 2.2183 | 2.1387 | 1.5493
18.3209 | 81.1311 | 80.1178 | 75.7411 | 2.2184 | 2.1389 | 1.5493
18.325 | 81.133 | 80.1099 | 75.7432 | 2.2185 | 2.139 | 1.5492
18.3292 | 81.1244 | 80.1033 | 75.746 | 2.2186 | 2.1388 | 1.5493
18.3334 | 81.1208 | 80.0997 | 75.7489 | 2.2186 | 2.1387 | 1.5493
18.3375 | 81.1262 | 80.1176 | 75.7427 | 2.2186 | 2.1388 | 1.5493
18.3417 | 81.1267 | 80.129 | 75.736 | 2.2186 | 2.1389 | 1.5493
18.3459 | 81.1326 | 80.1086 | 75.7428 | 2.2187 | 2.139 | 1.5493
18.35 | 81.1351 | 80.0948 | 75.7498 | 2.2188 | 2.139 | 1.5493
18.3542 | 81.1291 | 80.1051 | 75.7449 | 2.2188 | 2.1389 | 1.5493
18.3584 | 81.1235 | 80.1123 | 75.7404 | 2.2189 | 2.1389 | 1.5494
18.3625 | 81.1274 | 80.1163 | 75.7409 | 2.2189 | 2.139 | 1.5493
18.3667 | 81.1329 | 80.1176 | 75.741 | 2.2189 | 2.1391 | 1.5493
18.3709 | 81.1271 | 80.1035 | 75.7454 | 2.219 | 2.1391 | 1.5493
18.375 | 81.1219 | 80.0957 | 75.7496 | 2.2191 | 2.139 | 1.5494
18.3792 | 81.1217 | 80.1075 | 75.7419 | 2.2191 | 2.139 | 1.5494
18.3834 | 81.113 | 80.1144 | 75.7344 | 2.2191 | 2.1391 | 1.5494
18.3875 | 81.1207 | 80.1098 | 75.7417 | 2.2192 | 2.1391 | 1.5493
18.3917 | 81.1214 | 80.1053 | 75.7488 | 2.2193 | 2.1392 | 1.5493
18.3959 | 81.1154 | 80.1044 | 75.7457 | 2.2194 | 2.1391 | 1.5494
18.4 | 81.1134 | 80.1071 | 75.7424 | 2.2194 | 2.1391 | 1.5494
18.4042 | 81.1144 | 80.1082 | 75.7399 | 2.2194 | 2.1392 | 1.5494
18.4084 | 81.118 | 80.1065 | 75.7376 | 2.2195 | 2.1393 | 1.5493
18.4125 | 81.1193 | 80.1014 | 75.7434 | 2.2196 | 2.1392 | 1.5493
18.4167 | 81.1141 | 80.0968 | 75.7493 | 2.2197 | 2.1392 | 1.5494
18.4209 | 81.1101 | 80.1047 | 75.7429 | 2.2197 | 2.1392 | 1.5494
18.425 | 81.1062 | 80.1128 | 75.7366 | 2.2197 | 2.1392 | 1.5494
18.4292 | 81.1097 | 80.1058 | 75.7408 | 2.2198 | 2.1393 | 1.5494
18.4334 | 81.1106 | 80.0994 | 75.7447 | 2.2199 | 2.1394 | 1.5493
18.4375 | 81.1086 | 80.0996 | 75.7435 | 2.22 | 2.1393 | 1.5494
18.4417 | 81.1053 | 80.1002 | 75.7425 | 2.2201 | 2.1393 | 1.5494
18.4459 | 81.1045 | 80.1051 | 75.7409 | 2.2201 | 2.1393 | 1.5494
18.45 | 81.1107 | 80.1081 | 75.7393 | 2.2201 | 2.1394 | 1.5493
18.4542 | 81.111 | 80.1002 | 75.743 | 2.2202 | 2.1394 | 1.5494
18.4584 | 81.1111 | 80.0941 | 75.7463 | 2.2203 | 2.1394 | 1.5494
18.4625 | 81.1098 | 80.1001 | 75.7415 | 2.2204 | 2.1394 | 1.5494
18.4667 | 81.1108 | 80.1058 | 75.737 | 2.2204 | 2.1394 | 1.5494
18.4709 | 81.1166 | 80.1042 | 75.7413 | 2.2204 | 2.1395 | 1.5494
18.475 | 81.1177 | 80.1008 | 75.7457 | 2.2205 | 2.1395 | 1.5494
18.4792 | 81.114 | 80.0978 | 75.7436 | 2.2205 | 2.1395 | 1.5494
18.4834 | 81.1111 | 80.0971 | 75.7411 | 2.2206 | 2.1394 | 1.5495
18.4875 | 81.1114 | 80.1012 | 75.7398 | 2.2205 | 2.1395 | 1.5494
18.4917 | 81.1175 | 80.1047 | 75.7387 | 2.2205 | 2.1395 | 1.5494
18.4959 | 81.1237 | 80.1 | 75.7428 | 2.2206 | 2.1396 | 1.5494
18.5 | 81.1221 | 80.0936 | 75.7471 | 2.2207 | 2.1396 | 1.5494
18.5042 | 81.1149 | 80.0982 | 75.7418 | 2.2208 | 2.1395 | 1.5494
18.5084 | 81.1072 | 80.1041 | 75.7363 | 2.2208 | 2.1395 | 1.5494
18.5125 | 81.1079 | 80.1015 | 75.7404 | 2.2208 | 2.1396 | 1.5494
18.5167 | 81.1074 | 80.0986 | 75.7445 | 2.2208 | 2.1397 | 1.5494
18.5209 | 81.1035 | 80.0965 | 75.7432 | 2.2209 | 2.1396 | 1.5494
18.525 | 81.0946 | 80.0935 | 75.7423 | 2.2211 | 2.1396 | 1.5495
18.5292 | 81.0869 | 80.0994 | 75.7401 | 2.2211 | 2.1396 | 1.5494
18.5334 | 81.0881 | 80.1062 | 75.7377 | 2.2211 | 2.1396 | 1.5494
18.5375 | 81.0922 | 80.0971 | 75.7425 | 2.2212 | 2.1397 | 1.5494
18.5417 | 81.1 | 80.0878 | 75.7471 | 2.2213 | 2.1397 | 1.5494
18.5459 | 81.0961 | 80.0937 | 75.7416 | 2.2214 | 2.1397 | 1.5494
18.55 | 81.0917 | 80.099 | 75.7366 | 2.2215 | 2.1396 | 1.5495
18.5542 | 81.0937 | 80.1009 | 75.7399 | 2.2215 | 2.1397 | 1.5494
18.5584 | 81.1031 | 80.1037 | 75.7429 | 2.2215 | 2.1398 | 1.5494
18.5625 | 81.1048 | 80.0943 | 75.7433 | 2.2216 | 2.1398 | 1.5494
18.5667 | 81.1078 | 80.0852 | 75.7437 | 2.2218 | 2.1397 | 1.5495
18.5709 | 81.0954 | 80.0902 | 75.7406 | 2.2218 | 2.1398 | 1.5494
18.575 | 81.0856 | 80.0951 | 75.7378 | 2.2218 | 2.1398 | 1.5494
18.5792 | 81.0992 | 80.0994 | 75.7416 | 2.2218 | 2.1398 | 1.5494
18.5834 | 81.1149 | 80.1032 | 75.7449 | 2.2217 | 2.1398 | 1.5494
18.5875 | 81.1165 | 80.0997 | 75.7408 | 2.2219 | 2.1398 | 1.5494
18.5917 | 81.1161 | 80.0971 | 75.7372 | 2.2221 | 2.1398 | 1.5495
18.5959 | 81.0943 | 80.086 | 75.7406 | 2.2222 | 2.1399 | 1.5494
18.6 | 81.0719 | 80.0759 | 75.7444 | 2.2222 | 2.1399 | 1.5494
18.6042 | 81.0736 | 80.0825 | 75.7451 | 2.2223 | 2.1399 | 1.5494
18.6084 | 81.0836 | 80.0856 | 75.7451 | 2.2223 | 2.1399 | 1.5495
18.6125 | 81.0939 | 80.1036 | 75.7389 | 2.2224 | 2.1399 | 1.5494
18.6167 | 81.1011 | 80.1227 | 75.7326 | 2.2224 | 2.1398 | 1.5494
18.6209 | 81.1141 | 80.1052 | 75.7378 | 2.2224 | 2.1399 | 1.5494
18.625 | 81.1086 | 80.0916 | 75.7432 | 2.2225 | 2.14 | 1.5494
18.6292 | 81.1019 | 80.0696 | 75.7456 | 2.2227 | 2.14 | 1.5494
18.6334 | 81.077 | 80.0443 | 75.7484 | 2.2228 | 2.1401 | 1.5494
18.6375 | 81.0654 | 80.0738 | 75.7438 | 2.2229 | 2.14 | 1.5494
18.6417 | 81.0697 | 80.1019 | 75.7386 | 2.2228 | 2.14 | 1.5494
18.6459 | 81.0778 | 80.1137 | 75.738 | 2.2228 | 2.14 | 1.5494
18.65 | 81.0963 | 80.1254 | 75.7371 | 2.223 | 2.1402 | 1.5494
18.6542 | 81.1181 | 80.1035 | 75.7385 | 2.223 | 2.1401 | 1.5494
18.6584 | 81.1095 | 80.0852 | 75.7404 | 2.223 | 2.14 | 1.5495
18.6625 | 81.1184 | 80.0676 | 75.7435 | 2.2232 | 2.1401 | 1.5494
18.6667 | 81.0986 | 80.0531 | 75.7468 | 2.2233 | 2.1403 | 1.5494
18.6709 | 81.0683 | 80.0677 | 75.7455 | 2.2234 | 2.1402 | 1.5494
18.675 | 81.0417 | 80.0726 | 75.7442 | 2.2235 | 2.1402 | 1.5494
18.6792 | 81.0454 | 80.1007 | 75.7403 | 2.2235 | 2.1402 | 1.5494
18.6834 | 81.0563 | 80.1306 | 75.7357 | 2.2236 | 2.1402 | 1.5494
18.6875 | 81.0779 | 80.1041 | 75.7385 | 2.2238 | 2.1402 | 1.5494
18.6917 | 81.076 | 80.0849 | 75.7415 | 2.224 | 2.1403 | 1.5494
18.6959 | 81.0876 | 80.0843 | 75.7412 | 2.224 | 2.1402 | 1.5494
18.7 | 81.0885 | 80.0796 | 75.7411 | 2.2238 | 2.14 | 1.5495
18.7042 | 81.1025 | 80.0764 | 75.7432 | 2.2239 | 2.1402 | 1.5494
18.7084 | 81.102 | 80.0762 | 75.7451 | 2.2241 | 2.1405 | 1.5494
18.7125 | 81.0938 | 80.0706 | 75.7449 | 2.2242 | 2.1404 | 1.5494
18.7167 | 81.0553 | 80.0602 | 75.745 | 2.2244 | 2.1403 | 1.5494
18.7209 | 81.0356 | 80.0935 | 75.7415 | 2.2244 | 2.1403 | 1.5494
18.725 | 81.0365 | 80.1225 | 75.7376 | 2.2246 | 2.1403 | 1.5494
18.7292 | 81.0266 | 80.1032 | 75.7405 | 2.2246 | 2.1403 | 1.5494
18.7334 | 81.0397 | 80.093 | 75.7435 | 2.2249 | 2.1404 | 1.5494
18.7375 | 81.0518 | 80.0935 | 75.7412 | 2.2251 | 2.1402 | 1.5494
18.7417 | 81.0649 | 80.0907 | 75.739 | 2.225 | 2.14 | 1.5495
18.7459 | 81.071 | 80.0882 | 75.7414 | 2.2251 | 2.1402 | 1.5494
18.75 | 81.088 | 80.0868 | 75.7438 | 2.2252 | 2.1404 | 1.5494
18.7542 | 81.0805 | 80.076 | 75.7456 | 2.2253 | 2.1403 | 1.5494
18.7584 | 81.0648 | 80.065 | 75.7477 | 2.2255 | 2.1402 | 1.5494
18.7625 | 81.0328 | 80.0973 | 75.7442 | 2.2256 | 2.1402 | 1.5494
18.7667 | 81.0113 | 80.1202 | 75.7402 | 2.2258 | 2.1402 | 1.5494
18.7709 | 80.9912 | 80.107 | 75.7407 | 2.226 | 2.1402 | 1.5494
18.775 | 80.979 | 80.1012 | 75.7416 | 2.2263 | 2.1403 | 1.5494
18.7792 | 80.9609 | 80.1092 | 75.7396 | 2.2268 | 2.14 | 1.5494
18.7834 | 80.9554 | 80.1175 | 75.7374 | 2.2272 | 2.1397 | 1.5494
18.7875 | 80.9448 | 80.1229 | 75.7428 | 2.2275 | 2.1399 | 1.5494
18.7917 | 80.9503 | 80.1281 | 75.7479 | 2.2278 | 2.1399 | 1.5493
18.7959 | 81.0107 | 80.0994 | 75.7454 | 2.2279 | 2.1398 | 1.5494
18.8 | 81.0543 | 80.0792 | 75.7435 | 2.2279 | 2.1397 | 1.5495
18.8042 | 81.0851 | 80.0956 | 75.7366 | 2.228 | 2.1397 | 1.5494
18.8084 | 81.1217 | 80.1025 | 75.7295 | 2.2281 | 2.1397 | 1.5494
18.8125 | 81.1389 | 80.1073 | 75.7402 | 2.2281 | 2.1398 | 1.5494
18.8167 | 81.1508 | 80.1114 | 75.7506 | 2.2282 | 2.1398 | 1.5494
18.8209 | 81.1555 | 80.115 | 75.7517 | 2.2283 | 2.1396 | 1.5494
18.825 | 81.1725 | 80.1235 | 75.7527 | 2.2282 | 2.1395 | 1.5494
18.8292 | 81.1382 | 80.1191 | 75.7404 | 2.2284 | 2.1396 | 1.5494
18.8334 | 81.1538 | 80.1135 | 75.7282 | 2.2285 | 2.1396 | 1.5494
18.8375 | 81.1136 | 80.0944 | 75.7282 | 2.2284 | 2.1396 | 1.5494
18.8417 | 81.0924 | 80.0848 | 75.7282 | 2.2286 | 2.1395 | 1.5495
18.8459 | 81.075 | 80.0957 | 75.7418 | 2.2285 | 2.1395 | 1.5494
18.85 | 81.0505 | 80.1042 | 75.7553 | 2.2284 | 2.1395 | 1.5494
18.8542 | 81.035 | 80.0932 | 75.7548 | 2.2285 | 2.1397 | 1.5494
18.8584 | 81.0518 | 80.0796 | 75.7547 | 2.2285 | 2.1398 | 1.5494
18.8625 | 81.0492 | 80.0647 | 75.7414 | 2.2283 | 2.1398 | 1.5494
18.8667 | 81.0623 | 80.0512 | 75.7281 | 2.2284 | 2.1399 | 1.5494
18.8709 | 81.094 | 80.0693 | 75.7326 | 2.2283 | 2.14 | 1.5494
18.875 | 81.1198 | 80.072 | 75.737 | 2.2282 | 2.1401 | 1.5494
18.8792 | 81.1245 | 80.0891 | 75.7441 | 2.2284 | 2.1401 | 1.5494
18.8834 | 81.1537 | 80.1042 | 75.7511 | 2.2286 | 2.1401 | 1.5494
18.8875 | 81.1464 | 80.105 | 75.7476 | 2.2284 | 2.14 | 1.5494
18.8917 | 81.1461 | 80.1093 | 75.744 | 2.2285 | 2.1401 | 1.5494
18.8959 | 81.1616 | 80.1114 | 75.7439 | 2.2285 | 2.14 | 1.5494
18.9 | 81.1695 | 80.1118 | 75.7436 | 2.2283 | 2.1399 | 1.5494
18.9042 | 81.1787 | 80.1081 | 75.7412 | 2.2284 | 2.1399 | 1.5494
18.9084 | 81.2056 | 80.1162 | 75.7387 | 2.2284 | 2.1398 | 1.5494
18.9125 | 81.2202 | 80.1019 | 75.7353 | 2.2282 | 2.1398 | 1.5494
18.9167 | 81.228 | 80.089 | 75.7323 | 2.2284 | 2.1398 | 1.5494
18.9209 | 81.2482 | 80.0968 | 75.7387 | 2.2284 | 2.1398 | 1.5494
18.925 | 81.2484 | 80.1033 | 75.7444 | 2.2284 | 2.1396 | 1.5494
18.9292 | 81.2457 | 80.097 | 75.7467 | 2.2284 | 2.1398 | 1.5494
18.9334 | 81.2563 | 80.0963 | 75.7492 | 2.2283 | 2.1399 | 1.5494
18.9375 | 81.2575 | 80.0905 | 75.745 | 2.2282 | 2.1398 | 1.5494
18.9417 | 81.2715 | 80.0777 | 75.7413 | 2.2282 | 2.1398 | 1.5494
18.9459 | 81.2598 | 80.0868 | 75.7402 | 2.2282 | 2.1399 | 1.5494
18.95 | 81.2703 | 80.0955 | 75.7386 | 2.2281 | 2.1399 | 1.5494
18.9542 | 81.2841 | 80.0863 | 75.7381 | 2.2279 | 2.14 | 1.5494
18.9584 | 81.2865 | 80.076 | 75.7384 | 2.2279 | 2.1401 | 1.5494
18.9625 | 81.283 | 80.0888 | 75.7383 | 2.2279 | 2.14 | 1.5494
18.9667 | 81.2706 | 80.0964 | 75.7377 | 2.2279 | 2.1399 | 1.5495
18.9709 | 81.2321 | 80.0946 | 75.7387 | 2.228 | 2.14 | 1.5495
18.975 | 81.2128 | 80.0983 | 75.7392 | 2.2279 | 2.1402 | 1.5495
18.9792 | 81.2126 | 80.0949 | 75.7431 | 2.2276 | 2.14 | 1.5494
18.9834 | 81.2118 | 80.0885 | 75.7476 | 2.2275 | 2.1399 | 1.5494
18.9875 | 81.2474 | 80.0942 | 75.7413 | 2.2275 | 2.14 | 1.5495
18.9917 | 81.2565 | 80.1036 | 75.7347 | 2.2275 | 2.14 | 1.5495
18.9959 | 81.2689 | 80.083 | 75.7342 | 2.2276 | 2.1401 | 1.5495
19 | 81.2841 | 80.068 | 75.7341 | 2.2275 | 2.1402 | 1.5494
19.0042 | 81.2892 | 80.0826 | 75.7359 | 2.2274 | 2.1401 | 1.5495
19.0084 | 81.3088 | 80.0895 | 75.7377 | 2.2272 | 2.14 | 1.5496
19.0125 | 81.3235 | 80.085 | 75.7333 | 2.2271 | 2.1402 | 1.5496
19.0167 | 81.3187 | 80.0858 | 75.7289 | 2.2269 | 2.1404 | 1.5496
19.0209 | 81.3086 | 80.0771 | 75.7347 | 2.2268 | 2.1403 | 1.5496
19.025 | 81.2791 | 80.0659 | 75.7403 | 2.2267 | 2.1402 | 1.5496
19.0292 | 81.265 | 80.087 | 75.7377 | 2.2267 | 2.1403 | 1.5496
19.0334 | 81.2471 | 80.104 | 75.7347 | 2.2267 | 2.1403 | 1.5497
19.0375 | 81.2398 | 80.0783 | 75.7324 | 2.2266 | 2.1404 | 1.5496
19.0417 | 81.2281 | 80.0615 | 75.731 | 2.2266 | 2.1406 | 1.5496
19.0459 | 81.222 | 80.0725 | 75.7332 | 2.2266 | 2.1404 | 1.5496
19.05 | 81.2161 | 80.0755 | 75.7352 | 2.2266 | 2.1402 | 1.5497
19.0542 | 81.2121 | 80.0857 | 75.7334 | 2.2265 | 2.1405 | 1.5497
19.0584 | 81.2162 | 80.0969 | 75.7313 | 2.2264 | 2.1407 | 1.5497
19.0625 | 81.2245 | 80.0717 | 75.7309 | 2.2264 | 2.1406 | 1.5497
19.0667 | 81.2318 | 80.0514 | 75.731 | 2.2264 | 2.1406 | 1.5497
19.0709 | 81.2346 | 80.0783 | 75.7311 | 2.2265 | 2.1405 | 1.5497
19.075 | 81.2345 | 80.0962 | 75.7306 | 2.2265 | 2.1404 | 1.5497
19.0792 | 81.2273 | 80.0855 | 75.7324 | 2.2265 | 2.1406 | 1.5497
19.0834 | 81.2319 | 80.0799 | 75.7348 | 2.2264 | 2.1408 | 1.5497
19.0875 | 81.234 | 80.0769 | 75.7353 | 2.2263 | 2.1406 | 1.5497
19.0917 | 81.2374 | 80.0724 | 75.736 | 2.2264 | 2.1404 | 1.5497
19.0959 | 81.2348 | 80.0913 | 75.7358 | 2.2265 | 2.1405 | 1.5497
19.1 | 81.2302 | 80.1088 | 75.7348 | 2.2264 | 2.1406 | 1.5497
19.1042 | 81.226 | 80.0807 | 75.7344 | 2.2263 | 2.1406 | 1.5497
19.1084 | 81.2298 | 80.0606 | 75.7347 | 2.2263 | 2.1407 | 1.5497
19.1125 | 81.2377 | 80.0754 | 75.733 | 2.2262 | 2.1405 | 1.5497
19.1167 | 81.2358 | 80.0849 | 75.7311 | 2.2263 | 2.1404 | 1.5497
19.1209 | 81.2411 | 80.0832 | 75.731 | 2.2263 | 2.1407 | 1.5498
19.125 | 81.239 | 80.0832 | 75.731 | 2.2263 | 2.1408 | 1.5497
19.1292 | 81.2431 | 80.0714 | 75.7321 | 2.2262 | 2.1407 | 1.5498
19.1334 | 81.248 | 80.0599 | 75.7331 | 2.2262 | 2.1406 | 1.5498
19.1375 | 81.2511 | 80.0779 | 75.731 | 2.2262 | 2.1407 | 1.5498
19.1417 | 81.2423 | 80.0917 | 75.7281 | 2.2263 | 2.1407 | 1.5498
19.1459 | 81.2372 | 80.076 | 75.7305 | 2.2263 | 2.1408 | 1.5498
19.15 | 81.2241 | 80.0637 | 75.7336 | 2.2263 | 2.1409 | 1.5498
19.1542 | 81.2195 | 80.0752 | 75.7341 | 2.2262 | 2.1407 | 1.5498
19.1584 | 81.2188 | 80.0832 | 75.7344 | 2.2262 | 2.1406 | 1.5498
19.1625 | 81.2148 | 80.0807 | 75.7307 | 2.2262 | 2.1408 | 1.5498
19.1667 | 81.2086 | 80.0811 | 75.7267 | 2.2263 | 2.141 | 1.5498
19.1709 | 81.2018 | 80.0707 | 75.7312 | 2.2262 | 2.1408 | 1.5498
19.175 | 81.1903 | 80.0605 | 75.7362 | 2.2262 | 2.1407 | 1.5498
19.1792 | 81.1855 | 80.0796 | 75.7335 | 2.2262 | 2.1408 | 1.5498
19.1834 | 81.1845 | 80.0953 | 75.7304 | 2.2261 | 2.1408 | 1.5499
19.1875 | 81.1795 | 80.0759 | 75.7301 | 2.2262 | 2.1409 | 1.5498
19.1917 | 81.1777 | 80.0627 | 75.7299 | 2.2262 | 2.141 | 1.5498
19.1959 | 81.1702 | 80.0713 | 75.7325 | 2.2262 | 2.1408 | 1.5498
19.2 | 81.1603 | 80.0748 | 75.735 | 2.2262 | 2.1407 | 1.5499
19.2042 | 81.1543 | 80.0795 | 75.7305 | 2.2262 | 2.1409 | 1.5498
19.2084 | 81.1532 | 80.0851 | 75.7262 | 2.2262 | 2.141 | 1.5498
19.2125 | 81.1452 | 80.0688 | 75.7309 | 2.2262 | 2.1409 | 1.5498
19.2167 | 81.1432 | 80.0561 | 75.7355 | 2.2263 | 2.1409 | 1.5498
19.2209 | 81.1365 | 80.0751 | 75.7325 | 2.2262 | 2.1409 | 1.5498
19.225 | 81.1289 | 80.088 | 75.7291 | 2.2262 | 2.1409 | 1.5499
19.2292 | 81.1286 | 80.0733 | 75.7287 | 2.2262 | 2.141 | 1.5498
19.2334 | 81.1258 | 80.0641 | 75.729 | 2.2262 | 2.1411 | 1.5498
19.2375 | 81.1226 | 80.0678 | 75.7326 | 2.2262 | 2.1409 | 1.5498
19.2417 | 81.1205 | 80.0685 | 75.736 | 2.2263 | 2.1408 | 1.5499
19.2459 | 81.1137 | 80.0792 | 75.7307 | 2.2263 | 2.141 | 1.5499
19.25 | 81.1136 | 80.0884 | 75.7251 | 2.2262 | 2.1411 | 1.5499
19.2542 | 81.1086 | 80.0655 | 75.7297 | 2.2263 | 2.1411 | 1.5498
19.2584 | 81.1067 | 80.0491 | 75.7346 | 2.2263 | 2.1411 | 1.5498
19.2625 | 81.1015 | 80.0702 | 75.7322 | 2.2263 | 2.141 | 1.5499
19.2667 | 81.0923 | 80.083 | 75.7295 | 2.2264 | 2.1409 | 1.5499
19.2709 | 81.0892 | 80.0776 | 75.7292 | 2.2264 | 2.1411 | 1.5499
19.275 | 81.0873 | 80.0769 | 75.7289 | 2.2263 | 2.1412 | 1.5498
19.2792 | 81.0809 | 80.063 | 75.732 | 2.2264 | 2.1411 | 1.5499
19.2834 | 81.0812 | 80.0528 | 75.735 | 2.2264 | 2.141 | 1.5499
19.2875 | 81.0736 | 80.0734 | 75.7296 | 2.2264 | 2.1411 | 1.5499
19.2917 | 81.0715 | 80.0855 | 75.7242 | 2.2264 | 2.1411 | 1.5499
19.2959 | 81.0679 | 80.0696 | 75.73 | 2.2264 | 2.1412 | 1.5499
19.3 | 81.0656 | 80.0602 | 75.7359 | 2.2265 | 2.1413 | 1.5498
19.3042 | 81.058 | 80.0641 | 75.7321 | 2.2265 | 2.1411 | 1.5499
19.3084 | 81.0521 | 80.0669 | 75.7283 | 2.2266 | 2.141 | 1.55
19.3125 | 81.0508 | 80.0746 | 75.7276 | 2.2265 | 2.1412 | 1.5499
19.3167 | 81.0481 | 80.0789 | 75.727 | 2.2266 | 2.1413 | 1.5498
19.3209 | 81.049 | 80.0641 | 75.7322 | 2.2267 | 2.1412 | 1.5499
19.325 | 81.049 | 80.0545 | 75.7374 | 2.2267 | 2.1412 | 1.5499
19.3292 | 81.0397 | 80.0676 | 75.7301 | 2.2268 | 2.1412 | 1.5499
19.3334 | 81.0417 | 80.0767 | 75.7227 | 2.2268 | 2.1412 | 1.5499
19.3375 | 81.049 | 80.0703 | 75.7283 | 2.2268 | 2.1413 | 1.5499
19.3417 | 81.0533 | 80.0652 | 75.734 | 2.2269 | 2.1414 | 1.5498
19.3459 | 81.0543 | 80.0625 | 75.7326 | 2.227 | 2.1413 | 1.5499
19.35 | 81.0523 | 80.0609 | 75.7314 | 2.227 | 2.1412 | 1.55
19.3542 | 81.0471 | 80.0714 | 75.7283 | 2.227 | 2.1413 | 1.5499
19.3584 | 81.0479 | 80.0784 | 75.7249 | 2.227 | 2.1413 | 1.5498
19.3625 | 81.0522 | 80.065 | 75.7307 | 2.2271 | 2.1413 | 1.5499
19.3667 | 81.0514 | 80.0559 | 75.7365 | 2.2271 | 2.1414 | 1.5499
19.3709 | 81.0476 | 80.0643 | 75.7306 | 2.2272 | 2.1413 | 1.5499
19.375 | 81.049 | 80.0699 | 75.7251 | 2.2272 | 2.1412 | 1.5499
19.3792 | 81.0526 | 80.0707 | 75.7285 | 2.2272 | 2.1413 | 1.5499
19.3834 | 81.0583 | 80.0706 | 75.7315 | 2.2272 | 2.1414 | 1.5498
19.3875 | 81.0584 | 80.0615 | 75.7318 | 2.2273 | 2.1414 | 1.5499
19.3917 | 81.056 | 80.0557 | 75.7321 | 2.2273 | 2.1413 | 1.55
19.3959 | 81.0518 | 80.0677 | 75.7284 | 2.2273 | 2.1413 | 1.5499
19.4 | 81.0464 | 80.0756 | 75.7251 | 2.2273 | 2.1413 | 1.5499
19.4042 | 81.049 | 80.0678 | 75.7303 | 2.2274 | 2.1414 | 1.5499
19.4084 | 81.0449 | 80.0621 | 75.7351 | 2.2275 | 2.1415 | 1.5499
19.4125 | 81.0352 | 80.0606 | 75.7309 | 2.2275 | 2.1414 | 1.5499
19.4167 | 81.0334 | 80.0605 | 75.7267 | 2.2276 | 2.1413 | 1.5499
19.4209 | 81.0325 | 80.0658 | 75.7286 | 2.2276 | 2.1414 | 1.5499
19.425 | 81.0337 | 80.0678 | 75.7306 | 2.2277 | 2.1415 | 1.5499
19.4292 | 81.0396 | 80.0656 | 75.7309 | 2.2278 | 2.1414 | 1.5499
19.4334 | 81.0428 | 80.0661 | 75.7311 | 2.2278 | 2.1414 | 1.55
19.4375 | 81.0372 | 80.0656 | 75.7285 | 2.2279 | 2.1414 | 1.5499
19.4417 | 81.0343 | 80.0653 | 75.7263 | 2.2279 | 2.1415 | 1.5499
19.4459 | 81.0341 | 80.0579 | 75.7309 | 2.228 | 2.1415 | 1.5499
19.45 | 81.0291 | 80.0492 | 75.7356 | 2.228 | 2.1415 | 1.5499
19.4542 | 81.0285 | 80.0607 | 75.7311 | 2.2281 | 2.1415 | 1.5499
19.4584 | 81.0328 | 80.0726 | 75.7262 | 2.2282 | 2.1414 | 1.5499
19.4625 | 81.0441 | 80.0764 | 75.7268 | 2.2281 | 2.1415 | 1.5499
19.4667 | 81.0544 | 80.0806 | 75.7275 | 2.2281 | 2.1415 | 1.5499
19.4709 | 81.0589 | 80.0598 | 75.7304 | 2.2282 | 2.1415 | 1.5499
19.475 | 81.0552 | 80.0406 | 75.7339 | 2.2284 | 2.1416 | 1.5499
19.4792 | 81.0302 | 80.0438 | 75.7324 | 2.2285 | 2.1416 | 1.5499
19.4834 | 81.0107 | 80.0446 | 75.7309 | 2.2285 | 2.1416 | 1.5499
19.4875 | 81.0208 | 80.0679 | 75.7298 | 2.2285 | 2.1415 | 1.5499
19.4917 | 81.0409 | 80.0897 | 75.7278 | 2.2284 | 2.1415 | 1.5499
19.4959 | 81.0465 | 80.0804 | 75.7261 | 2.2286 | 2.1416 | 1.5499
19.5 | 81.0596 | 80.0744 | 75.7248 | 2.2288 | 2.1416 | 1.5499
19.5042 | 81.0582 | 80.0534 | 75.7299 | 2.2287 | 2.1416 | 1.5499
19.5084 | 81.0439 | 80.0339 | 75.735 | 2.2287 | 2.1416 | 1.5499
19.5125 | 81.0417 | 80.0373 | 75.7348 | 2.2289 | 2.1417 | 1.5499
19.5167 | 81.031 | 80.0368 | 75.7344 | 2.2289 | 2.1417 | 1.5499
19.5209 | 81.0057 | 80.0643 | 75.7288 | 2.229 | 2.1416 | 1.5499
19.525 | 81.0048 | 80.0892 | 75.723 | 2.2289 | 2.1415 | 1.5499
19.5292 | 81.0221 | 80.0844 | 75.7262 | 2.229 | 2.1416 | 1.5499
19.5334 | 81.0423 | 80.0845 | 75.7289 | 2.2289 | 2.1417 | 1.5499
19.5375 | 81.0556 | 80.0537 | 75.7302 | 2.2291 | 2.1417 | 1.5499
19.5417 | 81.0628 | 80.0254 | 75.7323 | 2.2293 | 2.1417 | 1.5499
19.5459 | 81.0554 | 80.041 | 75.7315 | 2.2293 | 2.1417 | 1.5499
19.55 | 81.0425 | 80.0527 | 75.7304 | 2.2293 | 2.1416 | 1.5499
19.5542 | 81.0263 | 80.0563 | 75.732 | 2.2294 | 2.1418 | 1.5499
19.5584 | 81.0146 | 80.0579 | 75.7335 | 2.2295 | 2.1419 | 1.5499
19.5625 | 81.0036 | 80.0635 | 75.7291 | 2.2294 | 2.1418 | 1.5499
19.5667 | 81.0091 | 80.0702 | 75.725 | 2.2295 | 2.1416 | 1.5499
19.5709 | 81.0138 | 80.0718 | 75.727 | 2.2297 | 2.1417 | 1.5499
19.575 | 81.0135 | 80.0762 | 75.7289 | 2.2297 | 2.1418 | 1.5499
19.5792 | 81.0152 | 80.0559 | 75.731 | 2.2298 | 2.1418 | 1.5499
19.5834 | 81.02 | 80.0366 | 75.7335 | 2.2297 | 2.1417 | 1.5499
19.5875 | 81.0409 | 80.0466 | 75.7309 | 2.2297 | 2.1417 | 1.5499
19.5917 | 81.0397 | 80.0548 | 75.7281 | 2.2298 | 2.1417 | 1.5499
19.5959 | 81.0476 | 80.0522 | 75.7314 | 2.23 | 2.1419 | 1.5499
19.6 | 81.0136 | 80.047 | 75.7349 | 2.2302 | 2.142 | 1.5499
19.6042 | 80.9929 | 80.0607 | 75.7315 | 2.2303 | 2.1418 | 1.5499
19.6084 | 80.9875 | 80.073 | 75.7281 | 2.2302 | 2.1416 | 1.5499
19.6125 | 80.9907 | 80.0741 | 75.7281 | 2.2303 | 2.1418 | 1.5499
19.6167 | 80.9934 | 80.0789 | 75.7278 | 2.2305 | 2.1419 | 1.5499
19.6209 | 81.0102 | 80.0611 | 75.7294 | 2.2306 | 2.1418 | 1.5499
19.625 | 81.0028 | 80.0443 | 75.7314 | 2.2307 | 2.1417 | 1.5499
19.6292 | 81.0008 | 80.0578 | 75.7303 | 2.2308 | 2.1417 | 1.5499
19.6334 | 81.0112 | 80.0702 | 75.7291 | 2.2308 | 2.1417 | 1.5499
19.6375 | 81.0173 | 80.0598 | 75.7335 | 2.2308 | 2.1418 | 1.5499
19.6417 | 81.0059 | 80.0489 | 75.7381 | 2.231 | 2.1419 | 1.5499
19.6459 | 80.999 | 80.0586 | 75.7317 | 2.2311 | 2.1417 | 1.5499
19.65 | 80.9907 | 80.0644 | 75.7255 | 2.2312 | 2.1416 | 1.5499
19.6542 | 80.9588 | 80.0739 | 75.7254 | 2.2314 | 2.1417 | 1.5499
19.6584 | 80.948 | 80.085 | 75.7251 | 2.2317 | 2.1418 | 1.5498
19.6625 | 80.93 | 80.0793 | 75.7322 | 2.232 | 2.1416 | 1.5499
19.6667 | 80.9061 | 80.0756 | 75.7393 | 2.2322 | 2.1414 | 1.5499
19.6709 | 80.9064 | 80.0817 | 75.7347 | 2.2326 | 2.1414 | 1.5499
19.675 | 80.917 | 80.0894 | 75.7301 | 2.2329 | 2.1414 | 1.5499
19.6792 | 80.9282 | 80.0649 | 75.725 | 2.2332 | 2.1415 | 1.5499
19.6834 | 80.9361 | 80.0446 | 75.7203 | 2.2335 | 2.1415 | 1.5499
19.6875 | 80.9589 | 80.0592 | 75.7248 | 2.2337 | 2.1414 | 1.5499
19.6917 | 80.9548 | 80.0675 | 75.7289 | 2.2338 | 2.1412 | 1.5499
19.6959 | 80.9851 | 80.0801 | 75.7379 | 2.2338 | 2.1414 | 1.5499
19.7 | 81.0005 | 80.0922 | 75.7467 | 2.2338 | 2.1415 | 1.5498
19.7042 | 81.0424 | 80.0728 | 75.737 | 2.2338 | 2.1414 | 1.5499
19.7084 | 81.0517 | 80.0584 | 75.7277 | 2.2338 | 2.1413 | 1.5499
19.7125 | 81.0859 | 80.0672 | 75.7192 | 2.2339 | 2.1413 | 1.5499
19.7167 | 81.1085 | 80.0734 | 75.7104 | 2.2338 | 2.1413 | 1.5499
19.7209 | 81.1204 | 80.0679 | 75.7238 | 2.2339 | 2.1414 | 1.5499
19.725 | 81.128 | 80.0667 | 75.7374 | 2.2341 | 2.1414 | 1.5499
19.7292 | 81.1314 | 80.0666 | 75.7392 | 2.2341 | 2.1413 | 1.5499
19.7334 | 81.1038 | 80.0677 | 75.741 | 2.2341 | 2.1412 | 1.5499
19.7375 | 81.0968 | 80.0589 | 75.7333 | 2.2342 | 2.1414 | 1.5499
19.7417 | 81.0797 | 80.0476 | 75.7257 | 2.2341 | 2.1416 | 1.5499
19.7459 | 81.0622 | 80.0385 | 75.7262 | 2.2341 | 2.1416 | 1.5499
19.75 | 81.0503 | 80.0287 | 75.7267 | 2.2342 | 2.1415 | 1.5499
19.7542 | 81.0558 | 80.051 | 75.7283 | 2.234 | 2.1416 | 1.5499
19.7584 | 81.0372 | 80.0635 | 75.7296 | 2.234 | 2.1417 | 1.5499
19.7625 | 81.045 | 80.0627 | 75.7306 | 2.2342 | 2.1417 | 1.5499
19.7667 | 81.0432 | 80.0605 | 75.7317 | 2.2341 | 2.1418 | 1.5499
19.7709 | 81.0195 | 80.0673 | 75.7337 | 2.2342 | 2.1416 | 1.5499
19.775 | 81.0066 | 80.0766 | 75.7353 | 2.2344 | 2.1415 | 1.5499
19.7792 | 80.9991 | 80.0809 | 75.7333 | 2.2342 | 2.1416 | 1.5499
19.7834 | 80.981 | 80.0845 | 75.7316 | 2.2341 | 2.1416 | 1.5499
19.7875 | 80.9802 | 80.0698 | 75.7275 | 2.2343 | 2.1415 | 1.5499
19.7917 | 80.9915 | 80.064 | 75.7235 | 2.2342 | 2.1414 | 1.5499
19.7959 | 80.986 | 80.0668 | 75.7249 | 2.2343 | 2.1414 | 1.5499
19.8 | 80.987 | 80.07 | 75.7259 | 2.2345 | 2.1414 | 1.5499
19.8042 | 81.003 | 80.0685 | 75.7302 | 2.2343 | 2.1415 | 1.5499
19.8084 | 80.9984 | 80.0656 | 75.7347 | 2.2344 | 2.1415 | 1.5499
19.8125 | 81.016 | 80.0602 | 75.7332 | 2.2345 | 2.1415 | 1.5499
19.8167 | 81.0104 | 80.0601 | 75.7315 | 2.2345 | 2.1414 | 1.5499
19.8209 | 81.0024 | 80.0607 | 75.7304 | 2.2346 | 2.1415 | 1.5499
19.825 | 81.0115 | 80.0543 | 75.7294 | 2.2345 | 2.1415 | 1.5499
19.8292 | 81.0328 | 80.0578 | 75.7311 | 2.2342 | 2.1416 | 1.5499
19.8334 | 81.048 | 80.0602 | 75.7328 | 2.2343 | 2.1415 | 1.5499
19.8375 | 81.0913 | 80.0556 | 75.7271 | 2.2344 | 2.1416 | 1.5499
19.8417 | 81.1048 | 80.0537 | 75.7214 | 2.2344 | 2.1417 | 1.55
19.8459 | 81.1108 | 80.0591 | 75.7253 | 2.2346 | 2.1416 | 1.5499
19.85 | 81.1246 | 80.0574 | 75.7289 | 2.2345 | 2.1416 | 1.5499
19.8542 | 81.1055 | 80.0646 | 75.7309 | 2.2346 | 2.1416 | 1.5499
19.8584 | 81.1066 | 80.0759 | 75.7327 | 2.2347 | 2.1416 | 1.55
19.8625 | 81.0971 | 80.0639 | 75.7294 | 2.2346 | 2.1416 | 1.5499
19.8667 | 81.0894 | 80.0537 | 75.7267 | 2.2345 | 2.1417 | 1.5499
19.8709 | 81.0936 | 80.0598 | 75.7288 | 2.2345 | 2.1416 | 1.5499
19.875 | 81.0962 | 80.0641 | 75.7303 | 2.2345 | 2.1415 | 1.55
19.8792 | 81.0951 | 80.0587 | 75.7269 | 2.2345 | 2.1417 | 1.55
19.8834 | 81.1159 | 80.0594 | 75.7238 | 2.2344 | 2.1418 | 1.55
19.8875 | 81.125 | 80.0525 | 75.7241 | 2.2343 | 2.1417 | 1.55
19.8917 | 81.1571 | 80.0415 | 75.7246 | 2.2343 | 2.1417 | 1.55
19.8959 | 81.1757 | 80.0545 | 75.7254 | 2.2343 | 2.1417 | 1.55
19.9 | 81.194 | 80.0667 | 75.7253 | 2.2344 | 2.1417 | 1.55
19.9042 | 81.2001 | 80.0566 | 75.7263 | 2.2344 | 2.1418 | 1.55
19.9084 | 81.2092 | 80.0488 | 75.7277 | 2.2343 | 2.1419 | 1.55
19.9125 | 81.2122 | 80.0523 | 75.726 | 2.2342 | 2.1418 | 1.55
19.9167 | 81.2207 | 80.0519 | 75.7243 | 2.2342 | 2.1417 | 1.5501
19.9209 | 81.2218 | 80.0536 | 75.724 | 2.2342 | 2.1419 | 1.55
19.925 | 81.2094 | 80.0593 | 75.7235 | 2.2341 | 2.142 | 1.55
19.9292 | 81.1995 | 80.0525 | 75.7259 | 2.2341 | 2.1419 | 1.55
19.9334 | 81.1967 | 80.0427 | 75.7288 | 2.234 | 2.1419 | 1.5501
19.9375 | 81.1924 | 80.0538 | 75.7252 | 2.234 | 2.1419 | 1.5501
19.9417 | 81.1882 | 80.0641 | 75.7211 | 2.234 | 2.1419 | 1.5501
19.9459 | 81.1883 | 80.0518 | 75.7223 | 2.234 | 2.142 | 1.5501
19.95 | 81.1819 | 80.0442 | 75.7234 | 2.2339 | 2.1421 | 1.5501
19.9542 | 81.1841 | 80.0515 | 75.7243 | 2.2339 | 2.142 | 1.5501
19.9584 | 81.1827 | 80.0516 | 75.7254 | 2.2339 | 2.1419 | 1.5501
19.9625 | 81.1819 | 80.0573 | 75.7243 | 2.2339 | 2.142 | 1.5501
19.9667 | 81.1787 | 80.0663 | 75.7231 | 2.2339 | 2.1421 | 1.5501
19.9709 | 81.1801 | 80.0544 | 75.7257 | 2.2338 | 2.142 | 1.5501
19.975 | 81.1815 | 80.0434 | 75.7286 | 2.2338 | 2.142 | 1.5501
19.9792 | 81.1822 | 80.0595 | 75.7278 | 2.2338 | 2.1419 | 1.5501
19.9834 | 81.1811 | 80.0719 | 75.7263 | 2.2338 | 2.1419 | 1.5501
19.9875 | 81.1706 | 80.0549 | 75.7243 | 2.2339 | 2.142 | 1.5501
19.9917 | 81.1672 | 80.0466 | 75.7228 | 2.2338 | 2.1422 | 1.5501
19.9959 | 81.1622 | 80.0494 | 75.7248 | 2.2337 | 2.142 | 1.5501
20 | 81.1635 | 80.0466 | 75.727 | 2.2337 | 2.1418 | 1.5501
20.0042 | 81.1644 | 80.0584 | 75.725 | 2.2337 | 2.142 | 1.5501
20.0084 | 81.0536 | 79.9798 | 75.6543 | 2.2328 | 2.1414 | 1.5496
20.0125 | 80.9032 | 79.7772 | 75.5175 | 2.2316 | 2.1399 | 1.5484
20.0167 | 80.6939 | 79.5292 | 75.3433 | 2.2291 | 2.1376 | 1.5466
20.0209 | 80.4638 | 79.2743 | 75.1343 | 2.2263 | 2.1342 | 1.5442
20.025 | 80.224 | 79.0103 | 74.9252 | 2.2238 | 2.131 | 1.5419
20.0292 | 79.9846 | 78.7263 | 74.7118 | 2.2213 | 2.1285 | 1.5398
20.0334 | 79.6736 | 78.3981 | 74.4603 | 2.2188 | 2.1259 | 1.5376
20.0375 | 79.3463 | 78.0098 | 74.1737 | 2.2164 | 2.1229 | 1.5355
20.0417 | 79.0673 | 77.6571 | 73.9131 | 2.2139 | 2.1201 | 1.5334
20.0459 | 78.8008 | 77.3735 | 73.6764 | 2.2114 | 2.1174 | 1.5313
20.05 | 78.5346 | 77.0932 | 73.4442 | 2.2094 | 2.1151 | 1.5294
20.0542 | 78.2761 | 76.7822 | 73.2173 | 2.2077 | 2.1132 | 1.5278
20.0584 | 77.9961 | 76.4667 | 72.9802 | 2.2056 | 2.1112 | 1.5261
20.0625 | 77.7215 | 76.1646 | 72.7333 | 2.2036 | 2.1088 | 1.5243
20.0667 | 77.4956 | 75.8955 | 72.5127 | 2.2017 | 2.1065 | 1.5226
20.0709 | 77.2843 | 75.6613 | 72.3147 | 2.1998 | 2.1047 | 1.5209
20.075 | 77.0467 | 75.4136 | 72.1043 | 2.1982 | 2.103 | 1.5192
20.0792 | 76.8022 | 75.1296 | 71.8727 | 2.1965 | 2.1011 | 1.5176
20.0834 | 76.5615 | 74.8532 | 71.6444 | 2.1947 | 2.0991 | 1.5158
20.0875 | 76.3278 | 74.6172 | 71.4052 | 2.1927 | 2.097 | 1.5138
20.0917 | 76.122 | 74.3959 | 71.1806 | 2.1909 | 2.0951 | 1.512
20.0959 | 75.9169 | 74.1616 | 70.9719 | 2.1893 | 2.0935 | 1.5102
20.1 | 75.6894 | 73.9153 | 70.7512 | 2.1877 | 2.0919 | 1.5084
20.1042 | 75.4505 | 73.6633 | 70.5117 | 2.186 | 2.0899 | 1.5068
20.1084 | 75.2297 | 73.4261 | 70.2863 | 2.1843 | 2.088 | 1.505
20.1125 | 75.0302 | 73.2218 | 70.0725 | 2.1825 | 2.0863 | 1.5032
20.1167 | 74.8298 | 73.0196 | 69.8625 | 2.1809 | 2.0847 | 1.5015
20.1209 | 74.6304 | 72.7907 | 69.6643 | 2.1795 | 2.0832 | 1.5
20.125 | 74.4172 | 72.5755 | 69.4606 | 2.1779 | 2.0817 | 1.4985
20.1292 | 74.1959 | 72.3776 | 69.242 | 2.1763 | 2.0801 | 1.4969
20.1334 | 74.0037 | 72.2044 | 69.0378 | 2.1747 | 2.0787 | 1.4954
20.1375 | 73.8218 | 72.0369 | 68.8552 | 2.1731 | 2.0776 | 1.4938
20.1417 | 73.6341 | 71.8647 | 68.6688 | 2.1716 | 2.0764 | 1.4923
20.1459 | 73.4336 | 71.6838 | 68.4795 | 2.1702 | 2.0752 | 1.4909
20.15 | 73.2313 | 71.5149 | 68.2925 | 2.1688 | 2.0738 | 1.4896
20.1542 | 73.036 | 71.359 | 68.0988 | 2.1672 | 2.0726 | 1.488
20.1584 | 72.8576 | 71.2079 | 67.9145 | 2.1657 | 2.0714 | 1.4866
20.1625 | 72.6894 | 71.0454 | 67.7521 | 2.1643 | 2.0703 | 1.4852
20.1667 | 72.5092 | 70.8743 | 67.5845 | 2.163 | 2.069 | 1.4839
20.1709 | 72.3129 | 70.7167 | 67.4022 | 2.1617 | 2.0678 | 1.4826
20.175 | 72.1288 | 70.5667 | 67.2273 | 2.1603 | 2.0665 | 1.4814
20.1792 | 71.9559 | 70.4129 | 67.0613 | 2.1588 | 2.0653 | 1.48
20.1834 | 71.7899 | 70.2589 | 66.8984 | 2.1575 | 2.0643 | 1.4786
20.1875 | 71.6246 | 70.1015 | 66.7453 | 2.1563 | 2.063 | 1.4775
20.1917 | 71.4436 | 69.9417 | 66.5899 | 2.1551 | 2.0618 | 1.4763
20.1959 | 71.2639 | 69.7979 | 66.4213 | 2.1538 | 2.0607 | 1.4751
20.2 | 71.0934 | 69.6606 | 66.2609 | 2.1525 | 2.0595 | 1.4739
20.2042 | 70.9366 | 69.5066 | 66.1187 | 2.1512 | 2.0585 | 1.4726
20.2084 | 70.7844 | 69.352 | 65.9754 | 2.1501 | 2.0574 | 1.4714
20.2125 | 70.6176 | 69.2108 | 65.8255 | 2.149 | 2.0562 | 1.4704
20.2167 | 70.4516 | 69.0702 | 65.6773 | 2.1479 | 2.0551 | 1.4693
20.2209 | 70.2977 | 68.9322 | 65.5303 | 2.1466 | 2.0541 | 1.4682
20.225 | 70.1495 | 68.7981 | 65.3892 | 2.1454 | 2.0531 | 1.467
20.2292 | 70.0054 | 68.6529 | 65.26 | 2.1443 | 2.052 | 1.466
20.2334 | 69.8558 | 68.5065 | 65.1287 | 2.1432 | 2.0509 | 1.465
20.2375 | 69.6937 | 68.3792 | 64.9857 | 2.1421 | 2.0499 | 1.464
20.2417 | 69.5346 | 68.254 | 64.847 | 2.141 | 2.0488 | 1.4629
20.2459 | 69.3969 | 68.1159 | 64.722 | 2.1398 | 2.0479 | 1.4619
20.25 | 69.2586 | 67.9805 | 64.5996 | 2.1387 | 2.0469 | 1.4608
20.2542 | 69.1148 | 67.8506 | 64.4748 | 2.1378 | 2.0459 | 1.4599
20.2584 | 68.9712 | 67.7191 | 64.3492 | 2.1368 | 2.0448 | 1.4591
20.2625 | 68.8217 | 67.5964 | 64.2213 | 2.1357 | 2.0439 | 1.4581
20.2667 | 68.6903 | 67.477 | 64.0978 | 2.1346 | 2.043 | 1.4571
20.2709 | 68.5602 | 67.3435 | 63.9869 | 2.1335 | 2.042 | 1.4562
20.275 | 68.4344 | 67.2111 | 63.8767 | 2.1326 | 2.0411 | 1.4553
20.2792 | 68.2945 | 67.0996 | 63.7559 | 2.1316 | 2.0401 | 1.4544
20.2834 | 68.1515 | 66.9867 | 63.6362 | 2.1306 | 2.0391 | 1.4536
20.2875 | 68.0187 | 66.8572 | 63.5273 | 2.1296 | 2.0383 | 1.4527
20.2917 | 67.8877 | 66.733 | 63.4218 | 2.1286 | 2.0375 | 1.4518
20.2959 | 67.7582 | 66.6119 | 63.3164 | 2.1277 | 2.0365 | 1.451
20.3 | 67.63 | 66.4896 | 63.2109 | 2.1268 | 2.0355 | 1.4502
20.3042 | 67.5027 | 66.3919 | 63.1001 | 2.1259 | 2.0347 | 1.4494
20.3084 | 67.3783 | 66.2936 | 62.9914 | 2.125 | 2.0338 | 1.4486
20.3125 | 67.2651 | 66.1634 | 62.8958 | 2.124 | 2.033 | 1.4478
20.3167 | 67.1512 | 66.0394 | 62.8025 | 2.1231 | 2.0322 | 1.447
20.3209 | 67.0173 | 65.9251 | 62.7021 | 2.1224 | 2.0313 | 1.4463
20.325 | 66.8856 | 65.8083 | 62.6021 | 2.1216 | 2.0304 | 1.4456
20.3292 | 66.7605 | 65.7104 | 62.5063 | 2.1207 | 2.0296 | 1.4448
20.3334 | 66.6441 | 65.6038 | 62.4127 | 2.1198 | 2.0288 | 1.444
20.3375 | 66.5424 | 65.4904 | 62.3203 | 2.119 | 2.0278 | 1.4434
20.3417 | 66.4478 | 65.3761 | 62.2288 | 2.1182 | 2.0268 | 1.4427
20.3459 | 66.3287 | 65.2488 | 62.1377 | 2.1174 | 2.0259 | 1.442
20.35 | 66.2114 | 65.1214 | 62.0482 | 2.1166 | 2.025 | 1.4413
20.3542 | 66.1017 | 64.9919 | 61.9666 | 2.1157 | 2.0241 | 1.4406
20.3584 | 65.9875 | 64.8601 | 61.8873 | 2.1149 | 2.0232 | 1.44
20.3625 | 65.8677 | 64.7621 | 61.7983 | 2.1142 | 2.0223 | 1.4393
20.3667 | 65.7501 | 64.6654 | 61.7165 | 2.1136 | 2.0214 | 1.4388
20.3709 | 65.6453 | 64.5711 | 61.6491 | 2.1127 | 2.0206 | 1.4383
20.375 | 65.5542 | 64.4788 | 61.587 | 2.1118 | 2.0198 | 1.4378
20.3792 | 65.4702 | 64.3413 | 61.5387 | 2.1111 | 2.0191 | 1.4375
20.3834 | 65.3858 | 64.2111 | 61.4919 | 2.1105 | 2.0183 | 1.4372
20.3875 | 65.2728 | 64.1029 | 61.4385 | 2.1097 | 2.0175 | 1.4369
20.3917 | 65.1496 | 63.9953 | 61.3892 | 2.1089 | 2.0167 | 1.4366
20.3959 | 65.0415 | 63.9237 | 61.3464 | 2.1082 | 2.016 | 1.4362
20.4 | 64.9418 | 63.8481 | 61.3014 | 2.1074 | 2.0154 | 1.4358
20.4042 | 64.8338 | 63.7468 | 61.2538 | 2.1069 | 2.0146 | 1.4355
20.4084 | 64.7295 | 63.6504 | 61.2058 | 2.1063 | 2.0139 | 1.4352
20.4125 | 64.6489 | 63.5556 | 61.1572 | 2.1056 | 2.0131 | 1.4348
20.4167 | 64.563 | 63.465 | 61.1096 | 2.1048 | 2.0124 | 1.4344
20.4209 | 64.4849 | 63.3638 | 61.0681 | 2.1042 | 2.0118 | 1.4341
20.425 | 64.4098 | 63.2633 | 61.0248 | 2.1036 | 2.0113 | 1.4337
20.4292 | 64.3081 | 63.1789 | 60.9729 | 2.1028 | 2.0106 | 1.4333
20.4334 | 64.1991 | 63.0943 | 60.9222 | 2.1021 | 2.0098 | 1.433
20.4375 | 64.1082 | 63.024 | 60.8745 | 2.1015 | 2.0093 | 1.4325
20.4417 | 64.0244 | 62.9532 | 60.8267 | 2.1008 | 2.0088 | 1.4321
20.4459 | 63.9173 | 62.8652 | 60.7804 | 2.1002 | 2.0081 | 1.4318
20.45 | 63.8275 | 62.7794 | 60.7335 | 2.0997 | 2.0075 | 1.4315
20.4542 | 63.7312 | 62.7089 | 60.683 | 2.0991 | 2.0068 | 1.4311
20.4584 | 63.645 | 62.6422 | 60.6337 | 2.0984 | 2.0062 | 1.4307
20.4625 | 63.5704 | 62.549 | 60.5913 | 2.0979 | 2.0058 | 1.4304
20.4667 | 63.5047 | 62.458 | 60.5485 | 2.0973 | 2.0053 | 1.43
20.4709 | 63.4286 | 62.3862 | 60.4997 | 2.0968 | 2.0047 | 1.4297
20.475 | 63.3371 | 62.3131 | 60.4512 | 2.0962 | 2.004 | 1.4293
20.4792 | 63.2531 | 62.2568 | 60.4054 | 2.0956 | 2.0036 | 1.4289
20.4834 | 63.1621 | 62.2 | 60.3602 | 2.095 | 2.0032 | 1.4285
20.4875 | 63.0729 | 62.1218 | 60.3153 | 2.0945 | 2.0026 | 1.4282
20.4917 | 62.9946 | 62.0448 | 60.2699 | 2.094 | 2.0021 | 1.4279
20.4959 | 62.9199 | 61.9891 | 60.2185 | 2.0935 | 2.0015 | 1.4275
20.5 | 62.8404 | 61.9357 | 60.1675 | 2.093 | 2.001 | 1.4272
20.5042 | 62.7612 | 61.8602 | 60.1277 | 2.0926 | 2.0006 | 1.4268
20.5084 | 62.6831 | 61.7875 | 60.0881 | 2.0921 | 2.0002 | 1.4264
20.5125 | 62.6105 | 61.7259 | 60.0436 | 2.0915 | 1.9996 | 1.4261
20.5167 | 62.5384 | 61.6642 | 59.9989 | 2.091 | 1.999 | 1.4258
20.5209 | 62.4799 | 61.6065 | 59.9497 | 2.0905 | 1.9987 | 1.4254
20.525 | 62.4059 | 61.5493 | 59.9013 | 2.0901 | 1.9984 | 1.425
20.5292 | 62.315 | 61.4829 | 59.8555 | 2.0897 | 1.9979 | 1.4247
20.5334 | 62.2344 | 61.4157 | 59.8099 | 2.0892 | 1.9974 | 1.4244
20.5375 | 62.1431 | 61.3835 | 59.7692 | 2.0888 | 1.9969 | 1.424
20.5417 | 62.0575 | 61.3507 | 59.728 | 2.0885 | 1.9964 | 1.4237
20.5459 | 61.9893 | 61.284 | 59.6875 | 2.0882 | 1.9961 | 1.4233
20.55 | 61.9118 | 61.2224 | 59.6479 | 2.0879 | 1.9957 | 1.423
20.5542 | 61.8336 | 61.1584 | 59.592 | 2.0877 | 1.9952 | 1.4227
20.5584 | 61.7801 | 61.0973 | 59.5361 | 2.0874 | 1.9946 | 1.4224
20.5625 | 61.7143 | 61.0514 | 59.4949 | 2.0871 | 1.9943 | 1.422
20.5667 | 61.6525 | 61.0054 | 59.4536 | 2.0868 | 1.9941 | 1.4216
20.5709 | 61.5835 | 60.9541 | 59.4228 | 2.0867 | 1.9936 | 1.4213
20.575 | 61.5126 | 60.9024 | 59.3923 | 2.0863 | 1.9932 | 1.421
20.5792 | 61.4377 | 60.8618 | 59.3413 | 2.086 | 1.9929 | 1.4207
20.5834 | 61.3787 | 60.8221 | 59.2903 | 2.0857 | 1.9925 | 1.4204
20.5875 | 61.3343 | 60.76 | 59.2407 | 2.0854 | 1.9922 | 1.42
20.5917 | 61.2658 | 60.7034 | 59.1915 | 2.085 | 1.992 | 1.4197
20.5959 | 61.2169 | 60.6771 | 59.1535 | 2.0847 | 1.9916 | 1.4194
20.6 | 61.1739 | 60.6519 | 59.1153 | 2.0841 | 1.9913 | 1.4191
20.6042 | 61.1268 | 60.6283 | 59.0774 | 2.0836 | 1.9913 | 1.4187
20.6084 | 61.0788 | 60.6072 | 59.0397 | 2.0831 | 1.9912 | 1.4184
20.6125 | 61.0302 | 60.561 | 58.9953 | 2.0826 | 1.991 | 1.4181
20.6167 | 60.9612 | 60.5195 | 58.9514 | 2.0821 | 1.9908 | 1.4178
20.6209 | 60.8887 | 60.5052 | 58.9076 | 2.0815 | 1.9907 | 1.4174
20.625 | 60.8296 | 60.4809 | 58.8637 | 2.081 | 1.9905 | 1.4171
20.6292 | 60.7695 | 60.4504 | 58.8227 | 2.0805 | 1.9905 | 1.4168
20.6334 | 60.7161 | 60.4201 | 58.7822 | 2.08 | 1.9904 | 1.4165
20.6375 | 60.6641 | 60.4016 | 58.7394 | 2.0796 | 1.9901 | 1.4162
20.6417 | 60.5983 | 60.3709 | 58.6965 | 2.0791 | 1.9898 | 1.4159
20.6459 | 60.5501 | 60.3585 | 58.659 | 2.0786 | 1.9897 | 1.4155
20.65 | 60.4979 | 60.3432 | 58.6214 | 2.0781 | 1.9896 | 1.4152
20.6542 | 60.4396 | 60.3125 | 58.5824 | 2.0777 | 1.9893 | 1.4149
20.6584 | 60.3805 | 60.286 | 58.5438 | 2.0774 | 1.9891 | 1.4146
20.6625 | 60.3116 | 60.2639 | 58.4976 | 2.077 | 1.9889 | 1.4143
20.6667 | 60.2399 | 60.2402 | 58.4514 | 2.0766 | 1.9887 | 1.414
20.6709 | 60.1924 | 60.205 | 58.4119 | 2.0762 | 1.9885 | 1.4137
20.675 | 60.1532 | 60.1771 | 58.3728 | 2.0758 | 1.9883 | 1.4133
20.6792 | 60.0955 | 60.1523 | 58.3354 | 2.0756 | 1.988 | 1.4131
20.6834 | 60.0511 | 60.1286 | 58.2979 | 2.0754 | 1.9878 | 1.4128
20.6875 | 60.0033 | 60.1006 | 58.2558 | 2.075 | 1.9877 | 1.4125
20.6917 | 59.9408 | 60.0716 | 58.2139 | 2.0746 | 1.9876 | 1.4122
20.6959 | 59.8941 | 60.0417 | 58.1787 | 2.0744 | 1.9874 | 1.4119
20.7 | 59.8454 | 60.0147 | 58.1435 | 2.0741 | 1.9871 | 1.4115
20.7042 | 59.7597 | 59.997 | 58.1025 | 2.0739 | 1.987 | 1.4113
20.7084 | 59.7023 | 59.9734 | 58.062 | 2.0737 | 1.9869 | 1.411
20.7125 | 59.6724 | 59.9405 | 58.0207 | 2.0734 | 1.9868 | 1.4107
20.7167 | 59.6226 | 59.9085 | 57.9799 | 2.0731 | 1.9866 | 1.4104
20.7209 | 59.6111 | 59.8886 | 57.9422 | 2.0729 | 1.9864 | 1.4101
20.725 | 59.5757 | 59.8692 | 57.9041 | 2.0727 | 1.9862 | 1.4098
20.7292 | 59.5194 | 59.8496 | 57.8658 | 2.0723 | 1.9861 | 1.4095
20.7334 | 59.4805 | 59.8244 | 57.8281 | 2.0719 | 1.986 | 1.4092
20.7375 | 59.4501 | 59.7951 | 57.7918 | 2.0714 | 1.9857 | 1.409
20.7417 | 59.4053 | 59.7709 | 57.7522 | 2.0711 | 1.9855 | 1.4087
20.7459 | 59.3567 | 59.7494 | 57.7098 | 2.0709 | 1.9853 | 1.4083
20.75 | 59.2921 | 59.7282 | 57.6652 | 2.0706 | 1.9852 | 1.408
20.7542 | 59.2327 | 59.6996 | 57.6243 | 2.0702 | 1.985 | 1.4076
20.7584 | 59.1775 | 59.67 | 57.5841 | 2.0699 | 1.9848 | 1.4073
20.7625 | 59.1417 | 59.6417 | 57.5385 | 2.0697 | 1.9847 | 1.407
20.7667 | 59.0973 | 59.6194 | 57.4913 | 2.0696 | 1.9845 | 1.4067
20.7709 | 59.0431 | 59.5961 | 57.4491 | 2.0694 | 1.9844 | 1.4064
20.775 | 59.0066 | 59.5677 | 57.4082 | 2.0692 | 1.9842 | 1.406
20.7792 | 58.9765 | 59.5471 | 57.3688 | 2.0688 | 1.9841 | 1.4057
20.7834 | 58.9538 | 59.5257 | 57.3298 | 2.0686 | 1.9838 | 1.4054
20.7875 | 58.9242 | 59.4979 | 57.2848 | 2.0684 | 1.9837 | 1.4051
20.7917 | 58.8921 | 59.4747 | 57.2393 | 2.0681 | 1.9836 | 1.4048
20.7959 | 58.8471 | 59.4499 | 57.2009 | 2.0677 | 1.9834 | 1.4045
20.8 | 58.8123 | 59.4193 | 57.1641 | 2.0673 | 1.9833 | 1.4042
20.8042 | 58.7849 | 59.4025 | 57.1244 | 2.0669 | 1.9831 | 1.4039
20.8084 | 58.7424 | 59.3881 | 57.0843 | 2.0666 | 1.9829 | 1.4036
20.8125 | 58.6932 | 59.3562 | 57.0432 | 2.0663 | 1.9828 | 1.4033
20.8167 | 58.6531 | 59.3258 | 57.0026 | 2.0659 | 1.9827 | 1.403
20.8209 | 58.6128 | 59.3068 | 56.9644 | 2.0655 | 1.9825 | 1.4027
20.825 | 58.5774 | 59.2839 | 56.9268 | 2.0652 | 1.9822 | 1.4024
20.8292 | 58.5456 | 59.2612 | 56.8875 | 2.065 | 1.9822 | 1.4022
20.8334 | 58.5007 | 59.2434 | 56.8476 | 2.0647 | 1.9821 | 1.4019
20.8375 | 58.4543 | 59.2122 | 56.8092 | 2.0645 | 1.9819 | 1.4016
20.8417 | 58.421 | 59.1775 | 56.7721 | 2.0641 | 1.9817 | 1.4013
20.8459 | 58.3958 | 59.1689 | 56.7362 | 2.0638 | 1.9815 | 1.401
20.85 | 58.3584 | 59.1584 | 56.7001 | 2.0636 | 1.9813 | 1.4007
20.8542 | 58.3263 | 59.1254 | 56.6583 | 2.0634 | 1.9812 | 1.4004
20.8584 | 58.2911 | 59.0976 | 56.6205 | 2.0631 | 1.9812 | 1.4001
20.8625 | 58.2539 | 59.0732 | 56.5849 | 2.0627 | 1.9809 | 1.3998
20.8667 | 58.2754 | 59.0827 | 56.5773 | 2.0621 | 1.9803 | 1.3993
20.8709 | 58.3066 | 59.1428 | 56.5941 | 2.0613 | 1.9796 | 1.3986
20.875 | 58.4317 | 59.2906 | 56.6825 | 2.0598 | 1.9782 | 1.3973
20.8792 | 58.5914 | 59.4953 | 56.8368 | 2.0579 | 1.9761 | 1.3955
20.8834 | 58.778 | 59.7054 | 56.9996 | 2.0552 | 1.9734 | 1.3934
20.8875 | 58.9667 | 59.9434 | 57.1724 | 2.0523 | 1.9701 | 1.3909
20.8917 | 59.0817 | 60.1069 | 57.2983 | 2.0486 | 1.9661 | 1.3879
20.8959 | 59.1641 | 60.1916 | 57.3764 | 2.0447 | 1.9616 | 1.3844
20.9 | 59.2176 | 60.2616 | 57.4491 | 2.0402 | 1.9566 | 1.3807
20.9042 | 59.2644 | 60.3131 | 57.5179 | 2.0354 | 1.9511 | 1.3767
20.9084 | 59.2695 | 60.3174 | 57.5571 | 2.031 | 1.9458 | 1.3729
20.9125 | 59.2567 | 60.2944 | 57.5653 | 2.0267 | 1.9409 | 1.3693
20.9167 | 59.1963 | 60.2389 | 57.5507 | 2.0224 | 1.9361 | 1.3657
20.9209 | 59.1192 | 60.1255 | 57.5142 | 2.0181 | 1.9312 | 1.362
20.925 | 59.0885 | 60.0547 | 57.5068 | 2.014 | 1.9266 | 1.3585
20.9292 | 59.0724 | 60.0479 | 57.5304 | 2.0101 | 1.9221 | 1.3551
20.9334 | 59.0346 | 60.0186 | 57.538 | 2.0067 | 1.918 | 1.352
20.9375 | 58.9994 | 59.9593 | 57.5311 | 2.0034 | 1.9145 | 1.3491
20.9417 | 58.9634 | 59.9143 | 57.5289 | 1.9999 | 1.9109 | 1.346
20.9459 | 58.9342 | 59.8695 | 57.5499 | 1.9964 | 1.9069 | 1.3427
20.95 | 58.95 | 59.8569 | 57.5925 | 1.9932 | 1.9031 | 1.3395
20.9542 | 58.9767 | 59.9022 | 57.6563 | 1.99 | 1.8998 | 1.3364
20.9584 | 58.9537 | 59.9087 | 57.6913 | 1.9869 | 1.8965 | 1.3334
20.9625 | 58.9253 | 59.8511 | 57.6889 | 1.9839 | 1.8933 | 1.3303
20.9667 | 58.9227 | 59.8206 | 57.7008 | 1.9805 | 1.8899 | 1.327
20.9709 | 58.9204 | 59.8309 | 57.7292 | 1.9771 | 1.8861 | 1.3236
20.975 | 58.935 | 59.8409 | 57.7595 | 1.9742 | 1.8827 | 1.3204
20.9792 | 58.9436 | 59.8513 | 57.7808 | 1.9713 | 1.8798 | 1.3175
20.9834 | 58.9082 | 59.8255 | 57.7804 | 1.9682 | 1.8769 | 1.3145
20.9875 | 58.8716 | 59.7565 | 57.7591 | 1.9652 | 1.8736 | 1.3114
20.9917 | 58.8726 | 59.7058 | 57.762 | 1.962 | 1.8704 | 1.3084
20.9959 | 58.8906 | 59.7179 | 57.79 | 1.9589 | 1.8674 | 1.3054
21 | 58.8798 | 59.7071 | 57.8048 | 1.9562 | 1.8647 | 1.3026
21.0042 | 58.8699 | 59.6463 | 57.8034 | 1.9536 | 1.8624 | 1.3
21.0084 | 58.8402 | 59.5971 | 57.7958 | 1.9506 | 1.86 | 1.2972
21.0125 | 58.8126 | 59.5582 | 57.7876 | 1.9476 | 1.8571 | 1.2944
21.0167 | 58.8239 | 59.5474 | 57.7988 | 1.9448 | 1.8545 | 1.2916
21.0209 | 58.8413 | 59.5756 | 57.827 | 1.942 | 1.8524 | 1.289
21.025 | 58.8207 | 59.5824 | 57.8335 | 1.9395 | 1.8503 | 1.2865
21.0292 | 58.7879 | 59.5272 | 57.8204 | 1.9369 | 1.8481 | 1.2841
21.0334 | 58.7739 | 59.4987 | 57.8164 | 1.9341 | 1.8457 | 1.2815
21.0375 | 58.7635 | 59.5176 | 57.8204 | 1.9313 | 1.8431 | 1.2789
21.0417 | 58.7697 | 59.5319 | 57.8308 | 1.9288 | 1.8407 | 1.2764
21.0459 | 58.7772 | 59.5372 | 57.8482 | 1.9264 | 1.8388 | 1.2741
21.05 | 58.7537 | 59.523 | 57.8475 | 1.9239 | 1.8367 | 1.2718
21.0542 | 58.7105 | 59.4781 | 57.8288 | 1.9214 | 1.8343 | 1.2694
21.0584 | 58.7107 | 59.4583 | 57.8268 | 1.9188 | 1.8318 | 1.2671
21.0625 | 58.715 | 59.4875 | 57.839 | 1.9162 | 1.8296 | 1.2647
21.0667 | 58.709 | 59.4954 | 57.8442 | 1.9139 | 1.8274 | 1.2625
21.0709 | 58.7028 | 59.4646 | 57.848 | 1.9117 | 1.8255 | 1.2604
21.075 | 58.6746 | 59.4349 | 57.845 | 1.9093 | 1.8234 | 1.2582
21.0792 | 58.64 | 59.4153 | 57.828 | 1.9069 | 1.821 | 1.256
21.0834 | 58.6403 | 59.4119 | 57.8256 | 1.9046 | 1.8187 | 1.2539
21.0875 | 58.6509 | 59.4275 | 57.8417 | 1.9023 | 1.8168 | 1.2517
21.0917 | 58.6388 | 59.4213 | 57.8437 | 1.9002 | 1.8149 | 1.2497
21.0959 | 58.6188 | 59.3813 | 57.834 | 1.8981 | 1.8129 | 1.2478
21.1 | 58.602 | 59.3564 | 57.8289 | 1.8958 | 1.8108 | 1.2458
21.1042 | 58.589 | 59.3621 | 57.82 | 1.8935 | 1.8086 | 1.2437
21.1084 | 58.5927 | 59.3677 | 57.8171 | 1.8914 | 1.8066 | 1.2417
21.1125 | 58.5994 | 59.3605 | 57.8301 | 1.8893 | 1.8049 | 1.2399
21.1167 | 58.5791 | 59.3405 | 57.8303 | 1.8873 | 1.803 | 1.238
21.1209 | 58.5498 | 59.3127 | 57.8108 | 1.8852 | 1.801 | 1.2362
21.125 | 58.5304 | 59.3018 | 57.8022 | 1.8831 | 1.7989 | 1.2344
21.1292 | 58.5366 | 59.3137 | 57.8044 | 1.8809 | 1.797 | 1.2324
21.1334 | 58.5305 | 59.3145 | 57.8031 | 1.879 | 1.7953 | 1.2306
21.1375 | 58.5218 | 59.2874 | 57.8056 | 1.8771 | 1.7935 | 1.229
21.1417 | 58.5017 | 59.2602 | 57.8021 | 1.8753 | 1.7917 | 1.2273
21.1459 | 58.4729 | 59.2526 | 57.7815 | 1.8731 | 1.7897 | 1.2255
21.15 | 58.4753 | 59.2542 | 57.7712 | 1.8712 | 1.7878 | 1.2238
21.1542 | 58.4857 | 59.2576 | 57.7804 | 1.8692 | 1.7862 | 1.2221
21.1584 | 58.4827 | 59.2475 | 57.7807 | 1.8674 | 1.7845 | 1.2205
21.1625 | 58.4596 | 59.215 | 57.7693 | 1.8657 | 1.7827 | 1.219
21.1667 | 58.4347 | 59.1917 | 57.7599 | 1.8638 | 1.7809 | 1.2174
21.1709 | 58.4131 | 59.1884 | 57.7487 | 1.8618 | 1.7791 | 1.2157
21.175 | 58.4052 | 59.1851 | 57.7426 | 1.86 | 1.7775 | 1.2141
21.1792 | 58.4121 | 59.182 | 57.7484 | 1.8583 | 1.7758 | 1.2127
21.1834 | 58.3993 | 59.1695 | 57.7452 | 1.8566 | 1.7742 | 1.2112
21.1875 | 58.3829 | 59.1533 | 57.724 | 1.8549 | 1.7724 | 1.2098
21.1917 | 58.373 | 59.1524 | 57.7093 | 1.8531 | 1.7707 | 1.2083
21.1959 | 58.3654 | 59.1364 | 57.7113 | 1.8513 | 1.7691 | 1.2068
21.2 | 58.3541 | 59.1245 | 57.7126 | 1.8497 | 1.7675 | 1.2053
21.2042 | 58.3417 | 59.1271 | 57.7077 | 1.8481 | 1.7658 | 1.204
21.2084 | 58.3187 | 59.126 | 57.6979 | 1.8465 | 1.7639 | 1.2027
21.2125 | 58.2947 | 59.1437 | 57.6771 | 1.8448 | 1.7622 | 1.2013
21.2167 | 58.294 | 59.1607 | 57.6627 | 1.8432 | 1.7605 | 1.1999
21.2209 | 58.3062 | 59.1453 | 57.667 | 1.8415 | 1.7587 | 1.1986
21.225 | 58.3154 | 59.124 | 57.6636 | 1.84 | 1.757 | 1.1973
21.2292 | 58.2965 | 59.0925 | 57.6445 | 1.8385 | 1.7553 | 1.1961
21.2334 | 58.2712 | 59.0598 | 57.6191 | 1.837 | 1.7536 | 1.195
21.2375 | 58.2466 | 59.059 | 57.5854 | 1.8353 | 1.7519 | 1.1938
21.2417 | 58.229 | 59.0534 | 57.5541 | 1.8337 | 1.7502 | 1.1928
21.2459 | 58.2265 | 59.0547 | 57.5249 | 1.8324 | 1.7487 | 1.1919
21.25 | 58.2235 | 59.0535 | 57.4955 | 1.831 | 1.7471 | 1.1911
21.2542 | 58.2049 | 59.0245 | 57.4678 | 1.8296 | 1.7456 | 1.1903
21.2584 | 58.1969 | 59.0027 | 57.4455 | 1.828 | 1.744 | 1.1895
21.2625 | 58.2082 | 58.9754 | 57.4348 | 1.8265 | 1.7426 | 1.1888
21.2667 | 58.2171 | 58.9494 | 57.4274 | 1.825 | 1.7412 | 1.188
21.2709 | 58.1949 | 58.9424 | 57.4165 | 1.8237 | 1.7398 | 1.1873
21.275 | 58.166 | 58.9318 | 57.4054 | 1.8224 | 1.7384 | 1.1866
21.2792 | 58.1372 | 58.9348 | 57.3958 | 1.8209 | 1.737 | 1.1859
21.2834 | 58.1159 | 58.9377 | 57.387 | 1.8194 | 1.7356 | 1.1851
21.2875 | 58.121 | 58.9174 | 57.3819 | 1.8182 | 1.7344 | 1.1843
21.2917 | 58.121 | 58.899 | 57.3756 | 1.817 | 1.7331 | 1.1836
21.2959 | 58.1095 | 58.8841 | 57.3639 | 1.8157 | 1.7317 | 1.1828
21.3 | 58.0926 | 58.8699 | 57.352 | 1.8144 | 1.7303 | 1.182
21.3042 | 58.0957 | 58.8569 | 57.3451 | 1.813 | 1.7292 | 1.1812
21.3084 | 58.1013 | 58.8441 | 57.3377 | 1.8116 | 1.7281 | 1.1804
21.3125 | 58.0957 | 58.8223 | 57.326 | 1.8103 | 1.7268 | 1.1796
21.3167 | 58.0805 | 58.7989 | 57.3142 | 1.8092 | 1.7256 | 1.1789
21.3209 | 58.0572 | 58.807 | 57.3002 | 1.8078 | 1.7244 | 1.1781
21.325 | 58.0413 | 58.8129 | 57.2864 | 1.8065 | 1.7232 | 1.1773
21.3292 | 58.0189 | 58.7943 | 57.2797 | 1.8054 | 1.7221 | 1.1765
21.3334 | 58.0159 | 58.7778 | 57.2727 | 1.8043 | 1.7211 | 1.1757
21.3375 | 57.9993 | 58.7598 | 57.258 | 1.8031 | 1.7199 | 1.175
21.3417 | 57.988 | 58.7434 | 57.244 | 1.8019 | 1.7186 | 1.1743
21.3459 | 57.9897 | 58.7344 | 57.2359 | 1.8007 | 1.7177 | 1.1735
21.35 | 57.992 | 58.7253 | 57.2274 | 1.7995 | 1.7168 | 1.1727
21.3542 | 57.9818 | 58.7025 | 57.2208 | 1.7985 | 1.7157 | 1.172
21.3584 | 57.9619 | 58.679 | 57.2144 | 1.7974 | 1.7146 | 1.1712
21.3625 | 57.9481 | 58.6849 | 57.2003 | 1.7962 | 1.7136 | 1.1705
21.3667 | 57.9339 | 58.6888 | 57.1866 | 1.795 | 1.7126 | 1.1697
21.3709 | 57.9297 | 58.6682 | 57.1782 | 1.794 | 1.7117 | 1.169
21.375 | 57.9272 | 58.6485 | 57.1693 | 1.793 | 1.7109 | 1.1682
21.3792 | 57.9057 | 58.6384 | 57.1573 | 1.792 | 1.7097 | 1.1675
21.3834 | 57.8828 | 58.6289 | 57.1456 | 1.7909 | 1.7086 | 1.1668
21.3875 | 57.8736 | 58.6268 | 57.1417 | 1.7899 | 1.7078 | 1.166
21.3917 | 57.8664 | 58.625 | 57.1375 | 1.7888 | 1.707 | 1.1653
21.3959 | 57.8756 | 58.5918 | 57.1277 | 1.7879 | 1.7061 | 1.1646
21.4 | 57.8723 | 58.5603 | 57.1179 | 1.7869 | 1.7052 | 1.1639
21.4042 | 57.8569 | 58.5593 | 57.0984 | 1.786 | 1.7043 | 1.1632
21.4084 | 57.8428 | 58.5563 | 57.0797 | 1.7849 | 1.7034 | 1.1624
21.4125 | 57.8206 | 58.5484 | 57.0813 | 1.784 | 1.7027 | 1.1617
21.4167 | 57.8032 | 58.5383 | 57.0823 | 1.783 | 1.7019 | 1.161
21.4209 | 57.7882 | 58.532 | 57.0758 | 1.7822 | 1.7009 | 1.1603
21.425 | 57.7631 | 58.5267 | 57.0693 | 1.7814 | 1.7 | 1.1596
21.4292 | 57.7479 | 58.5127 | 57.05 | 1.7806 | 1.6993 | 1.1589
21.4334 | 57.7375 | 58.5016 | 57.0314 | 1.7798 | 1.6986 | 1.1582
21.4375 | 57.7314 | 58.4734 | 57.0229 | 1.779 | 1.6978 | 1.1575
21.4417 | 57.7339 | 58.4459 | 57.0139 | 1.7782 | 1.697 | 1.1568
21.4459 | 57.7266 | 58.4537 | 57.0119 | 1.7775 | 1.6962 | 1.1561
21.45 | 57.7215 | 58.4588 | 57.01 | 1.7766 | 1.6954 | 1.1554
21.4542 | 57.707 | 58.4342 | 57.0042 | 1.7759 | 1.6949 | 1.1547
21.4584 | 57.704 | 58.4079 | 56.9987 | 1.775 | 1.6943 | 1.154
21.4625 | 57.6949 | 58.377 | 56.9814 | 1.7743 | 1.6936 | 1.1533
21.4667 | 57.6847 | 58.3455 | 56.9637 | 1.7735 | 1.6929 | 1.1527
21.4709 | 57.6887 | 58.3317 | 56.9559 | 1.7727 | 1.6925 | 1.1519
21.475 | 57.6842 | 58.3192 | 56.9485 | 1.7717 | 1.6922 | 1.1512
21.4792 | 57.6869 | 58.2959 | 56.945 | 1.7709 | 1.6917 | 1.1506
21.4834 | 57.6966 | 58.2771 | 56.9414 | 1.77 | 1.6913 | 1.15
21.4875 | 57.7038 | 58.2694 | 56.9303 | 1.769 | 1.6909 | 1.1493
21.4917 | 57.6886 | 58.2677 | 56.9189 | 1.7681 | 1.6905 | 1.1486
21.4959 | 57.6868 | 58.249 | 56.9136 | 1.7672 | 1.6902 | 1.1479
21.5 | 57.6758 | 58.233 | 56.9088 | 1.7662 | 1.6899 | 1.1472
21.5042 | 57.6482 | 58.2266 | 56.8992 | 1.7653 | 1.6894 | 1.1466
21.5084 | 57.6444 | 58.2191 | 56.8893 | 1.7644 | 1.6889 | 1.146
21.5125 | 57.6407 | 58.2137 | 56.8771 | 1.7635 | 1.6887 | 1.1453
21.5167 | 57.6205 | 58.204 | 56.8652 | 1.7627 | 1.6884 | 1.1446
21.5209 | 57.6205 | 58.1955 | 56.862 | 1.7619 | 1.6879 | 1.144
21.525 | 57.6194 | 58.1783 | 56.859 | 1.761 | 1.6874 | 1.1433
21.5292 | 57.6023 | 58.1859 | 56.8522 | 1.7602 | 1.687 | 1.1427
21.5334 | 57.5937 | 58.1921 | 56.8449 | 1.7594 | 1.6866 | 1.1421
21.5375 | 57.5892 | 58.1723 | 56.8343 | 1.7586 | 1.6862 | 1.1414
21.5417 | 57.5619 | 58.1547 | 56.8244 | 1.7578 | 1.6859 | 1.1407
21.5459 | 57.5408 | 58.1474 | 56.8178 | 1.7572 | 1.6853 | 1.1401
21.55 | 57.536 | 58.1398 | 56.8108 | 1.7565 | 1.6847 | 1.1395
21.5542 | 57.5171 | 58.1304 | 56.8013 | 1.7557 | 1.6844 | 1.1389
21.5584 | 57.5159 | 58.1274 | 56.792 | 1.7551 | 1.6841 | 1.1382
21.5625 | 57.5272 | 58.1043 | 56.7851 | 1.7544 | 1.6836 | 1.1376
21.5667 | 57.5152 | 58.083 | 56.7785 | 1.7537 | 1.6832 | 1.137
21.5709 | 57.5065 | 58.0826 | 56.7719 | 1.7531 | 1.6828 | 1.1364
21.575 | 57.5001 | 58.0809 | 56.7646 | 1.7524 | 1.6824 | 1.1358
21.5792 | 57.4717 | 58.0661 | 56.7589 | 1.7518 | 1.682 | 1.1351
21.5834 | 57.4635 | 58.053 | 56.7539 | 1.7511 | 1.6817 | 1.1345
21.5875 | 57.4521 | 58.0429 | 56.745 | 1.7506 | 1.6813 | 1.1339
21.5917 | 57.4319 | 58.029 | 56.7361 | 1.75 | 1.6808 | 1.1333
21.5959 | 57.4399 | 58.0245 | 56.7267 | 1.7494 | 1.6805 | 1.1327
21.6 | 57.4331 | 58.0198 | 56.7185 | 1.7488 | 1.6802 | 1.132
21.6042 | 57.4369 | 58.0087 | 56.7155 | 1.7482 | 1.6798 | 1.1314
21.6084 | 57.4438 | 57.9971 | 56.7161 | 1.7476 | 1.6794 | 1.1308
21.6125 | 57.4348 | 57.9939 | 56.7102 | 1.7469 | 1.679 | 1.1302
21.6167 | 57.4304 | 57.9878 | 56.7047 | 1.7463 | 1.6786 | 1.1296
21.6209 | 57.4328 | 57.9774 | 56.7057 | 1.7455 | 1.6783 | 1.1289
21.625 | 57.4265 | 57.9703 | 56.7043 | 1.7448 | 1.6779 | 1.1282
21.6292 | 57.4136 | 57.9629 | 56.6996 | 1.7442 | 1.6775 | 1.1276
21.6334 | 57.3936 | 57.9554 | 56.6946 | 1.7437 | 1.6771 | 1.1269
21.6375 | 57.3722 | 57.942 | 56.6861 | 1.743 | 1.6767 | 1.1262
21.6417 | 57.3521 | 57.9304 | 56.6765 | 1.7424 | 1.6764 | 1.1255
21.6459 | 57.353 | 57.919 | 56.6727 | 1.7418 | 1.676 | 1.1249
21.65 | 57.3469 | 57.9098 | 56.6678 | 1.7414 | 1.6756 | 1.1243
21.6542 | 57.3315 | 57.9081 | 56.6592 | 1.7409 | 1.6752 | 1.1236
21.6584 | 57.3246 | 57.902 | 56.6521 | 1.7405 | 1.6749 | 1.123
21.6625 | 57.3219 | 57.887 | 56.6459 | 1.7398 | 1.6746 | 1.1224
21.6667 | 57.3348 | 57.8743 | 56.6391 | 1.7392 | 1.6742 | 1.1217
21.6709 | 57.3414 | 57.8694 | 56.6325 | 1.7387 | 1.6738 | 1.1211
21.675 | 57.3446 | 57.8647 | 56.6256 | 1.7382 | 1.6734 | 1.1205
21.6792 | 57.3263 | 57.8587 | 56.6197 | 1.7375 | 1.6731 | 1.1199
21.6834 | 57.3175 | 57.8487 | 56.6153 | 1.7369 | 1.6728 | 1.1193
21.6875 | 57.3178 | 57.837 | 56.6099 | 1.7362 | 1.6724 | 1.1187
21.6917 | 57.318 | 57.8289 | 56.6035 | 1.7355 | 1.672 | 1.1181
21.6959 | 57.3066 | 57.8264 | 56.5965 | 1.7351 | 1.6716 | 1.1175
21.7 | 57.2897 | 57.822 | 56.5895 | 1.7345 | 1.6713 | 1.1169
21.7042 | 57.2724 | 57.8074 | 56.5831 | 1.7339 | 1.671 | 1.1163
21.7084 | 57.2614 | 57.7901 | 56.5763 | 1.7333 | 1.6707 | 1.1157
21.7125 | 57.2589 | 57.7786 | 56.5686 | 1.7328 | 1.6703 | 1.1152
21.7167 | 57.2625 | 57.7822 | 56.5671 | 1.7323 | 1.6699 | 1.1145
21.7209 | 57.2593 | 57.7958 | 56.5796 | 1.7317 | 1.6694 | 1.1138
21.725 | 57.2749 | 57.8175 | 56.6004 | 1.731 | 1.6689 | 1.1131
21.7292 | 57.3136 | 57.8513 | 56.6299 | 1.7301 | 1.6683 | 1.1123
21.7334 | 57.3148 | 57.8572 | 56.6364 | 1.7295 | 1.6677 | 1.1115
21.7375 | 57.305 | 57.8359 | 56.6201 | 1.729 | 1.6672 | 1.1108
21.7417 | 57.2891 | 57.8187 | 56.5992 | 1.7282 | 1.6666 | 1.1101
21.7459 | 57.2584 | 57.7956 | 56.577 | 1.7272 | 1.6658 | 1.1092
21.75 | 57.3265 | 57.843 | 56.6082 | 1.726 | 1.6646 | 1.1081
21.7542 | 57.433 | 57.9735 | 56.6857 | 1.7246 | 1.6632 | 1.1069
21.7584 | 57.5684 | 58.1381 | 56.7864 | 1.7228 | 1.6613 | 1.1055
21.7625 | 57.7083 | 58.3165 | 56.9075 | 1.721 | 1.6592 | 1.1038
21.7667 | 57.8443 | 58.4803 | 57.0196 | 1.7182 | 1.6563 | 1.1017
21.7709 | 57.9712 | 58.6381 | 57.1266 | 1.715 | 1.6526 | 1.0992
21.775 | 58.0897 | 58.7759 | 57.2309 | 1.7114 | 1.6485 | 1.0964
21.7792 | 58.207 | 58.9079 | 57.3274 | 1.7077 | 1.644 | 1.0934
21.7834 | 58.2518 | 58.9908 | 57.3933 | 1.7038 | 1.6395 | 1.0904
21.7875 | 58.2688 | 59.0026 | 57.4323 | 1.6998 | 1.6348 | 1.0872
21.7917 | 58.2618 | 58.9755 | 57.4495 | 1.6957 | 1.6301 | 1.0841
21.7959 | 58.2391 | 58.9356 | 57.4503 | 1.6916 | 1.6253 | 1.0809
21.8 | 58.2112 | 58.8959 | 57.4558 | 1.688 | 1.6208 | 1.0779
21.8042 | 58.1816 | 58.8445 | 57.4566 | 1.6845 | 1.6168 | 1.0751
21.8084 | 58.139 | 58.7932 | 57.4525 | 1.6812 | 1.6131 | 1.0724
21.8125 | 58.0974 | 58.7352 | 57.448 | 1.678 | 1.6095 | 1.0698
21.8167 | 58.0766 | 58.6838 | 57.4475 | 1.675 | 1.606 | 1.0672
21.8209 | 58.0675 | 58.6579 | 57.4586 | 1.6721 | 1.6028 | 1.0647
21.825 | 58.0651 | 58.6565 | 57.4823 | 1.6694 | 1.5998 | 1.0623
21.8292 | 58.0704 | 58.6511 | 57.5224 | 1.6667 | 1.5968 | 1.0598
21.8334 | 58.0783 | 58.6438 | 57.5583 | 1.664 | 1.594 | 1.0573
21.8375 | 58.0925 | 58.6603 | 57.5934 | 1.6613 | 1.5911 | 1.0549
21.8417 | 58.1054 | 58.6686 | 57.6258 | 1.6587 | 1.5881 | 1.0524
21.8459 | 58.1202 | 58.6656 | 57.6484 | 1.6561 | 1.5854 | 1.0498
21.85 | 58.1392 | 58.6833 | 57.6767 | 1.6534 | 1.5827 | 1.0473
21.8542 | 58.1489 | 58.6974 | 57.7106 | 1.6507 | 1.5797 | 1.0447
21.8584 | 58.1608 | 58.6955 | 57.7354 | 1.6481 | 1.5768 | 1.0421
21.8625 | 58.1699 | 58.7106 | 57.7447 | 1.6455 | 1.5742 | 1.0397
21.8667 | 58.166 | 58.7062 | 57.7533 | 1.6428 | 1.5715 | 1.0373
21.8709 | 58.168 | 58.6725 | 57.7591 | 1.6403 | 1.5688 | 1.0348
21.875 | 58.1775 | 58.6495 | 57.7729 | 1.6376 | 1.5663 | 1.0323
21.8792 | 58.1924 | 58.6498 | 57.799 | 1.635 | 1.5637 | 1.03
21.8834 | 58.1876 | 58.6318 | 57.8136 | 1.6326 | 1.5613 | 1.0278
21.8875 | 58.1907 | 58.6038 | 57.8112 | 1.6302 | 1.5593 | 1.0256
21.8917 | 58.1862 | 58.5894 | 57.8147 | 1.6277 | 1.5572 | 1.0234
21.8959 | 58.187 | 58.5667 | 57.8317 | 1.6252 | 1.5548 | 1.0211
21.9 | 58.2029 | 58.5631 | 57.8531 | 1.6229 | 1.5527 | 1.0189
21.9042 | 58.2155 | 58.5896 | 57.8763 | 1.6205 | 1.5508 | 1.0168
21.9084 | 58.206 | 58.6022 | 57.886 | 1.6182 | 1.5488 | 1.0148
21.9125 | 58.197 | 58.5754 | 57.8804 | 1.6159 | 1.5469 | 1.0127
21.9167 | 58.2029 | 58.5724 | 57.8876 | 1.6136 | 1.5449 | 1.0106
21.9209 | 58.2143 | 58.5967 | 57.9144 | 1.6112 | 1.5426 | 1.0085
21.925 | 58.2232 | 58.6118 | 57.9369 | 1.6091 | 1.5405 | 1.0065
21.9292 | 58.229 | 58.6277 | 57.9459 | 1.607 | 1.5388 | 1.0047
21.9334 | 58.2178 | 58.6304 | 57.9462 | 1.6048 | 1.5368 | 1.0027
21.9375 | 58.2031 | 58.5992 | 57.9438 | 1.6025 | 1.5347 | 1.0007
21.9417 | 58.2204 | 58.5895 | 57.9568 | 1.6003 | 1.5326 | 0.99869
21.9459 | 58.2423 | 58.6302 | 57.9848 | 1.5982 | 1.5305 | 0.9968
21.95 | 58.2387 | 58.6448 | 57.9995 | 1.5962 | 1.5285 | 0.99502
21.9542 | 58.2316 | 58.6209 | 57.9961 | 1.5943 | 1.5269 | 0.99327
21.9584 | 58.2231 | 58.606 | 57.9941 | 1.5921 | 1.5251 | 0.99143
21.9625 | 58.2121 | 58.5938 | 58.0007 | 1.59 | 1.5228 | 0.9895
21.9667 | 58.2282 | 58.5943 | 58.0179 | 1.588 | 1.5208 | 0.98769
21.9709 | 58.2528 | 58.6302 | 58.0397 | 1.5861 | 1.5191 | 0.98601
21.975 | 58.2388 | 58.64 | 58.0449 | 1.5842 | 1.5174 | 0.98436
21.9792 | 58.2268 | 58.5961 | 58.036 | 1.5824 | 1.5156 | 0.98267
21.9834 | 58.2335 | 58.5776 | 58.0386 | 1.5803 | 1.5138 | 0.98091
21.9875 | 58.2383 | 58.5991 | 58.0537 | 1.5783 | 1.5117 | 0.97914
21.9917 | 58.2516 | 58.6125 | 58.0686 | 1.5765 | 1.5099 | 0.97752
21.9959 | 58.2659 | 58.624 | 58.0801 | 1.5748 | 1.5085 | 0.976
22 | 58.2492 | 58.6218 | 58.0797 | 1.5729 | 1.5069 | 0.97442
22.0042 | 58.2331 | 58.5854 | 58.0714 | 1.571 | 1.505 | 0.97279
22.0084 | 58.2404 | 58.5757 | 58.0789 | 1.5692 | 1.5031 | 0.97117
22.0125 | 58.2574 | 58.613 | 58.0987 | 1.5672 | 1.5014 | 0.96957
22.0167 | 58.254 | 58.6274 | 58.1077 | 1.5656 | 1.4997 | 0.96809
22.0209 | 58.248 | 58.606 | 58.1092 | 1.564 | 1.4983 | 0.96668
22.025 | 58.2412 | 58.5905 | 58.1091 | 1.5623 | 1.4967 | 0.96516
22.0292 | 58.2317 | 58.5896 | 58.1046 | 1.5604 | 1.4947 | 0.96361
22.0334 | 58.256 | 58.601 | 58.1119 | 1.5586 | 1.4929 | 0.96215
22.0375 | 58.2791 | 58.6271 | 58.1318 | 1.557 | 1.4915 | 0.96071
22.0417 | 58.2708 | 58.631 | 58.1367 | 1.5554 | 1.4901 | 0.9593
22.0459 | 58.2462 | 58.584 | 58.1308 | 1.5539 | 1.4885 | 0.95797
22.05 | 58.2336 | 58.559 | 58.134 | 1.5521 | 1.4869 | 0.95657
22.0542 | 58.2363 | 58.596 | 58.1364 | 1.5503 | 1.485 | 0.95509
22.0584 | 58.2458 | 58.6223 | 58.1406 | 1.5488 | 1.4833 | 0.95374
22.0625 | 58.2678 | 58.6284 | 58.1546 | 1.5473 | 1.4821 | 0.95247
22.0667 | 58.2579 | 58.6236 | 58.1568 | 1.5458 | 1.4808 | 0.95115
22.0709 | 58.2436 | 58.5792 | 58.1463 | 1.5442 | 1.479 | 0.94986
22.075 | 58.2477 | 58.5665 | 58.1487 | 1.5426 | 1.4773 | 0.94858
22.0792 | 58.2558 | 58.6009 | 58.1612 | 1.541 | 1.4758 | 0.94721
22.0834 | 58.2439 | 58.6177 | 58.1653 | 1.5397 | 1.4743 | 0.94595
22.0875 | 58.2409 | 58.6246 | 58.1625 | 1.5383 | 1.4729 | 0.94487
22.0917 | 58.2303 | 58.6324 | 58.1585 | 1.5368 | 1.4713 | 0.94371
22.0959 | 58.2202 | 58.6374 | 58.1486 | 1.5352 | 1.4695 | 0.94242
22.1 | 58.2457 | 58.6543 | 58.15 | 1.5338 | 1.4678 | 0.94121
22.1042 | 58.2697 | 58.6559 | 58.1735 | 1.5323 | 1.4664 | 0.94004
22.1084 | 58.2673 | 58.6349 | 58.18 | 1.5309 | 1.4649 | 0.93894
22.1125 | 58.2509 | 58.6075 | 58.1607 | 1.5296 | 1.4633 | 0.93797
22.1167 | 58.2417 | 58.5898 | 58.1446 | 1.5282 | 1.4617 | 0.93696
22.1209 | 58.2224 | 58.6163 | 58.1264 | 1.5267 | 1.4601 | 0.93584
22.125 | 58.2223 | 58.6364 | 58.1125 | 1.5254 | 1.4586 | 0.93486
22.1292 | 58.2409 | 58.6331 | 58.1127 | 1.5241 | 1.4573 | 0.93409
22.1334 | 58.24 | 58.6216 | 58.1035 | 1.5228 | 1.456 | 0.93332
22.1375 | 58.2272 | 58.582 | 58.0793 | 1.5215 | 1.4545 | 0.93256
22.1417 | 58.2382 | 58.5631 | 58.0694 | 1.5202 | 1.4531 | 0.93179
22.1459 | 58.2508 | 58.5798 | 58.0779 | 1.5187 | 1.4517 | 0.93095
22.15 | 58.2552 | 58.5838 | 58.0846 | 1.5173 | 1.4504 | 0.9302
22.1542 | 58.2519 | 58.5744 | 58.0899 | 1.5163 | 1.4494 | 0.92958
22.1584 | 58.234 | 58.5651 | 58.0912 | 1.515 | 1.4482 | 0.92887
22.1625 | 58.2108 | 58.5607 | 58.0828 | 1.5137 | 1.4467 | 0.92803
22.1667 | 58.2041 | 58.5655 | 58.0837 | 1.5124 | 1.4454 | 0.92722
22.1709 | 58.2283 | 58.5819 | 58.1011 | 1.5112 | 1.4443 | 0.92641
22.175 | 58.2315 | 58.586 | 58.109 | 1.5101 | 1.4432 | 0.92563
22.1792 | 58.2205 | 58.5566 | 58.1045 | 1.509 | 1.442 | 0.92491
22.1834 | 58.2109 | 58.5376 | 58.102 | 1.5079 | 1.4408 | 0.92412
22.1875 | 58.2216 | 58.5414 | 58.0996 | 1.5064 | 1.4395 | 0.92321
22.1917 | 58.2354 | 58.5442 | 58.1008 | 1.5052 | 1.4384 | 0.92237
22.1959 | 58.2506 | 58.5448 | 58.1099 | 1.5041 | 1.4374 | 0.92163
22.2 | 58.2438 | 58.536 | 58.1116 | 1.5031 | 1.4365 | 0.92086
22.2042 | 58.2081 | 58.5283 | 58.1 | 1.5019 | 1.4352 | 0.92008
22.2084 | 58.1922 | 58.5297 | 58.0949 | 1.5007 | 1.434 | 0.91929
22.2125 | 58.198 | 58.5392 | 58.0993 | 1.4995 | 1.433 | 0.91845
22.2167 | 58.215 | 58.5439 | 58.1019 | 1.4984 | 1.4321 | 0.91766
22.2209 | 58.2129 | 58.5219 | 58.1023 | 1.4975 | 1.4311 | 0.91698
22.225 | 58.2029 | 58.5009 | 58.0999 | 1.4965 | 1.43 | 0.91626
22.2292 | 58.1892 | 58.5041 | 58.0947 | 1.4954 | 1.4289 | 0.91543
22.2334 | 58.1893 | 58.5122 | 58.0947 | 1.4941 | 1.4279 | 0.91463
22.2375 | 58.2055 | 58.5097 | 58.106 | 1.4931 | 1.4271 | 0.91387
22.2417 | 58.2085 | 58.4997 | 58.1129 | 1.4922 | 1.4263 | 0.91312
22.2459 | 58.2005 | 58.4888 | 58.1022 | 1.4913 | 1.4252 | 0.91244
22.25 | 58.1894 | 58.4812 | 58.0931 | 1.4901 | 1.4241 | 0.91172
22.2542 | 58.178 | 58.4902 | 58.0921 | 1.4891 | 1.4233 | 0.91088
22.2584 | 58.184 | 58.499 | 58.093 | 1.4881 | 1.4224 | 0.91008
22.2625 | 58.1819 | 58.4915 | 58.1046 | 1.4873 | 1.4215 | 0.90939
22.2667 | 58.1639 | 58.4804 | 58.1124 | 1.4864 | 1.4206 | 0.90869
22.2709 | 58.1641 | 58.4783 | 58.1036 | 1.4854 | 1.4197 | 0.90795
22.275 | 58.1629 | 58.4827 | 58.098 | 1.4844 | 1.4187 | 0.9072
22.2792 | 58.1745 | 58.4653 | 58.0964 | 1.4834 | 1.418 | 0.90644
22.2834 | 58.1864 | 58.4464 | 58.094 | 1.4826 | 1.4173 | 0.90571
22.2875 | 58.1772 | 58.4479 | 58.0956 | 1.4817 | 1.4164 | 0.90503
22.2917 | 58.1594 | 58.4459 | 58.0955 | 1.4808 | 1.4154 | 0.90433
22.2959 | 58.1476 | 58.4584 | 58.1009 | 1.4799 | 1.4147 | 0.90355
22.3 | 58.1432 | 58.4725 | 58.1088 | 1.479 | 1.414 | 0.90278
22.3042 | 58.1375 | 58.4519 | 58.107 | 1.4782 | 1.4132 | 0.90211
22.3084 | 58.1277 | 58.43 | 58.1035 | 1.4775 | 1.4124 | 0.90145
22.3125 | 58.1158 | 58.4283 | 58.0918 | 1.4768 | 1.4116 | 0.90073
22.3167 | 58.1073 | 58.4295 | 58.0806 | 1.476 | 1.4107 | 0.9
22.3209 | 58.1142 | 58.4245 | 58.0909 | 1.4752 | 1.4101 | 0.89926
22.325 | 58.1321 | 58.4201 | 58.102 | 1.4744 | 1.4095 | 0.89854
22.3292 | 58.1289 | 58.417 | 58.1041 | 1.4738 | 1.4087 | 0.8979
22.3334 | 58.1264 | 58.4105 | 58.1047 | 1.473 | 1.4079 | 0.89726
22.3375 | 58.1198 | 58.3995 | 58.0978 | 1.4722 | 1.4074 | 0.89651
22.3417 | 58.115 | 58.3898 | 58.0923 | 1.4713 | 1.4068 | 0.89575
22.3459 | 58.1213 | 58.3652 | 58.0955 | 1.4706 | 1.4062 | 0.89508
22.35 | 58.1293 | 58.3384 | 58.0983 | 1.4698 | 1.4057 | 0.89442
22.3542 | 58.1269 | 58.3407 | 58.095 | 1.4691 | 1.4052 | 0.89376
22.3584 | 58.1254 | 58.3437 | 58.091 | 1.4682 | 1.4046 | 0.89308
22.3625 | 58.1427 | 58.3255 | 58.0915 | 1.4673 | 1.4043 | 0.89238
22.3667 | 58.1489 | 58.3131 | 58.0931 | 1.4664 | 1.404 | 0.89169
22.3709 | 58.1592 | 58.3096 | 58.0967 | 1.4656 | 1.4035 | 0.89103
22.375 | 58.157 | 58.3073 | 58.099 | 1.4647 | 1.4029 | 0.89037
22.3792 | 58.1397 | 58.3114 | 58.0963 | 1.4638 | 1.4027 | 0.8897
22.3834 | 58.1309 | 58.3203 | 58.094 | 1.4629 | 1.4023 | 0.88902
22.3875 | 58.1277 | 58.3039 | 58.0919 | 1.4621 | 1.4019 | 0.88835
22.3917 | 58.1235 | 58.2864 | 58.0904 | 1.4613 | 1.4014 | 0.88769
22.3959 | 58.1227 | 58.3008 | 58.0905 | 1.4605 | 1.401 | 0.88704
22.4 | 58.1158 | 58.307 | 58.0895 | 1.4597 | 1.4005 | 0.88639
22.4042 | 58.1111 | 58.3056 | 58.0906 | 1.4589 | 1.4001 | 0.88573
22.4084 | 58.1161 | 58.3023 | 58.0927 | 1.4581 | 1.3998 | 0.88507
22.4125 | 58.1211 | 58.3 | 58.0927 | 1.4573 | 1.3992 | 0.88442
22.4167 | 58.1091 | 58.2945 | 58.0921 | 1.4567 | 1.3986 | 0.88379
22.4209 | 58.0971 | 58.2994 | 58.0901 | 1.456 | 1.3982 | 0.88314
22.425 | 58.0833 | 58.3038 | 58.0878 | 1.4553 | 1.3978 | 0.88249
22.4292 | 58.0611 | 58.2905 | 58.0892 | 1.4546 | 1.3973 | 0.88184
22.4334 | 58.0709 | 58.2817 | 58.0913 | 1.4539 | 1.3968 | 0.88119
22.4375 | 58.0793 | 58.2793 | 58.0873 | 1.4533 | 1.3964 | 0.8806
22.4417 | 58.0679 | 58.2793 | 58.0826 | 1.4527 | 1.3959 | 0.88
22.4459 | 58.0788 | 58.27 | 58.0831 | 1.4521 | 1.3955 | 0.87933
22.45 | 58.0786 | 58.263 | 58.0845 | 1.4513 | 1.3951 | 0.87866
22.4542 | 58.0592 | 58.2606 | 58.0878 | 1.4507 | 1.3946 | 0.87807
22.4584 | 58.0696 | 58.258 | 58.0915 | 1.4501 | 1.3941 | 0.87749
22.4625 | 58.0583 | 58.2552 | 58.0881 | 1.4495 | 1.3938 | 0.87684
22.4667 | 58.0383 | 58.2514 | 58.0835 | 1.4489 | 1.3934 | 0.8762
22.4709 | 58.045 | 58.2441 | 58.0855 | 1.4484 | 1.393 | 0.87557
22.475 | 58.0395 | 58.2354 | 58.0876 | 1.4477 | 1.3925 | 0.87494
22.4792 | 58.0381 | 58.2404 | 58.0844 | 1.4472 | 1.3921 | 0.87436
22.4834 | 58.0394 | 58.2436 | 58.0834 | 1.4467 | 1.3917 | 0.87376
22.4875 | 58.0466 | 58.2354 | 58.0839 | 1.446 | 1.3914 | 0.87311
22.4917 | 58.0447 | 58.2265 | 58.086 | 1.4454 | 1.391 | 0.87245
22.4959 | 58.0545 | 58.2289 | 58.0909 | 1.4448 | 1.3905 | 0.87185
22.5 | 58.0611 | 58.2297 | 58.0951 | 1.4442 | 1.39 | 0.87124
22.5042 | 58.0546 | 58.2306 | 58.0965 | 1.4435 | 1.3897 | 0.87058
22.5084 | 58.0489 | 58.2329 | 58.0973 | 1.4429 | 1.3893 | 0.8699
22.5125 | 58.0445 | 58.2195 | 58.0988 | 1.4422 | 1.3889 | 0.86926
22.5167 | 58.0341 | 58.2088 | 58.0991 | 1.4416 | 1.3884 | 0.86862
22.5209 | 58.0243 | 58.2106 | 58.098 | 1.4411 | 1.388 | 0.86797
22.525 | 58.0136 | 58.2128 | 58.0953 | 1.4406 | 1.3876 | 0.86732
22.5292 | 58.0049 | 58.2067 | 58.096 | 1.44 | 1.3872 | 0.86668
22.5334 | 57.9992 | 58.2008 | 58.0972 | 1.4395 | 1.3869 | 0.86604
22.5375 | 57.9985 | 58.1965 | 58.0945 | 1.439 | 1.3864 | 0.86543
22.5417 | 58.0038 | 58.1917 | 58.0919 | 1.4385 | 1.386 | 0.86483
22.5459 | 58.0025 | 58.1918 | 58.0908 | 1.438 | 1.3857 | 0.8642
22.55 | 58.0107 | 58.1916 | 58.0892 | 1.4374 | 1.3853 | 0.86357
22.5542 | 58.0155 | 58.1845 | 58.0892 | 1.4368 | 1.3849 | 0.86299
22.5584 | 58.02 | 58.1759 | 58.0899 | 1.4363 | 1.3845 | 0.86241
22.5625 | 58.0131 | 58.1759 | 58.0876 | 1.4358 | 1.3841 | 0.86181
22.5667 | 58.0173 | 58.1796 | 58.0884 | 1.4351 | 1.3837 | 0.86119
22.5709 | 58.0206 | 58.1833 | 58.0958 | 1.4344 | 1.3833 | 0.86055
22.575 | 58.0236 | 58.1865 | 58.1019 | 1.4338 | 1.3829 | 0.85993
22.5792 | 58.0281 | 58.189 | 58.104 | 1.4333 | 1.3825 | 0.85933
22.5834 | 58.0047 | 58.1758 | 58.0958 | 1.4328 | 1.3821 | 0.85879
22.5875 | 57.9719 | 58.1462 | 58.0766 | 1.4323 | 1.3818 | 0.85826
22.5917 | 57.964 | 58.1344 | 58.0679 | 1.4317 | 1.3815 | 0.85766
22.5959 | 57.9707 | 58.1391 | 58.0747 | 1.4311 | 1.3809 | 0.857
22.6 | 58.0048 | 58.174 | 58.1034 | 1.4304 | 1.3803 | 0.85628
22.6042 | 58.057 | 58.2442 | 58.153 | 1.4298 | 1.3797 | 0.85549
22.6084 | 58.073 | 58.2874 | 58.1843 | 1.4291 | 1.3791 | 0.85472
22.6125 | 58.0884 | 58.295 | 58.1989 | 1.4283 | 1.3784 | 0.85392
22.6167 | 58.0839 | 58.2825 | 58.1935 | 1.4274 | 1.3776 | 0.85307
22.6209 | 58.0711 | 58.2597 | 58.1721 | 1.4265 | 1.3766 | 0.85214
22.625 | 58.0838 | 58.2704 | 58.1727 | 1.4255 | 1.3755 | 0.85118
22.6292 | 58.104 | 58.3099 | 58.19 | 1.4244 | 1.3745 | 0.85019
22.6334 | 58.1676 | 58.3834 | 58.2291 | 1.4231 | 1.3732 | 0.84913
22.6375 | 58.2516 | 58.4822 | 58.2888 | 1.4216 | 1.3716 | 0.84795
22.6417 | 58.36 | 58.5992 | 58.3574 | 1.4197 | 1.3695 | 0.84652
22.6459 | 58.4657 | 58.7422 | 58.4356 | 1.4177 | 1.367 | 0.84487
22.65 | 58.5758 | 58.8889 | 58.5225 | 1.415 | 1.3641 | 0.84294
22.6542 | 58.6884 | 59.032 | 58.6121 | 1.4121 | 1.3606 | 0.84076
22.6584 | 58.7758 | 59.143 | 58.6862 | 1.4089 | 1.3569 | 0.83844
22.6625 | 58.8578 | 59.2306 | 58.7487 | 1.4055 | 1.3528 | 0.83596
22.6667 | 58.8836 | 59.2718 | 58.7842 | 1.4021 | 1.3486 | 0.83341
22.6709 | 58.8776 | 59.2639 | 58.7978 | 1.3986 | 1.3444 | 0.83079
22.675 | 58.859 | 59.2389 | 58.8079 | 1.3951 | 1.3403 | 0.8282
22.6792 | 58.8386 | 59.1983 | 58.8113 | 1.3916 | 1.3362 | 0.82561
22.6834 | 58.8031 | 59.1443 | 58.8073 | 1.3885 | 1.3324 | 0.82321
22.6875 | 58.7654 | 59.086 | 58.7923 | 1.3857 | 1.329 | 0.821
22.6917 | 58.7152 | 59.0269 | 58.7733 | 1.3831 | 1.3259 | 0.81886
22.6959 | 58.6595 | 58.9509 | 58.7544 | 1.3805 | 1.323 | 0.81675
22.7 | 58.6446 | 58.9071 | 58.7539 | 1.378 | 1.3202 | 0.8147
22.7042 | 58.6503 | 58.9043 | 58.7771 | 1.3757 | 1.3176 | 0.81272
22.7084 | 58.6481 | 58.9022 | 58.7977 | 1.3736 | 1.3151 | 0.81083
22.7125 | 58.648 | 58.8993 | 58.8153 | 1.3716 | 1.313 | 0.80899
22.7167 | 58.6497 | 58.8949 | 58.8327 | 1.3694 | 1.3108 | 0.80707
22.7209 | 58.6576 | 58.8904 | 58.8544 | 1.3671 | 1.3083 | 0.80498
22.725 | 58.6903 | 58.9055 | 58.8858 | 1.3649 | 1.3059 | 0.80293
22.7292 | 58.7268 | 58.9447 | 58.9213 | 1.3628 | 1.3036 | 0.80093
22.7334 | 58.7371 | 58.9724 | 58.9434 | 1.3607 | 1.3014 | 0.79896
22.7375 | 58.7293 | 58.9697 | 58.9477 | 1.3586 | 1.2991 | 0.79695
22.7417 | 58.7362 | 58.9597 | 58.9547 | 1.3562 | 1.2968 | 0.79487
22.7459 | 58.7491 | 58.9679 | 58.9658 | 1.3539 | 1.2942 | 0.79278
22.75 | 58.7626 | 58.9728 | 58.9809 | 1.3517 | 1.2919 | 0.79078
22.7542 | 58.7779 | 58.9713 | 58.9923 | 1.3496 | 1.2898 | 0.78891
22.7584 | 58.7652 | 58.9552 | 58.9934 | 1.3475 | 1.2878 | 0.78704
22.7625 | 58.7533 | 58.92 | 58.9897 | 1.3453 | 1.2856 | 0.78515
22.7667 | 58.7551 | 58.8901 | 58.9944 | 1.3431 | 1.2836 | 0.78324
22.7709 | 58.7756 | 58.8921 | 59.0073 | 1.341 | 1.2816 | 0.78142
22.775 | 58.7796 | 58.9009 | 59.019 | 1.339 | 1.2798 | 0.77968
22.7792 | 58.7763 | 58.8839 | 59.0279 | 1.3371 | 1.2781 | 0.77797
22.7834 | 58.7733 | 58.8725 | 59.0312 | 1.3351 | 1.2765 | 0.77623
22.7875 | 58.7666 | 58.871 | 59.0357 | 1.3329 | 1.2746 | 0.77448
22.7917 | 58.7761 | 58.8787 | 59.0472 | 1.331 | 1.2727 | 0.77276
22.7959 | 58.7947 | 58.8983 | 59.0603 | 1.3291 | 1.2711 | 0.77108
22.8 | 58.7938 | 58.9194 | 59.0692 | 1.3272 | 1.2695 | 0.76945
22.8042 | 58.7826 | 58.915 | 59.0777 | 1.3254 | 1.2678 | 0.7678
22.8084 | 58.7842 | 58.9083 | 59.0843 | 1.3234 | 1.266 | 0.76614
22.8125 | 58.7855 | 58.9256 | 59.088 | 1.3215 | 1.2642 | 0.76452
22.8167 | 58.7925 | 58.9403 | 59.0959 | 1.3197 | 1.2623 | 0.76294
22.8209 | 58.8041 | 58.9418 | 59.1058 | 1.3179 | 1.2607 | 0.76133
22.825 | 58.8044 | 58.9414 | 59.1125 | 1.3161 | 1.259 | 0.75975
22.8292 | 58.7974 | 58.9402 | 59.1202 | 1.3143 | 1.2572 | 0.75822
22.8334 | 58.8016 | 58.9334 | 59.1272 | 1.3125 | 1.2553 | 0.75669
22.8375 | 58.8013 | 58.9376 | 59.1275 | 1.3108 | 1.2537 | 0.75518
22.8417 | 58.8041 | 58.9451 | 59.1307 | 1.309 | 1.2521 | 0.75369
22.8459 | 58.8056 | 58.937 | 59.1422 | 1.3074 | 1.2504 | 0.75217
22.85 | 58.8058 | 58.9297 | 59.1514 | 1.3057 | 1.2488 | 0.75068
22.8542 | 58.8085 | 58.9385 | 59.1562 | 1.304 | 1.2471 | 0.74929
22.8584 | 58.8071 | 58.9419 | 59.1597 | 1.3023 | 1.2455 | 0.7479
22.8625 | 58.8105 | 58.9313 | 59.1595 | 1.3007 | 1.244 | 0.74645
22.8667 | 58.8171 | 58.9311 | 59.163 | 1.299 | 1.2425 | 0.74501
22.8709 | 58.8187 | 58.9372 | 59.1769 | 1.2974 | 1.2408 | 0.74361
22.875 | 58.8219 | 58.9367 | 59.1871 | 1.2958 | 1.2392 | 0.74225
22.8792 | 58.8295 | 58.9483 | 59.1852 | 1.2942 | 1.2378 | 0.74096
22.8834 | 58.8249 | 58.9575 | 59.183 | 1.2926 | 1.2363 | 0.73965
22.8875 | 58.8234 | 58.9348 | 59.1871 | 1.2911 | 1.2348 | 0.73825
22.8917 | 58.8251 | 58.9251 | 59.1959 | 1.2895 | 1.2334 | 0.73687
22.8959 | 58.8224 | 58.9449 | 59.2088 | 1.2879 | 1.2318 | 0.73562
22.9 | 58.8174 | 58.9492 | 59.2149 | 1.2865 | 1.2302 | 0.73441
22.9042 | 58.8186 | 58.9527 | 59.2074 | 1.285 | 1.2289 | 0.73316
22.9084 | 58.8286 | 58.9616 | 59.2031 | 1.2835 | 1.2275 | 0.73187
22.9125 | 58.8283 | 58.9484 | 59.2127 | 1.282 | 1.2259 | 0.73056
22.9167 | 58.8434 | 58.943 | 59.2247 | 1.2805 | 1.2244 | 0.72932
22.9209 | 58.8453 | 58.9566 | 59.2328 | 1.2791 | 1.2231 | 0.72818
22.925 | 58.8322 | 58.9578 | 59.2332 | 1.2776 | 1.2217 | 0.72703
22.9292 | 58.8197 | 58.9417 | 59.2264 | 1.2763 | 1.2203 | 0.72582
22.9334 | 58.8153 | 58.9382 | 59.2274 | 1.2748 | 1.219 | 0.72458
22.9375 | 58.8253 | 58.9681 | 59.2366 | 1.2734 | 1.2173 | 0.7234
22.9417 | 58.836 | 58.9869 | 59.2434 | 1.272 | 1.2158 | 0.7223
22.9459 | 58.8481 | 58.979 | 59.2475 | 1.2708 | 1.2147 | 0.72121
22.95 | 58.8405 | 58.9711 | 59.2462 | 1.2694 | 1.2135 | 0.72007
22.9542 | 58.8323 | 58.9333 | 59.2453 | 1.268 | 1.212 | 0.71893
22.9584 | 58.8307 | 58.9167 | 59.2517 | 1.2666 | 1.2105 | 0.71782
22.9625 | 58.8351 | 58.971 | 59.2549 | 1.2653 | 1.2091 | 0.71676
22.9667 | 58.8251 | 59.0041 | 59.2505 | 1.2642 | 1.2077 | 0.71576
22.9709 | 58.8192 | 59 | 59.2433 | 1.2629 | 1.2066 | 0.71477
22.975 | 58.8173 | 59.0061 | 59.2404 | 1.2616 | 1.2052 | 0.71371
22.9792 | 58.8245 | 58.9945 | 59.246 | 1.2602 | 1.2035 | 0.71266
22.9834 | 58.8484 | 58.9901 | 59.2554 | 1.259 | 1.202 | 0.71169
22.9875 | 58.8592 | 59.0071 | 59.2645 | 1.2578 | 1.2008 | 0.71076
22.9917 | 58.847 | 58.999 | 59.2607 | 1.2566 | 1.1995 | 0.70983
22.9959 | 58.8289 | 58.9765 | 59.2438 | 1.2554 | 1.1981 | 0.70894
23 | 58.8275 | 58.9693 | 59.2347 | 1.2541 | 1.1967 | 0.70804
23.0042 | 58.8214 | 58.9918 | 59.2302 | 1.2528 | 1.1952 | 0.70713
23.0084 | 58.8246 | 59.004 | 59.2235 | 1.2518 | 1.194 | 0.70635
23.0125 | 58.8347 | 58.9939 | 59.2184 | 1.2507 | 1.1929 | 0.70569
23.0167 | 58.83 | 58.9782 | 59.2082 | 1.2494 | 1.1918 | 0.70499
23.0209 | 58.8232 | 58.9455 | 59.1931 | 1.2483 | 1.1904 | 0.70427
23.025 | 58.8449 | 58.9365 | 59.1928 | 1.2471 | 1.1892 | 0.70357
23.0292 | 58.8494 | 58.9628 | 59.2067 | 1.2459 | 1.188 | 0.70286
23.0334 | 58.8387 | 58.968 | 59.2129 | 1.2448 | 1.1869 | 0.70221
23.0375 | 58.8417 | 58.9505 | 59.2127 | 1.2438 | 1.186 | 0.70164
23.0417 | 58.8316 | 58.9411 | 59.2137 | 1.2425 | 1.185 | 0.70096
23.0459 | 58.8157 | 58.9412 | 59.213 | 1.2415 | 1.1836 | 0.70016
23.05 | 58.8158 | 58.9502 | 59.2206 | 1.2405 | 1.1825 | 0.69942
23.0542 | 58.8291 | 58.9752 | 59.2396 | 1.2394 | 1.1815 | 0.69872
23.0584 | 58.8159 | 58.98 | 59.2451 | 1.2383 | 1.1805 | 0.69801
23.0625 | 58.8178 | 58.9385 | 59.2357 | 1.2374 | 1.1796 | 0.69733
23.0667 | 58.83 | 58.9183 | 59.2342 | 1.2363 | 1.1785 | 0.69658
23.0709 | 58.834 | 58.9339 | 59.2381 | 1.2351 | 1.1773 | 0.69573
23.075 | 58.8387 | 58.9406 | 59.2424 | 1.2341 | 1.1762 | 0.69498
23.0792 | 58.8457 | 58.9515 | 59.2525 | 1.2332 | 1.1755 | 0.69432
23.0834 | 58.8331 | 58.9512 | 59.253 | 1.2321 | 1.1747 | 0.69361
23.0875 | 58.8069 | 58.9214 | 59.2382 | 1.2311 | 1.1736 | 0.69289
23.0917 | 58.8115 | 58.912 | 59.2359 | 1.2301 | 1.1725 | 0.69215
23.0959 | 58.8215 | 58.942 | 59.2441 | 1.229 | 1.1715 | 0.69138
23.1 | 58.8259 | 58.9544 | 59.245 | 1.2281 | 1.1706 | 0.69069
23.1042 | 58.819 | 58.9314 | 59.2478 | 1.2273 | 1.1699 | 0.69009
23.1084 | 58.808 | 58.915 | 59.2489 | 1.2264 | 1.1691 | 0.68939
23.1125 | 58.7952 | 58.9087 | 59.2442 | 1.2254 | 1.1679 | 0.68863
23.1167 | 58.7983 | 58.9118 | 59.2489 | 1.2243 | 1.1669 | 0.68791
23.1209 | 58.8293 | 58.9314 | 59.2603 | 1.2235 | 1.1662 | 0.68722
23.125 | 58.8338 | 58.9327 | 59.2608 | 1.2226 | 1.1656 | 0.68655
23.1292 | 58.8119 | 58.8979 | 59.2487 | 1.2218 | 1.1647 | 0.68594
23.1334 | 58.8034 | 58.8778 | 59.2429 | 1.2209 | 1.1638 | 0.68527
23.1375 | 58.7912 | 58.9091 | 59.2499 | 1.2199 | 1.1628 | 0.68446
23.1417 | 58.791 | 58.9344 | 59.2586 | 1.2189 | 1.1619 | 0.68373
23.1459 | 58.8082 | 58.9302 | 59.2726 | 1.2182 | 1.1614 | 0.68314
23.15 | 58.7967 | 58.9192 | 59.2781 | 1.2174 | 1.1607 | 0.68249
23.1542 | 58.7809 | 58.887 | 59.2563 | 1.2167 | 1.1597 | 0.68184
23.1584 | 58.7807 | 58.8725 | 59.2443 | 1.2157 | 1.1587 | 0.68117
23.1625 | 58.7969 | 58.8972 | 59.2551 | 1.2148 | 1.1581 | 0.6804
23.1667 | 58.806 | 58.9078 | 59.2606 | 1.214 | 1.1574 | 0.67969
23.1709 | 58.8067 | 58.8942 | 59.271 | 1.2134 | 1.1568 | 0.67914
23.175 | 58.791 | 58.8816 | 59.2792 | 1.2126 | 1.156 | 0.67853
23.1792 | 58.767 | 58.8851 | 59.2674 | 1.2118 | 1.1551 | 0.67779
23.1834 | 58.7631 | 58.8962 | 59.2634 | 1.2109 | 1.1543 | 0.6771
23.1875 | 58.7728 | 58.8929 | 59.2713 | 1.2102 | 1.1538 | 0.67643
23.1917 | 58.7661 | 58.878 | 59.2712 | 1.2096 | 1.1533 | 0.67578
23.1959 | 58.753 | 58.8612 | 59.2655 | 1.2091 | 1.1525 | 0.67521
23.2 | 58.7496 | 58.8551 | 59.2636 | 1.2083 | 1.1516 | 0.67459
23.2042 | 58.7491 | 58.8715 | 59.268 | 1.2075 | 1.151 | 0.67384
23.2084 | 58.7685 | 58.887 | 59.2745 | 1.2067 | 1.1505 | 0.67316
23.2125 | 58.7813 | 58.8685 | 59.2817 | 1.2062 | 1.15 | 0.67259
23.2167 | 58.7737 | 58.843 | 59.2827 | 1.2055 | 1.1494 | 0.672
23.2209 | 58.7562 | 58.834 | 59.2729 | 1.2049 | 1.1487 | 0.67133
23.225 | 58.7554 | 58.834 | 59.2694 | 1.204 | 1.148 | 0.67065
23.2292 | 58.7636 | 58.8307 | 59.2776 | 1.2032 | 1.1477 | 0.66998
23.2334 | 58.7763 | 58.8199 | 59.283 | 1.2025 | 1.1473 | 0.66936
23.2375 | 58.7864 | 58.8022 | 59.28 | 1.2019 | 1.1469 | 0.66881
23.2417 | 58.7758 | 58.7855 | 59.2748 | 1.2011 | 1.1463 | 0.66822
23.2459 | 58.7841 | 58.7887 | 59.2739 | 1.2003 | 1.1459 | 0.66752
23.25 | 58.7945 | 58.7999 | 59.2779 | 1.1993 | 1.1456 | 0.66685
23.2542 | 58.8047 | 58.7958 | 59.2883 | 1.1986 | 1.1453 | 0.66626
23.2584 | 58.8051 | 58.7881 | 59.2937 | 1.1979 | 1.1449 | 0.66568
23.2625 | 58.7879 | 58.7854 | 59.2844 | 1.1971 | 1.1445 | 0.66509
23.2667 | 58.7665 | 58.7903 | 59.2771 | 1.1963 | 1.144 | 0.66446
23.2709 | 58.7644 | 58.7913 | 59.2799 | 1.1955 | 1.1436 | 0.66379
23.275 | 58.7711 | 58.7893 | 59.2845 | 1.1947 | 1.1433 | 0.66315
23.2792 | 58.7697 | 58.7957 | 59.2901 | 1.1941 | 1.1429 | 0.6626
23.2834 | 58.7664 | 58.7927 | 59.2915 | 1.1935 | 1.1423 | 0.66204
23.2875 | 58.7678 | 58.794 | 59.2838 | 1.1927 | 1.1419 | 0.66143
23.2917 | 58.7565 | 58.799 | 59.2801 | 1.192 | 1.1416 | 0.66081
23.2959 | 58.7637 | 58.7986 | 59.2887 | 1.1913 | 1.141 | 0.66016
23.3 | 58.7672 | 58.7903 | 59.2959 | 1.1907 | 1.1406 | 0.65955
23.3042 | 58.7364 | 58.7967 | 59.2947 | 1.1901 | 1.1401 | 0.65903
23.3084 | 58.7287 | 58.8039 | 59.2919 | 1.1895 | 1.1396 | 0.65848
23.3125 | 58.7254 | 58.7886 | 59.2873 | 1.1889 | 1.1392 | 0.65782
23.3167 | 58.7229 | 58.7821 | 59.2858 | 1.1882 | 1.1389 | 0.65718
23.3209 | 58.7448 | 58.7821 | 59.2923 | 1.1877 | 1.1383 | 0.65663
23.325 | 58.7443 | 58.7781 | 59.2958 | 1.1872 | 1.1378 | 0.65609
23.3292 | 58.728 | 58.7769 | 59.2915 | 1.1866 | 1.1375 | 0.65553
23.3334 | 58.729 | 58.7816 | 59.2897 | 1.186 | 1.1371 | 0.65493
23.3375 | 58.7264 | 58.7695 | 59.2945 | 1.1853 | 1.1367 | 0.65431
23.3417 | 58.7321 | 58.7578 | 59.2998 | 1.1847 | 1.1363 | 0.65371
23.3459 | 58.735 | 58.7673 | 59.3018 | 1.1843 | 1.1359 | 0.65318
23.35 | 58.7178 | 58.7709 | 59.2998 | 1.1838 | 1.1354 | 0.65264
23.3542 | 58.7065 | 58.7633 | 59.2967 | 1.1832 | 1.1351 | 0.65202
23.3584 | 58.7054 | 58.7602 | 59.2974 | 1.1826 | 1.1348 | 0.65139
23.3625 | 58.7144 | 58.7585 | 59.2998 | 1.182 | 1.1343 | 0.65084
23.3667 | 58.7178 | 58.7521 | 59.3024 | 1.1816 | 1.1339 | 0.65031
23.3709 | 58.7239 | 58.7592 | 59.3028 | 1.1811 | 1.1335 | 0.64973
23.375 | 58.7149 | 58.7641 | 59.3026 | 1.1805 | 1.1332 | 0.64912
23.3792 | 58.7185 | 58.7579 | 59.3072 | 1.1799 | 1.1327 | 0.64853
23.3834 | 58.7308 | 58.7545 | 59.3142 | 1.1793 | 1.1323 | 0.64793
23.3875 | 58.7346 | 58.7576 | 59.3158 | 1.1787 | 1.1319 | 0.64735
23.3917 | 58.7257 | 58.7585 | 59.3144 | 1.1782 | 1.1315 | 0.64678
23.3959 | 58.7197 | 58.7515 | 59.3155 | 1.1776 | 1.1311 | 0.64616
23.4 | 58.7066 | 58.7485 | 59.3158 | 1.177 | 1.1308 | 0.64553
23.4042 | 58.7004 | 58.7458 | 59.3172 | 1.1764 | 1.1303 | 0.64495
23.4084 | 58.6991 | 58.7433 | 59.3191 | 1.176 | 1.1299 | 0.64439
23.4125 | 58.6902 | 58.7441 | 59.3178 | 1.1755 | 1.1296 | 0.64379
23.4167 | 58.6807 | 58.745 | 59.316 | 1.1751 | 1.1292 | 0.6432
23.4209 | 58.6838 | 58.7406 | 59.3179 | 1.1745 | 1.1288 | 0.64261
23.425 | 58.6936 | 58.7362 | 59.3192 | 1.174 | 1.1284 | 0.64204
23.4292 | 58.6937 | 58.7383 | 59.317 | 1.1735 | 1.128 | 0.6415
23.4334 | 58.6936 | 58.733 | 59.312 | 1.1732 | 1.1277 | 0.64097
23.4375 | 58.6835 | 58.717 | 59.3047 | 1.1726 | 1.1274 | 0.64045
23.4417 | 58.6907 | 58.7141 | 59.3064 | 1.172 | 1.127 | 0.63987
23.4459 | 58.7051 | 58.7306 | 59.3189 | 1.1714 | 1.1265 | 0.63925
23.45 | 58.7286 | 58.7507 | 59.3348 | 1.1708 | 1.126 | 0.63865
23.4542 | 58.7428 | 58.7745 | 59.352 | 1.1703 | 1.1256 | 0.63806
23.4584 | 58.7231 | 58.7707 | 59.3498 | 1.1697 | 1.1253 | 0.63751
23.4625 | 58.6971 | 58.7313 | 59.3281 | 1.1692 | 1.1249 | 0.637
23.4667 | 58.676 | 58.6997 | 59.3091 | 1.1686 | 1.1245 | 0.63645
23.4709 | 58.6524 | 58.6866 | 59.2948 | 1.1681 | 1.1241 | 0.63586
23.475 | 58.6724 | 58.7103 | 59.3071 | 1.1675 | 1.1236 | 0.63524
23.4792 | 58.7101 | 58.7607 | 59.3451 | 1.1669 | 1.1231 | 0.63459
23.4834 | 58.7403 | 58.8085 | 59.3813 | 1.1662 | 1.1225 | 0.63392
23.4875 | 58.7849 | 58.8551 | 59.4172 | 1.1656 | 1.1218 | 0.63317
23.4917 | 58.7999 | 58.8776 | 59.4335 | 1.1647 | 1.1209 | 0.63235
23.4959 | 58.7997 | 58.8818 | 59.4336 | 1.1638 | 1.12 | 0.63145
23.5 | 58.8057 | 58.8911 | 59.4362 | 1.1628 | 1.119 | 0.63052
23.5042 | 58.8198 | 58.8996 | 59.439 | 1.1617 | 1.1178 | 0.62953
23.5084 | 58.8418 | 58.9235 | 59.4499 | 1.1606 | 1.1166 | 0.62857
23.5125 | 58.8721 | 58.9665 | 59.4683 | 1.1595 | 1.1153 | 0.62759
23.5167 | 58.9251 | 59.028 | 59.495 | 1.1581 | 1.1137 | 0.6265
23.5209 | 58.9766 | 59.0991 | 59.5305 | 1.1565 | 1.112 | 0.62527
23.525 | 59.0657 | 59.1992 | 59.5866 | 1.1545 | 1.1098 | 0.62385
23.5292 | 59.1721 | 59.3345 | 59.6579 | 1.1524 | 1.1072 | 0.62224
23.5334 | 59.2603 | 59.4579 | 59.7256 | 1.1499 | 1.1042 | 0.62051
23.5375 | 59.3447 | 59.569 | 59.7875 | 1.1474 | 1.1011 | 0.61865
23.5417 | 59.4013 | 59.6464 | 59.8304 | 1.1444 | 1.0977 | 0.61661
23.5459 | 59.4396 | 59.685 | 59.8628 | 1.1413 | 1.0939 | 0.61438
23.55 | 59.4589 | 59.7024 | 59.8888 | 1.1381 | 1.09 | 0.61211
23.5542 | 59.4668 | 59.711 | 59.9075 | 1.1351 | 1.0862 | 0.60985
23.5584 | 59.4337 | 59.6849 | 59.9101 | 1.1321 | 1.0826 | 0.6077
23.5625 | 59.3917 | 59.6184 | 59.892 | 1.1293 | 1.0793 | 0.60562
23.5667 | 59.3448 | 59.5434 | 59.8678 | 1.1266 | 1.0761 | 0.60359
23.5709 | 59.2944 | 59.4647 | 59.842 | 1.1241 | 1.0731 | 0.60163
23.575 | 59.2579 | 59.4089 | 59.8274 | 1.122 | 1.0704 | 0.5998
23.5792 | 59.2227 | 59.3683 | 59.8215 | 1.1199 | 1.0681 | 0.59812
23.5834 | 59.1969 | 59.3355 | 59.8171 | 1.118 | 1.066 | 0.59651
23.5875 | 59.1807 | 59.3078 | 59.8186 | 1.1162 | 1.064 | 0.59492
23.5917 | 59.1823 | 59.2871 | 59.8249 | 1.1144 | 1.062 | 0.59332
23.5959 | 59.1901 | 59.2909 | 59.8401 | 1.1127 | 1.0601 | 0.59171
23.6 | 59.2057 | 59.3085 | 59.8621 | 1.1109 | 1.0583 | 0.59011
23.6042 | 59.2242 | 59.3231 | 59.887 | 1.1092 | 1.0564 | 0.58846
23.6084 | 59.2466 | 59.3396 | 59.9068 | 1.1073 | 1.0546 | 0.5868
23.6125 | 59.2672 | 59.3631 | 59.9232 | 1.1055 | 1.0526 | 0.5851
23.6167 | 59.2817 | 59.379 | 59.9369 | 1.1036 | 1.0505 | 0.58337
23.6209 | 59.2886 | 59.3924 | 59.9422 | 1.1017 | 1.0486 | 0.58164
23.625 | 59.2967 | 59.4034 | 59.95 | 1.0997 | 1.0466 | 0.57993
23.6292 | 59.3067 | 59.4031 | 59.9587 | 1.0978 | 1.0445 | 0.57819
23.6334 | 59.3109 | 59.3922 | 59.9619 | 1.0958 | 1.0425 | 0.5765
23.6375 | 59.3157 | 59.388 | 59.9595 | 1.094 | 1.0406 | 0.57492
23.6417 | 59.3032 | 59.3736 | 59.9569 | 1.0921 | 1.0388 | 0.57332
23.6459 | 59.2969 | 59.3462 | 59.9529 | 1.0903 | 1.037 | 0.57171
23.65 | 59.2985 | 59.3287 | 59.9545 | 1.0884 | 1.0354 | 0.57013
23.6542 | 59.3078 | 59.3226 | 59.9654 | 1.0865 | 1.0336 | 0.5686
23.6584 | 59.3095 | 59.3174 | 59.9697 | 1.0849 | 1.032 | 0.56713
23.6625 | 59.3009 | 59.3084 | 59.9651 | 1.0832 | 1.0306 | 0.5657
23.6667 | 59.2973 | 59.3071 | 59.9634 | 1.0815 | 1.0292 | 0.56424
23.6709 | 59.2969 | 59.3016 | 59.9691 | 1.0797 | 1.0276 | 0.5627
23.675 | 59.3095 | 59.3092 | 59.9787 | 1.078 | 1.026 | 0.56122
23.6792 | 59.3205 | 59.3336 | 59.9903 | 1.0764 | 1.0246 | 0.55985
23.6834 | 59.3166 | 59.3499 | 59.993 | 1.0748 | 1.0231 | 0.55849
23.6875 | 59.2973 | 59.3427 | 59.9852 | 1.0732 | 1.0217 | 0.55708
23.6917 | 59.2995 | 59.3406 | 59.9846 | 1.0715 | 1.0201 | 0.55563
23.6959 | 59.313 | 59.3563 | 59.9956 | 1.0698 | 1.0184 | 0.55418
23.7 | 59.3215 | 59.3685 | 60.0059 | 1.0682 | 1.0167 | 0.55282
23.7042 | 59.3301 | 59.379 | 60.0087 | 1.0668 | 1.0154 | 0.55154
23.7084 | 59.3201 | 59.3782 | 60.0046 | 1.0652 | 1.0139 | 0.55023
23.7125 | 59.302 | 59.3578 | 59.9983 | 1.0636 | 1.0123 | 0.54884
23.7167 | 59.3127 | 59.3463 | 60.0016 | 1.062 | 1.0107 | 0.54746
23.7209 | 59.329 | 59.3674 | 60.0137 | 1.0605 | 1.0091 | 0.54616
23.725 | 59.3266 | 59.3804 | 60.0197 | 1.0591 | 1.0076 | 0.54492
23.7292 | 59.324 | 59.368 | 60.0157 | 1.0577 | 1.0064 | 0.5437
23.7334 | 59.3144 | 59.3564 | 60.0104 | 1.0562 | 1.005 | 0.54242
23.7375 | 59.3071 | 59.3439 | 60.0109 | 1.0546 | 1.0034 | 0.5411
23.7417 | 59.3188 | 59.3409 | 60.0189 | 1.0532 | 1.0019 | 0.53983
23.7459 | 59.3346 | 59.3639 | 60.0275 | 1.0518 | 1.0006 | 0.53866
23.75 | 59.3299 | 59.3767 | 60.0274 | 1.0504 | 0.99929 | 0.5375
23.7542 | 59.3231 | 59.362 | 60.0212 | 1.049 | 0.99798 | 0.53631
23.7584 | 59.3276 | 59.3532 | 60.0192 | 1.0476 | 0.99663 | 0.53507
23.7625 | 59.3345 | 59.3564 | 60.0239 | 1.046 | 0.99514 | 0.53386
23.7667 | 59.3372 | 59.363 | 60.0312 | 1.0447 | 0.99373 | 0.53272
23.7709 | 59.3406 | 59.3661 | 60.0361 | 1.0435 | 0.99256 | 0.5316
23.775 | 59.3245 | 59.3627 | 60.0338 | 1.0421 | 0.99136 | 0.53047
23.7792 | 59.3086 | 59.3594 | 60.0287 | 1.0407 | 0.98992 | 0.52933
23.7834 | 59.3174 | 59.3586 | 60.0302 | 1.0394 | 0.98851 | 0.52819
23.7875 | 59.3345 | 59.3795 | 60.0331 | 1.038 | 0.98719 | 0.52707
23.7917 | 59.3493 | 59.3986 | 60.0339 | 1.0367 | 0.98591 | 0.52601
23.7959 | 59.3416 | 59.3704 | 60.0396 | 1.0356 | 0.98478 | 0.52493
23.8 | 59.3344 | 59.3467 | 60.042 | 1.0343 | 0.98361 | 0.52382
23.8042 | 59.3207 | 59.3517 | 60.0378 | 1.0329 | 0.98213 | 0.52278
23.8084 | 59.3188 | 59.3571 | 60.0384 | 1.0316 | 0.98069 | 0.52177
23.8125 | 59.3288 | 59.3868 | 60.0371 | 1.0305 | 0.97958 | 0.52071
23.8167 | 59.3282 | 59.4098 | 60.0333 | 1.0293 | 0.97846 | 0.51966
23.8209 | 59.3255 | 59.3906 | 60.0385 | 1.0281 | 0.97714 | 0.51867
23.825 | 59.3295 | 59.3754 | 60.0441 | 1.0268 | 0.97583 | 0.51766
23.8292 | 59.3396 | 59.3706 | 60.0443 | 1.0255 | 0.97456 | 0.51666
23.8334 | 59.342 | 59.3688 | 60.0442 | 1.0244 | 0.97331 | 0.5157
23.8375 | 59.3389 | 59.3683 | 60.0442 | 1.0232 | 0.97219 | 0.51471
23.8417 | 59.3235 | 59.3675 | 60.0411 | 1.0221 | 0.97105 | 0.51373
23.8459 | 59.3116 | 59.3888 | 60.0335 | 1.0209 | 0.96969 | 0.51284
23.85 | 59.3116 | 59.4097 | 60.0289 | 1.0198 | 0.96832 | 0.51196
23.8542 | 59.3207 | 59.4136 | 60.0269 | 1.0186 | 0.96721 | 0.51104
23.8584 | 59.3259 | 59.421 | 60.0258 | 1.0176 | 0.96605 | 0.51014
23.8625 | 59.3338 | 59.4042 | 60.0326 | 1.0165 | 0.9647 | 0.50929
23.8667 | 59.3408 | 59.386 | 60.037 | 1.0153 | 0.96336 | 0.50845
23.8709 | 59.3336 | 59.4005 | 60.0311 | 1.0142 | 0.96214 | 0.50763
23.875 | 59.3325 | 59.406 | 60.0247 | 1.0131 | 0.96091 | 0.50682
23.8792 | 59.3261 | 59.3999 | 60.0199 | 1.012 | 0.95979 | 0.506
23.8834 | 59.3174 | 59.3954 | 60.0142 | 1.0109 | 0.95867 | 0.5052
23.8875 | 59.3155 | 59.3944 | 60.0081 | 1.0099 | 0.95738 | 0.50451
23.8917 | 59.3209 | 59.3893 | 60.0008 | 1.0089 | 0.95618 | 0.50384
23.8959 | 59.3177 | 59.386 | 59.989 | 1.0078 | 0.95517 | 0.50318
23.9 | 59.3187 | 59.3839 | 59.9804 | 1.0068 | 0.95414 | 0.50252
23.9042 | 59.3226 | 59.3639 | 59.9812 | 1.0058 | 0.95305 | 0.50189
23.9084 | 59.3327 | 59.3532 | 59.9849 | 1.0047 | 0.95202 | 0.50127
23.9125 | 59.3331 | 59.3598 | 59.9876 | 1.0037 | 0.951 | 0.50069
23.9167 | 59.3294 | 59.3573 | 59.9891 | 1.0027 | 0.95003 | 0.50011
23.9209 | 59.3279 | 59.3559 | 59.9894 | 1.0017 | 0.94914 | 0.49948
23.925 | 59.3164 | 59.3602 | 59.9928 | 1.0006 | 0.94818 | 0.49882
23.9292 | 59.3087 | 59.3615 | 60.0031 | 0.99974 | 0.94712 | 0.49815
23.9334 | 59.3072 | 59.365 | 60.0126 | 0.99885 | 0.94616 | 0.49749
23.9375 | 59.3099 | 59.371 | 60.0157 | 0.99783 | 0.94525 | 0.49685
23.9417 | 59.3027 | 59.3679 | 60.0145 | 0.99693 | 0.9443 | 0.4962
23.9459 | 59.3146 | 59.3482 | 60.0114 | 0.996 | 0.94341 | 0.49549
23.95 | 59.3275 | 59.3416 | 60.0124 | 0.99502 | 0.9425 | 0.49477
23.9542 | 59.3215 | 59.3506 | 60.021 | 0.99408 | 0.94148 | 0.49405
23.9584 | 59.3153 | 59.3499 | 60.0262 | 0.99327 | 0.94058 | 0.49338
23.9625 | 59.3176 | 59.3549 | 60.0229 | 0.99227 | 0.93983 | 0.49275
23.9667 | 59.3111 | 59.3562 | 60.0179 | 0.99124 | 0.93897 | 0.49208
23.9709 | 59.3062 | 59.3352 | 60.01 | 0.99042 | 0.93807 | 0.49138
23.975 | 59.3212 | 59.3279 | 60.0084 | 0.98954 | 0.93725 | 0.4907
23.9792 | 59.3076 | 59.3481 | 60.0152 | 0.98867 | 0.9363 | 0.49006
23.9834 | 59.2928 | 59.3523 | 60.0156 | 0.98781 | 0.93541 | 0.48945
23.9875 | 59.2926 | 59.342 | 60.0161 | 0.98705 | 0.93477 | 0.48883
23.9917 | 59.2906 | 59.3416 | 60.0192 | 0.98607 | 0.93402 | 0.48815
23.9959 | 59.2941 | 59.3256 | 60.0182 | 0.98528 | 0.93305 | 0.48748
24 | 59.3024 | 59.3149 | 60.0212 | 0.98448 | 0.93223 | 0.48686
24.0042 | 59.3089 | 59.3324 | 60.0208 | 0.98367 | 0.93154 | 0.48625
24.0084 | 59.303 | 59.3337 | 60.0126 | 0.98276 | 0.93079 | 0.48564
24.0125 | 59.2895 | 59.3128 | 60.0113 | 0.98206 | 0.93013 | 0.485
24.0167 | 59.292 | 59.3078 | 60.0171 | 0.98119 | 0.92944 | 0.48432
24.0209 | 59.2857 | 59.3292 | 60.0274 | 0.98038 | 0.92843 | 0.48365
24.025 | 59.2772 | 59.3409 | 60.0355 | 0.97961 | 0.92758 | 0.48305
24.0292 | 59.2835 | 59.3363 | 60.031 | 0.97897 | 0.92713 | 0.48248
24.0334 | 59.2745 | 59.329 | 60.0213 | 0.97815 | 0.92654 | 0.48185
24.0375 | 59.2668 | 59.2931 | 60.0108 | 0.97746 | 0.92567 | 0.4812
24.0417 | 59.273 | 59.2749 | 60.0096 | 0.97669 | 0.92488 | 0.48056
24.0459 | 59.2858 | 59.3161 | 60.0254 | 0.9759 | 0.92413 | 0.47991
24.05 | 59.2848 | 59.3372 | 60.0332 | 0.97515 | 0.92343 | 0.47931
24.0542 | 59.2819 | 59.3138 | 60.0318 | 0.97456 | 0.92304 | 0.47877
24.0584 | 59.274 | 59.2994 | 60.032 | 0.97379 | 0.92251 | 0.47815
24.0625 | 59.2563 | 59.2882 | 60.0221 | 0.97307 | 0.92152 | 0.47747
24.0667 | 59.2497 | 59.2824 | 60.0184 | 0.97238 | 0.9207 | 0.47686
24.0709 | 59.2584 | 59.3065 | 60.03 | 0.97173 | 0.92029 | 0.47625
24.075 | 59.2526 | 59.3136 | 60.0314 | 0.97108 | 0.91982 | 0.47563
24.0792 | 59.2401 | 59.2758 | 60.0231 | 0.97058 | 0.91923 | 0.47511
24.0834 | 59.2459 | 59.2577 | 60.0227 | 0.96989 | 0.9186 | 0.47454
24.0875 | 59.2485 | 59.2798 | 60.0247 | 0.96914 | 0.91781 | 0.47384
24.0917 | 59.2558 | 59.2939 | 60.0259 | 0.96848 | 0.91716 | 0.47321
24.0959 | 59.2673 | 59.2846 | 60.0361 | 0.96795 | 0.91694 | 0.47269
24.1 | 59.2662 | 59.2692 | 60.0396 | 0.96724 | 0.91657 | 0.47211
24.1042 | 59.2402 | 59.2409 | 60.0259 | 0.96666 | 0.91583 | 0.47151
24.1084 | 59.2451 | 59.2289 | 60.0224 | 0.96591 | 0.91515 | 0.47092
24.1125 | 59.259 | 59.2504 | 60.0302 | 0.96516 | 0.91482 | 0.47027
24.1167 | 59.2595 | 59.2542 | 60.0307 | 0.96445 | 0.91453 | 0.46966
24.1209 | 59.272 | 59.2225 | 60.0309 | 0.96397 | 0.91426 | 0.46919
24.125 | 59.2724 | 59.1975 | 60.0311 | 0.96317 | 0.91387 | 0.46864
24.1292 | 59.2651 | 59.2057 | 60.0258 | 0.96235 | 0.91327 | 0.46797
24.1334 | 59.2745 | 59.2235 | 60.0273 | 0.96158 | 0.91278 | 0.46737
24.1375 | 59.2931 | 59.2308 | 60.0381 | 0.96081 | 0.91268 | 0.46681
24.1417 | 59.2802 | 59.2267 | 60.0395 | 0.96013 | 0.9125 | 0.46626
24.1459 | 59.2579 | 59.2041 | 60.0301 | 0.95955 | 0.912 | 0.46573
24.15 | 59.2495 | 59.1958 | 60.0271 | 0.95878 | 0.91142 | 0.46515
24.1542 | 59.2346 | 59.2217 | 60.0291 | 0.95798 | 0.91102 | 0.4645
24.1584 | 59.2421 | 59.2407 | 60.0316 | 0.95734 | 0.9107 | 0.46392
24.1625 | 59.2631 | 59.231 | 60.0375 | 0.95676 | 0.91043 | 0.46343
24.1667 | 59.2465 | 59.2117 | 60.0366 | 0.95616 | 0.91006 | 0.46289
24.1709 | 59.2394 | 59.211 | 60.0263 | 0.95556 | 0.90944 | 0.46232
24.175 | 59.236 | 59.219 | 60.0248 | 0.95485 | 0.90888 | 0.46175
24.1792 | 59.2254 | 59.2361 | 60.0358 | 0.9542 | 0.90853 | 0.46113
24.1834 | 59.2343 | 59.2393 | 60.0418 | 0.95365 | 0.90826 | 0.46056
24.1875 | 59.2219 | 59.2196 | 60.0392 | 0.95319 | 0.9078 | 0.4601
24.1917 | 59.2062 | 59.2052 | 60.0346 | 0.95264 | 0.90727 | 0.45959
24.1959 | 59.2047 | 59.2073 | 60.0264 | 0.95205 | 0.90675 | 0.45896
24.2 | 59.2049 | 59.2184 | 60.0245 | 0.95142 | 0.90634 | 0.45836
24.2042 | 59.2141 | 59.2176 | 60.0369 | 0.95094 | 0.90602 | 0.45784
24.2084 | 59.2227 | 59.2078 | 60.0431 | 0.95045 | 0.90567 | 0.45732
24.2125 | 59.208 | 59.1928 | 60.033 | 0.94997 | 0.90524 | 0.45684
24.2167 | 59.2008 | 59.19 | 60.0273 | 0.94939 | 0.90475 | 0.45632
24.2209 | 59.2059 | 59.1965 | 60.0328 | 0.94878 | 0.90436 | 0.45566
24.225 | 59.2096 | 59.1993 | 60.0384 | 0.94816 | 0.90405 | 0.45505
24.2292 | 59.2093 | 59.1985 | 60.045 | 0.94778 | 0.90372 | 0.45461
24.2334 | 59.201 | 59.1905 | 60.0458 | 0.9473 | 0.9033 | 0.45414
24.2375 | 59.1847 | 59.1812 | 60.0325 | 0.94677 | 0.90291 | 0.45355
24.2417 | 59.1762 | 59.1825 | 60.0264 | 0.94618 | 0.90254 | 0.45296
24.2459 | 59.1937 | 59.1897 | 60.0376 | 0.94564 | 0.90214 | 0.45239
24.25 | 59.1995 | 59.1852 | 60.0456 | 0.94517 | 0.90179 | 0.45185
24.2542 | 59.1969 | 59.1863 | 60.0433 | 0.94476 | 0.90145 | 0.4514
24.2584 | 59.1899 | 59.1878 | 60.0408 | 0.94429 | 0.90103 | 0.45088
24.2625 | 59.1881 | 59.1806 | 60.0382 | 0.94359 | 0.90061 | 0.45025
24.2667 | 59.1957 | 59.1812 | 60.041 | 0.94299 | 0.90027 | 0.44963
24.2709 | 59.2123 | 59.188 | 60.052 | 0.94244 | 0.89984 | 0.44912
24.275 | 59.2078 | 59.1838 | 60.0546 | 0.94203 | 0.89942 | 0.44861
24.2792 | 59.1866 | 59.1737 | 60.0457 | 0.94152 | 0.89912 | 0.44808
24.2834 | 59.1685 | 59.1727 | 60.0394 | 0.94099 | 0.89876 | 0.4475
24.2875 | 59.1626 | 59.1647 | 60.0406 | 0.94034 | 0.89832 | 0.4469
24.2917 | 59.1716 | 59.1631 | 60.0473 | 0.93987 | 0.89792 | 0.44633
24.2959 | 59.1794 | 59.1802 | 60.0566 | 0.93944 | 0.89754 | 0.4458
24.3 | 59.1718 | 59.1862 | 60.0572 | 0.93909 | 0.89712 | 0.44528
24.3042 | 59.1593 | 59.174 | 60.0499 | 0.93858 | 0.89682 | 0.44473
24.3084 | 59.1521 | 59.159 | 60.0399 | 0.93807 | 0.89654 | 0.4442
24.3125 | 59.1439 | 59.1395 | 60.0278 | 0.93763 | 0.89615 | 0.44371
24.3167 | 59.1548 | 59.1282 | 60.0246 | 0.93721 | 0.89575 | 0.44321
24.3209 | 59.1565 | 59.1399 | 60.0295 | 0.93678 | 0.89542 | 0.44269
24.325 | 59.1723 | 59.1665 | 60.0444 | 0.93617 | 0.89501 | 0.44213
24.3292 | 59.2024 | 59.1959 | 60.0708 | 0.93552 | 0.89452 | 0.44152
24.3334 | 59.2154 | 59.2052 | 60.0838 | 0.93489 | 0.89411 | 0.44095
24.3375 | 59.2138 | 59.2015 | 60.0814 | 0.93444 | 0.8937 | 0.44042
24.3417 | 59.1831 | 59.177 | 60.0638 | 0.93392 | 0.89326 | 0.43989
24.3459 | 59.1397 | 59.1321 | 60.0322 | 0.93339 | 0.89287 | 0.43934
24.35 | 59.1326 | 59.1242 | 60.0238 | 0.93269 | 0.89243 | 0.43875
24.3542 | 59.149 | 59.1477 | 60.0387 | 0.9321 | 0.89184 | 0.43813
24.3584 | 59.1818 | 59.184 | 60.0642 | 0.93155 | 0.89128 | 0.43754
24.3625 | 59.2165 | 59.2351 | 60.0991 | 0.93106 | 0.89082 | 0.43696
24.3667 | 59.231 | 59.272 | 60.1214 | 0.9303 | 0.89012 | 0.43627
24.3709 | 59.249 | 59.2912 | 60.1355 | 0.92941 | 0.88917 | 0.43542
24.375 | 59.276 | 59.3165 | 60.1526 | 0.92837 | 0.88811 | 0.43451
24.3792 | 59.3059 | 59.356 | 60.1713 | 0.92734 | 0.88692 | 0.43353
24.3834 | 59.3202 | 59.3823 | 60.1818 | 0.92637 | 0.88573 | 0.43259
24.3875 | 59.3258 | 59.3887 | 60.1827 | 0.92529 | 0.8846 | 0.43167
24.3917 | 59.3398 | 59.4034 | 60.1833 | 0.92396 | 0.88325 | 0.43064
24.3959 | 59.3571 | 59.4263 | 60.1888 | 0.92258 | 0.88159 | 0.4295
24.4 | 59.4174 | 59.4824 | 60.2167 | 0.92104 | 0.87977 | 0.4283
24.4042 | 59.4805 | 59.575 | 60.2591 | 0.91944 | 0.87788 | 0.42706
24.4084 | 59.5438 | 59.6685 | 60.3043 | 0.91754 | 0.87571 | 0.42571
24.4125 | 59.6157 | 59.7572 | 60.3481 | 0.91549 | 0.87322 | 0.42422
24.4167 | 59.6829 | 59.8394 | 60.3868 | 0.91301 | 0.87038 | 0.42253
24.4209 | 59.7435 | 59.9204 | 60.4277 | 0.91052 | 0.8672 | 0.42068
24.425 | 59.7929 | 59.9846 | 60.4636 | 0.90784 | 0.86388 | 0.41875
24.4292 | 59.8245 | 60.0262 | 60.4933 | 0.90509 | 0.8605 | 0.41675
24.4334 | 59.817 | 60.0288 | 60.505 | 0.90229 | 0.85714 | 0.41475
24.4375 | 59.8063 | 60.0029 | 60.5 | 0.89955 | 0.85371 | 0.41271
24.4417 | 59.7722 | 59.9527 | 60.4832 | 0.89694 | 0.85047 | 0.41072
24.4459 | 59.7239 | 59.8811 | 60.4548 | 0.89448 | 0.84752 | 0.40881
24.45 | 59.6782 | 59.8161 | 60.4294 | 0.89228 | 0.84484 | 0.40702
24.4542 | 59.6304 | 59.7439 | 60.4051 | 0.89015 | 0.84236 | 0.4053
24.4584 | 59.5873 | 59.6825 | 60.3829 | 0.8883 | 0.84018 | 0.40371
24.4625 | 59.5509 | 59.6406 | 60.365 | 0.88663 | 0.83826 | 0.40225
24.4667 | 59.5308 | 59.6059 | 60.352 | 0.88507 | 0.8365 | 0.40083
24.4709 | 59.5107 | 59.5758 | 60.3455 | 0.88356 | 0.83493 | 0.39943
24.475 | 59.5165 | 59.5655 | 60.3507 | 0.88208 | 0.8334 | 0.39803
24.4792 | 59.5345 | 59.5776 | 60.3697 | 0.88062 | 0.83178 | 0.39661
24.4834 | 59.5517 | 59.5952 | 60.3868 | 0.87912 | 0.83021 | 0.39521
24.4875 | 59.5676 | 59.6189 | 60.3994 | 0.8777 | 0.82875 | 0.3938
24.4917 | 59.5873 | 59.639 | 60.4097 | 0.87606 | 0.82718 | 0.39233
24.4959 | 59.602 | 59.6519 | 60.4176 | 0.87439 | 0.82542 | 0.39075
24.5 | 59.622 | 59.6686 | 60.4288 | 0.87266 | 0.82362 | 0.38916
24.5042 | 59.6423 | 59.6957 | 60.4395 | 0.871 | 0.8218 | 0.38762
24.5084 | 59.6451 | 59.7086 | 60.4414 | 0.86926 | 0.82003 | 0.38611
24.5125 | 59.6425 | 59.6991 | 60.4311 | 0.86757 | 0.81831 | 0.3846
24.5167 | 59.6372 | 59.6807 | 60.4231 | 0.86578 | 0.8166 | 0.38307
24.5209 | 59.642 | 59.6677 | 60.4201 | 0.86401 | 0.81473 | 0.38154
24.525 | 59.6348 | 59.6556 | 60.4218 | 0.86236 | 0.81302 | 0.38009
24.5292 | 59.6341 | 59.6453 | 60.4228 | 0.86077 | 0.81152 | 0.37875
24.5334 | 59.625 | 59.6316 | 60.4179 | 0.85918 | 0.81012 | 0.37742
24.5375 | 59.6121 | 59.6033 | 60.4114 | 0.85753 | 0.80865 | 0.37606
24.5417 | 59.6131 | 59.585 | 60.4109 | 0.856 | 0.80724 | 0.3747
24.5459 | 59.6207 | 59.5892 | 60.4175 | 0.85441 | 0.80583 | 0.37338
24.55 | 59.6196 | 59.6014 | 60.4246 | 0.85296 | 0.80448 | 0.37212
24.5542 | 59.6152 | 59.6 | 60.4288 | 0.8515 | 0.80329 | 0.37086
24.5584 | 59.6178 | 59.6016 | 60.4284 | 0.85001 | 0.80204 | 0.36958
24.5625 | 59.6082 | 59.6053 | 60.4291 | 0.84848 | 0.8006 | 0.36829
24.5667 | 59.6137 | 59.6127 | 60.4343 | 0.84706 | 0.79913 | 0.36701
24.5709 | 59.618 | 59.6317 | 60.4394 | 0.84564 | 0.79782 | 0.36575
24.575 | 59.6142 | 59.6472 | 60.4429 | 0.8442 | 0.79647 | 0.36453
24.5792 | 59.616 | 59.6445 | 60.4458 | 0.84278 | 0.79506 | 0.36329
24.5834 | 59.6193 | 59.6375 | 60.4464 | 0.84133 | 0.79363 | 0.36204
24.5875 | 59.6159 | 59.6419 | 60.4459 | 0.83996 | 0.79217 | 0.36083
24.5917 | 59.6156 | 59.6429 | 60.4484 | 0.83859 | 0.79072 | 0.35964
24.5959 | 59.6133 | 59.6436 | 60.4501 | 0.83721 | 0.78937 | 0.35843
24.6 | 59.6138 | 59.6426 | 60.4507 | 0.83578 | 0.78803 | 0.35725
24.6042 | 59.6192 | 59.638 | 60.4547 | 0.83442 | 0.78662 | 0.35609
24.6084 | 59.6172 | 59.6314 | 60.4568 | 0.83312 | 0.78525 | 0.35493
24.6125 | 59.6134 | 59.6238 | 60.454 | 0.83184 | 0.78399 | 0.35381
24.6167 | 59.6037 | 59.6201 | 60.4542 | 0.8305 | 0.78273 | 0.3527
24.6209 | 59.601 | 59.6154 | 60.4592 | 0.82918 | 0.78142 | 0.35153
24.625 | 59.6061 | 59.6124 | 60.463 | 0.82788 | 0.78017 | 0.3504
24.6292 | 59.6145 | 59.6265 | 60.4652 | 0.8266 | 0.77889 | 0.34936
24.6334 | 59.6149 | 59.6347 | 60.4649 | 0.82537 | 0.77762 | 0.34831
24.6375 | 59.614 | 59.6224 | 60.4603 | 0.82412 | 0.77648 | 0.34721
24.6417 | 59.6164 | 59.6195 | 60.4601 | 0.82278 | 0.7753 | 0.34612
24.6459 | 59.615 | 59.6111 | 60.4715 | 0.82148 | 0.774 | 0.34503
24.65 | 59.6085 | 59.6022 | 60.4798 | 0.82033 | 0.77276 | 0.34398
24.6542 | 59.6077 | 59.6225 | 60.4752 | 0.81913 | 0.77158 | 0.34303
24.6584 | 59.5958 | 59.6337 | 60.469 | 0.8179 | 0.77036 | 0.34205
24.6625 | 59.5904 | 59.6287 | 60.4657 | 0.8167 | 0.7692 | 0.34095
24.6667 | 59.6065 | 59.6311 | 60.4684 | 0.81549 | 0.76804 | 0.33988
24.6709 | 59.6176 | 59.628 | 60.482 | 0.81423 | 0.76675 | 0.33891
24.675 | 59.6202 | 59.6224 | 60.4889 | 0.8131 | 0.76551 | 0.33798
24.6792 | 59.6091 | 59.6103 | 60.4823 | 0.81206 | 0.76451 | 0.33704
24.6834 | 59.5957 | 59.6004 | 60.4764 | 0.81086 | 0.76343 | 0.33605
24.6875 | 59.5832 | 59.6104 | 60.475 | 0.80963 | 0.7621 | 0.33504
24.6917 | 59.5864 | 59.6222 | 60.4789 | 0.80847 | 0.76084 | 0.33408
24.6959 | 59.6018 | 59.6475 | 60.4834 | 0.80742 | 0.75974 | 0.33321
24.7 | 59.599 | 59.6638 | 60.4817 | 0.80635 | 0.75863 | 0.33233
24.7042 | 59.5939 | 59.6253 | 60.4811 | 0.8053 | 0.75756 | 0.33139
24.7084 | 59.5936 | 59.5974 | 60.4846 | 0.80414 | 0.75645 | 0.33043
24.7125 | 59.6017 | 59.6047 | 60.4903 | 0.8029 | 0.75511 | 0.32952
24.7167 | 59.604 | 59.6093 | 60.4938 | 0.80187 | 0.75385 | 0.32868
24.7209 | 59.5965 | 59.6268 | 60.488 | 0.80092 | 0.75296 | 0.32785
24.725 | 59.5752 | 59.6385 | 60.4779 | 0.79994 | 0.75199 | 0.32699
24.7292 | 59.561 | 59.6249 | 60.4716 | 0.79878 | 0.75072 | 0.32614
24.7334 | 59.566 | 59.6236 | 60.473 | 0.79767 | 0.74945 | 0.3253
24.7375 | 59.5869 | 59.6413 | 60.4779 | 0.79664 | 0.74828 | 0.32452
24.7417 | 59.5942 | 59.6516 | 60.4779 | 0.79575 | 0.74715 | 0.32378
24.7459 | 59.5862 | 59.635 | 60.4761 | 0.79479 | 0.74614 | 0.32303
24.75 | 59.5783 | 59.6176 | 60.4742 | 0.7937 | 0.74504 | 0.32224
24.7542 | 59.5706 | 59.618 | 60.4723 | 0.79257 | 0.74374 | 0.32147
24.7584 | 59.5788 | 59.6193 | 60.4736 | 0.79156 | 0.74253 | 0.32076
24.7625 | 59.5832 | 59.6302 | 60.4731 | 0.79063 | 0.74157 | 0.32007
24.7667 | 59.5686 | 59.6287 | 60.4646 | 0.78973 | 0.74063 | 0.31939
24.7709 | 59.5529 | 59.6076 | 60.4533 | 0.7888 | 0.73952 | 0.31876
24.775 | 59.5541 | 59.5942 | 60.4473 | 0.78771 | 0.73841 | 0.31812
24.7792 | 59.5542 | 59.5969 | 60.4442 | 0.78675 | 0.73735 | 0.31748
24.7834 | 59.5635 | 59.6005 | 60.443 | 0.78588 | 0.7364 | 0.31691
24.7875 | 59.5729 | 59.5861 | 60.4444 | 0.785 | 0.73558 | 0.31638
24.7917 | 59.5658 | 59.5694 | 60.4425 | 0.78395 | 0.73472 | 0.31582
24.7959 | 59.5581 | 59.5596 | 60.4395 | 0.78304 | 0.73372 | 0.31525
24.8 | 59.5614 | 59.5575 | 60.4443 | 0.78206 | 0.73275 | 0.31466
24.8042 | 59.5588 | 59.5754 | 60.4555 | 0.78111 | 0.73189 | 0.31405
24.8084 | 59.5411 | 59.5872 | 60.4632 | 0.78028 | 0.73107 | 0.31345
24.8125 | 59.5395 | 59.5757 | 60.468 | 0.77944 | 0.73024 | 0.31288
24.8167 | 59.5351 | 59.5663 | 60.4707 | 0.77847 | 0.72936 | 0.31226
24.8209 | 59.5313 | 59.5613 | 60.4684 | 0.77757 | 0.7284 | 0.31159
24.825 | 59.5399 | 59.5599 | 60.4702 | 0.77679 | 0.72749 | 0.31095
24.8292 | 59.5455 | 59.5667 | 60.4805 | 0.77591 | 0.72669 | 0.31028
24.8334 | 59.536 | 59.5676 | 60.4845 | 0.77504 | 0.72588 | 0.30963
24.8375 | 59.5303 | 59.5547 | 60.4848 | 0.77421 | 0.72506 | 0.309
24.8417 | 59.5332 | 59.5444 | 60.4868 | 0.77333 | 0.72424 | 0.30835
24.8459 | 59.5338 | 59.5457 | 60.4788 | 0.77239 | 0.72337 | 0.3077
24.85 | 59.5383 | 59.5458 | 60.4731 | 0.77156 | 0.72254 | 0.30709
24.8542 | 59.5315 | 59.5447 | 60.4754 | 0.77082 | 0.72182 | 0.30647
24.8584 | 59.5274 | 59.5419 | 60.4735 | 0.76993 | 0.7211 | 0.30584
24.8625 | 59.5058 | 59.5381 | 60.4765 | 0.76916 | 0.72024 | 0.30525
24.8667 | 59.4977 | 59.5358 | 60.483 | 0.76834 | 0.71942 | 0.30465
24.8709 | 59.5089 | 59.5392 | 60.4838 | 0.76755 | 0.71867 | 0.30403
24.875 | 59.5072 | 59.5436 | 60.4844 | 0.7667 | 0.71792 | 0.30343
24.8792 | 59.5086 | 59.5218 | 60.4819 | 0.76607 | 0.71725 | 0.30286
24.8834 | 59.5099 | 59.5017 | 60.4778 | 0.76528 | 0.7166 | 0.30226
24.8875 | 59.4995 | 59.5066 | 60.4766 | 0.76447 | 0.71577 | 0.30167
24.8917 | 59.4967 | 59.5079 | 60.4778 | 0.76364 | 0.71496 | 0.30108
24.8959 | 59.4996 | 59.5187 | 60.4886 | 0.76294 | 0.71436 | 0.30045
24.9 | 59.4995 | 59.5305 | 60.498 | 0.76214 | 0.71376 | 0.29983
24.9042 | 59.4831 | 59.5151 | 60.4966 | 0.76151 | 0.713 | 0.29928
24.9084 | 59.4713 | 59.4988 | 60.4948 | 0.76079 | 0.71229 | 0.29872
24.9125 | 59.4682 | 59.4992 | 60.4856 | 0.76006 | 0.71158 | 0.2981
24.9167 | 59.4644 | 59.4999 | 60.4775 | 0.75928 | 0.71086 | 0.2975
24.9209 | 59.4714 | 59.4904 | 60.4871 | 0.75868 | 0.71028 | 0.2969
24.925 | 59.478 | 59.4854 | 60.4959 | 0.75798 | 0.70972 | 0.2963
24.9292 | 59.4702 | 59.4905 | 60.4976 | 0.7573 | 0.70895 | 0.29576
24.9334 | 59.4632 | 59.4889 | 60.4983 | 0.75659 | 0.70821 | 0.29524
24.9375 | 59.4642 | 59.4842 | 60.4946 | 0.75589 | 0.70772 | 0.29461
24.9417 | 59.4584 | 59.4833 | 60.4923 | 0.75517 | 0.70719 | 0.29398
24.9459 | 59.4491 | 59.4667 | 60.4971 | 0.7546 | 0.70649 | 0.29341
24.95 | 59.4413 | 59.4507 | 60.5016 | 0.75398 | 0.70586 | 0.29286
24.9542 | 59.4304 | 59.4644 | 60.4986 | 0.75333 | 0.70527 | 0.29231
24.9584 | 59.4243 | 59.4715 | 60.4941 | 0.75268 | 0.70466 | 0.29175
24.9625 | 59.4311 | 59.4489 | 60.4935 | 0.75208 | 0.70425 | 0.29117
24.9667 | 59.4365 | 59.4371 | 60.4957 | 0.75145 | 0.70382 | 0.29058
24.9709 | 59.4349 | 59.4402 | 60.5017 | 0.75086 | 0.70306 | 0.29002
24.975 | 59.4357 | 59.4367 | 60.5053 | 0.75021 | 0.70239 | 0.28948
24.9792 | 59.4304 | 59.439 | 60.5046 | 0.74957 | 0.7021 | 0.28892
24.9834 | 59.4309 | 59.4414 | 60.503 | 0.74884 | 0.70171 | 0.28834
24.9875 | 59.4245 | 59.4065 | 60.4985 | 0.74828 | 0.70118 | 0.28777
24.9917 | 59.423 | 59.3807 | 60.4979 | 0.74761 | 0.70071 | 0.28722
24.9959 | 59.4238 | 59.3999 | 60.5024 | 0.74696 | 0.70021 | 0.28664
25 | 59.4222 | 59.4041 | 60.5021 | 0.74622 | 0.69972 | 0.28608
25.0042 | 59.4305 | 59.3836 | 60.5005 | 0.74559 | 0.6996 | 0.28557
25.0084 | 59.4371 | 59.3729 | 60.5012 | 0.74486 | 0.69938 | 0.28502
25.0125 | 59.4416 | 59.3646 | 60.5 | 0.74412 | 0.69875 | 0.28443
25.0167 | 59.4336 | 59.3603 | 60.5006 | 0.74344 | 0.69823 | 0.28387
25.0209 | 59.4339 | 59.3818 | 60.5061 | 0.74272 | 0.69804 | 0.28334
25.025 | 59.4235 | 59.3935 | 60.5061 | 0.74197 | 0.69777 | 0.2828
25.0292 | 59.3974 | 59.3639 | 60.5007 | 0.74141 | 0.69741 | 0.28227
25.0334 | 59.4009 | 59.3499 | 60.5013 | 0.74072 | 0.69699 | 0.28172
25.0375 | 59.398 | 59.3717 | 60.5025 | 0.74 | 0.69641 | 0.28114
25.0417 | 59.384 | 59.3831 | 60.5009 | 0.73941 | 0.69591 | 0.28062
25.0459 | 59.4035 | 59.3811 | 60.5031 | 0.73886 | 0.69576 | 0.28012
25.05 | 59.3928 | 59.373 | 60.5028 | 0.7382 | 0.69548 | 0.27957
25.0542 | 59.3698 | 59.3589 | 60.4987 | 0.73765 | 0.6948 | 0.27903
25.0584 | 59.3777 | 59.3534 | 60.502 | 0.73708 | 0.69421 | 0.2785
25.0625 | 59.3693 | 59.3784 | 60.5079 | 0.73639 | 0.69383 | 0.27794
25.0667 | 59.358 | 59.3874 | 60.5064 | 0.73588 | 0.69349 | 0.27742
25.0709 | 59.3597 | 59.358 | 60.5046 | 0.73544 | 0.69313 | 0.27693
25.075 | 59.352 | 59.3383 | 60.5041 | 0.73485 | 0.69271 | 0.27639
25.0792 | 59.3339 | 59.3418 | 60.4989 | 0.73432 | 0.69205 | 0.27583
25.0834 | 59.3399 | 59.3512 | 60.4987 | 0.73381 | 0.69152 | 0.27533
25.0875 | 59.3469 | 59.3526 | 60.5058 | 0.73325 | 0.69134 | 0.2748
25.0917 | 59.3423 | 59.3448 | 60.506 | 0.73271 | 0.6911 | 0.27427
25.0959 | 59.3393 | 59.3176 | 60.501 | 0.7323 | 0.69059 | 0.2738
25.1 | 59.3381 | 59.3051 | 60.5019 | 0.7317 | 0.69005 | 0.2733
25.1042 | 59.3289 | 59.3269 | 60.5053 | 0.73112 | 0.68963 | 0.27269
25.1084 | 59.3276 | 59.3406 | 60.5072 | 0.73058 | 0.68928 | 0.27215
25.1125 | 59.3318 | 59.3242 | 60.5119 | 0.73011 | 0.68908 | 0.27169
25.1167 | 59.3206 | 59.3043 | 60.5118 | 0.72957 | 0.68876 | 0.27118
25.1209 | 59.3101 | 59.2965 | 60.5013 | 0.7291 | 0.68818 | 0.27065
25.125 | 59.3028 | 59.298 | 60.498 | 0.72859 | 0.68767 | 0.27012
25.1292 | 59.3059 | 59.3161 | 60.5078 | 0.72801 | 0.6874 | 0.26955
25.1334 | 59.3052 | 59.3192 | 60.513 | 0.72752 | 0.68716 | 0.26901
25.1375 | 59.3074 | 59.298 | 60.5102 | 0.72706 | 0.68678 | 0.26859
25.1417 | 59.3067 | 59.2854 | 60.5103 | 0.72657 | 0.68631 | 0.26809
25.1459 | 59.306 | 59.2969 | 60.5098 | 0.72592 | 0.68575 | 0.26746
25.15 | 59.3051 | 59.3077 | 60.5101 | 0.72539 | 0.68535 | 0.26688
25.1542 | 59.3097 | 59.304 | 60.5192 | 0.72483 | 0.68512 | 0.26641
25.1584 | 59.2997 | 59.2874 | 60.5186 | 0.72437 | 0.68484 | 0.26593
25.1625 | 59.2746 | 59.2586 | 60.5013 | 0.72389 | 0.68438 | 0.26544
25.1667 | 59.2678 | 59.2564 | 60.4979 | 0.72338 | 0.68386 | 0.2649
25.1709 | 59.2723 | 59.2823 | 60.5141 | 0.72269 | 0.68339 | 0.26423
25.175 | 59.2808 | 59.3013 | 60.5278 | 0.72219 | 0.68304 | 0.26364
25.1792 | 59.2908 | 59.3041 | 60.5394 | 0.72177 | 0.68274 | 0.26321
25.1834 | 59.273 | 59.2822 | 60.5314 | 0.72142 | 0.68236 | 0.26277
25.1875 | 59.2314 | 59.2419 | 60.4984 | 0.72098 | 0.68197 | 0.26225
25.1917 | 59.2183 | 59.2223 | 60.4791 | 0.72046 | 0.68157 | 0.26172
25.1959 | 59.2172 | 59.2221 | 60.481 | 0.71991 | 0.68119 | 0.26118
25.2 | 59.2458 | 59.2355 | 60.4974 | 0.71939 | 0.68083 | 0.26067
25.2042 | 59.2747 | 59.2675 | 60.5233 | 0.71899 | 0.68044 | 0.26021
25.2084 | 59.2848 | 59.2891 | 60.5398 | 0.71842 | 0.67996 | 0.2597
25.2125 | 59.2884 | 59.2969 | 60.5475 | 0.71779 | 0.67946 | 0.25909
25.2167 | 59.2794 | 59.2883 | 60.5439 | 0.71705 | 0.679 | 0.25848
25.2209 | 59.2667 | 59.2668 | 60.5331 | 0.71647 | 0.67847 | 0.25791
25.225 | 59.251 | 59.2469 | 60.5241 | 0.71588 | 0.67792 | 0.25735
25.2292 | 59.2293 | 59.2318 | 60.511 | 0.71535 | 0.67742 | 0.25679
25.2334 | 59.2226 | 59.241 | 60.5113 | 0.71468 | 0.6769 | 0.25622
25.2375 | 59.2367 | 59.2612 | 60.5288 | 0.71401 | 0.67631 | 0.2556
25.2417 | 59.262 | 59.2852 | 60.5495 | 0.71328 | 0.67567 | 0.25495
25.2459 | 59.2892 | 59.3227 | 60.5759 | 0.71264 | 0.67494 | 0.25429
25.25 | 59.3082 | 59.361 | 60.6018 | 0.71181 | 0.67397 | 0.25351
25.2542 | 59.3317 | 59.3973 | 60.6223 | 0.71079 | 0.67288 | 0.2526
25.2584 | 59.352 | 59.4321 | 60.641 | 0.70964 | 0.67173 | 0.25165
25.2625 | 59.3829 | 59.4641 | 60.662 | 0.70849 | 0.6704 | 0.25063
25.2667 | 59.3988 | 59.4777 | 60.6696 | 0.70733 | 0.669 | 0.24962
25.2709 | 59.3938 | 59.4777 | 60.6664 | 0.70615 | 0.66761 | 0.24861
25.275 | 59.4064 | 59.4981 | 60.6732 | 0.70472 | 0.666 | 0.24749
25.2792 | 59.4285 | 59.5301 | 60.6868 | 0.70313 | 0.66416 | 0.24624
25.2834 | 59.4753 | 59.5789 | 60.7146 | 0.70146 | 0.66227 | 0.24498
25.2875 | 59.532 | 59.6544 | 60.7526 | 0.69985 | 0.66028 | 0.24373
25.2917 | 59.5794 | 59.7218 | 60.785 | 0.69796 | 0.65799 | 0.24235
25.2959 | 59.6153 | 59.7739 | 60.8105 | 0.69591 | 0.65551 | 0.24084
25.3 | 59.6668 | 59.8402 | 60.8442 | 0.6935 | 0.65274 | 0.23915
25.3042 | 59.7258 | 59.9181 | 60.8907 | 0.69102 | 0.6496 | 0.23728
25.3084 | 59.7588 | 59.964 | 60.9255 | 0.68857 | 0.64651 | 0.23544
25.3125 | 59.7769 | 59.9899 | 60.9473 | 0.68618 | 0.64352 | 0.23363
25.3167 | 59.7519 | 59.9735 | 60.9469 | 0.68367 | 0.64049 | 0.23177
25.3209 | 59.7196 | 59.9138 | 60.9267 | 0.68113 | 0.63737 | 0.2298
25.325 | 59.6903 | 59.8592 | 60.9106 | 0.67878 | 0.6345 | 0.22791
25.3292 | 59.6625 | 59.8112 | 60.8995 | 0.67662 | 0.63184 | 0.22612
25.3334 | 59.6124 | 59.7516 | 60.881 | 0.67483 | 0.62955 | 0.22453
25.3375 | 59.5534 | 59.6741 | 60.8493 | 0.67314 | 0.62766 | 0.2231
25.3417 | 59.5062 | 59.6062 | 60.8208 | 0.67151 | 0.62589 | 0.22169
25.3459 | 59.4697 | 59.5523 | 60.8015 | 0.66995 | 0.62414 | 0.22028
25.35 | 59.4681 | 59.5256 | 60.8 | 0.66864 | 0.62261 | 0.21896
25.3542 | 59.4701 | 59.5268 | 60.8147 | 0.66746 | 0.62139 | 0.21777
25.3584 | 59.4685 | 59.5282 | 60.8264 | 0.66625 | 0.62019 | 0.2166
25.3625 | 59.4713 | 59.5244 | 60.8349 | 0.66501 | 0.61894 | 0.21537
25.3667 | 59.4901 | 59.5331 | 60.8483 | 0.66357 | 0.61758 | 0.21406
25.3709 | 59.5171 | 59.5662 | 60.8707 | 0.66218 | 0.6161 | 0.21267
25.375 | 59.548 | 59.6016 | 60.8957 | 0.66076 | 0.61462 | 0.2113
25.3792 | 59.5674 | 59.6287 | 60.9158 | 0.65936 | 0.61321 | 0.20995
25.3834 | 59.576 | 59.644 | 60.9243 | 0.65775 | 0.61169 | 0.20858
25.3875 | 59.5825 | 59.649 | 60.9238 | 0.65614 | 0.60993 | 0.20714
25.3917 | 59.5898 | 59.6501 | 60.9247 | 0.65447 | 0.6082 | 0.20569
25.3959 | 59.6 | 59.6568 | 60.9257 | 0.65287 | 0.60655 | 0.2043
25.4 | 59.5926 | 59.6528 | 60.9274 | 0.65131 | 0.60498 | 0.20297
25.4042 | 59.5866 | 59.6299 | 60.9263 | 0.64974 | 0.60341 | 0.20167
25.4084 | 59.5715 | 59.6042 | 60.9212 | 0.64817 | 0.60191 | 0.20039
25.4125 | 59.5623 | 59.5865 | 60.9159 | 0.64662 | 0.60038 | 0.19916
25.4167 | 59.5582 | 59.5723 | 60.9154 | 0.64519 | 0.59899 | 0.19794
25.4209 | 59.5549 | 59.5561 | 60.9179 | 0.64372 | 0.59775 | 0.19675
25.425 | 59.5469 | 59.5461 | 60.9226 | 0.64237 | 0.59655 | 0.19559
25.4292 | 59.5467 | 59.5365 | 60.9309 | 0.64092 | 0.59525 | 0.19444
25.4334 | 59.5454 | 59.5355 | 60.9358 | 0.63954 | 0.59398 | 0.1933
25.4375 | 59.5344 | 59.5397 | 60.9376 | 0.63822 | 0.59283 | 0.19218
25.4417 | 59.5386 | 59.5475 | 60.9422 | 0.63689 | 0.59165 | 0.19105
25.4459 | 59.5351 | 59.5524 | 60.95 | 0.6355 | 0.59039 | 0.18989
25.45 | 59.5344 | 59.5598 | 60.9586 | 0.63415 | 0.58906 | 0.18875
25.4542 | 59.5409 | 59.5732 | 60.9675 | 0.63286 | 0.58777 | 0.18765
25.4584 | 59.5378 | 59.5816 | 60.9718 | 0.63155 | 0.58645 | 0.18657
25.4625 | 59.5274 | 59.5766 | 60.9695 | 0.63027 | 0.58519 | 0.18545
25.4667 | 59.5282 | 59.5685 | 60.9701 | 0.62893 | 0.58387 | 0.18432
25.4709 | 59.5282 | 59.573 | 60.9758 | 0.6276 | 0.58243 | 0.18318
25.475 | 59.5282 | 59.574 | 60.9801 | 0.62631 | 0.58104 | 0.18207
25.4792 | 59.5312 | 59.5779 | 60.9793 | 0.62509 | 0.57978 | 0.18102
25.4834 | 59.5274 | 59.576 | 60.9748 | 0.62378 | 0.57855 | 0.17996
25.4875 | 59.5181 | 59.5503 | 60.97 | 0.62252 | 0.57728 | 0.17885
25.4917 | 59.5141 | 59.5316 | 60.9699 | 0.62127 | 0.57603 | 0.17774
25.4959 | 59.5126 | 59.5328 | 60.9756 | 0.62003 | 0.57473 | 0.17668
25.5 | 59.5006 | 59.5327 | 60.9781 | 0.61885 | 0.5735 | 0.17567
25.5042 | 59.4971 | 59.5376 | 60.9712 | 0.61767 | 0.57238 | 0.17467
25.5084 | 59.5006 | 59.5391 | 60.963 | 0.6164 | 0.57124 | 0.17365
25.5125 | 59.4986 | 59.5254 | 60.9616 | 0.61515 | 0.57002 | 0.17258
25.5167 | 59.5039 | 59.5196 | 60.9649 | 0.614 | 0.56881 | 0.17154
25.5209 | 59.5048 | 59.5134 | 60.9697 | 0.61279 | 0.56765 | 0.17057
25.525 | 59.4908 | 59.5074 | 60.9694 | 0.61155 | 0.5665 | 0.16963
25.5292 | 59.4748 | 59.5004 | 60.9625 | 0.61042 | 0.56539 | 0.16864
25.5334 | 59.4627 | 59.4908 | 60.9567 | 0.60925 | 0.56426 | 0.16762
25.5375 | 59.4599 | 59.5064 | 60.9527 | 0.60801 | 0.56297 | 0.16665
25.5417 | 59.4563 | 59.5201 | 60.9521 | 0.60685 | 0.5617 | 0.16572
25.5459 | 59.4593 | 59.5102 | 60.954 | 0.60576 | 0.56068 | 0.16477
25.55 | 59.4616 | 59.5012 | 60.9515 | 0.60461 | 0.55964 | 0.16382
25.5542 | 59.4494 | 59.4703 | 60.9517 | 0.60344 | 0.55842 | 0.16288
25.5584 | 59.4412 | 59.4427 | 60.9526 | 0.60231 | 0.55721 | 0.16194
25.5625 | 59.4323 | 59.4604 | 60.9438 | 0.6012 | 0.55606 | 0.16103
25.5667 | 59.4204 | 59.4754 | 60.9358 | 0.60006 | 0.55491 | 0.16016
25.5709 | 59.4056 | 59.4757 | 60.932 | 0.59903 | 0.55387 | 0.15924
25.575 | 59.3984 | 59.4758 | 60.9278 | 0.59794 | 0.55282 | 0.15831
25.5792 | 59.4025 | 59.464 | 60.9274 | 0.5968 | 0.55156 | 0.15747
25.5834 | 59.3993 | 59.4538 | 60.9281 | 0.5957 | 0.5503 | 0.15664
25.5875 | 59.401 | 59.442 | 60.9251 | 0.5947 | 0.54929 | 0.15576
25.5917 | 59.395 | 59.4308 | 60.9209 | 0.59363 | 0.54825 | 0.15488
25.5959 | 59.3808 | 59.4238 | 60.9198 | 0.59249 | 0.54707 | 0.15403
25.6 | 59.3675 | 59.4153 | 60.9168 | 0.59142 | 0.5459 | 0.1532
25.6042 | 59.3599 | 59.4253 | 60.9061 | 0.5904 | 0.54483 | 0.15241
25.6084 | 59.3455 | 59.4353 | 60.8963 | 0.58942 | 0.54375 | 0.15165
25.6125 | 59.3372 | 59.4216 | 60.8915 | 0.58839 | 0.54267 | 0.15085
25.6167 | 59.3338 | 59.4126 | 60.8882 | 0.58737 | 0.54158 | 0.15007
25.6209 | 59.3366 | 59.4149 | 60.8883 | 0.58633 | 0.54037 | 0.14938
25.625 | 59.3387 | 59.4141 | 60.8875 | 0.58537 | 0.53916 | 0.14871
25.6292 | 59.3293 | 59.4054 | 60.8823 | 0.58443 | 0.53821 | 0.148
25.6334 | 59.3193 | 59.3958 | 60.8784 | 0.58344 | 0.53722 | 0.14728
25.6375 | 59.3141 | 59.3845 | 60.8796 | 0.58236 | 0.53603 | 0.14659
25.6417 | 59.3132 | 59.3708 | 60.8795 | 0.58132 | 0.53489 | 0.14592
25.6459 | 59.3065 | 59.3798 | 60.8735 | 0.58043 | 0.53387 | 0.14531
25.65 | 59.2922 | 59.3809 | 60.8649 | 0.57956 | 0.53288 | 0.1447
25.6542 | 59.2717 | 59.3589 | 60.8565 | 0.57862 | 0.53191 | 0.14407
25.6584 | 59.2639 | 59.3435 | 60.8518 | 0.57757 | 0.53094 | 0.14345
25.6625 | 59.2689 | 59.3331 | 60.8507 | 0.57661 | 0.52988 | 0.14289
25.6667 | 59.2798 | 59.3228 | 60.8489 | 0.57568 | 0.52889 | 0.14237
25.6709 | 59.2765 | 59.3124 | 60.8435 | 0.57484 | 0.52811 | 0.14185
25.675 | 59.2602 | 59.3008 | 60.8391 | 0.5739 | 0.52729 | 0.1413
25.6792 | 59.2446 | 59.2886 | 60.8435 | 0.57294 | 0.52633 | 0.14072
25.6834 | 59.2375 | 59.2838 | 60.8525 | 0.57189 | 0.52539 | 0.14014
25.6875 | 59.2366 | 59.2924 | 60.8607 | 0.57099 | 0.52454 | 0.13959
25.6917 | 59.2237 | 59.2939 | 60.8645 | 0.57019 | 0.52371 | 0.13905
25.6959 | 59.2144 | 59.2764 | 60.8595 | 0.56934 | 0.52291 | 0.13847
25.7 | 59.2011 | 59.2629 | 60.8562 | 0.56836 | 0.52204 | 0.13784
25.7042 | 59.1882 | 59.2576 | 60.8636 | 0.56745 | 0.52106 | 0.13717
25.7084 | 59.1887 | 59.2549 | 60.8715 | 0.56662 | 0.52014 | 0.13653
25.7125 | 59.1879 | 59.2576 | 60.8789 | 0.56573 | 0.51935 | 0.13594
25.7167 | 59.1674 | 59.251 | 60.8801 | 0.56491 | 0.51854 | 0.13534
25.7209 | 59.1603 | 59.2235 | 60.8685 | 0.56403 | 0.51771 | 0.1347
25.725 | 59.1642 | 59.2046 | 60.8623 | 0.56303 | 0.51685 | 0.13405
25.7292 | 59.1495 | 59.2014 | 60.8604 | 0.56212 | 0.51594 | 0.13342
25.7334 | 59.147 | 59.1934 | 60.8568 | 0.56134 | 0.51512 | 0.13284
25.7375 | 59.1267 | 59.1942 | 60.8595 | 0.56052 | 0.51438 | 0.13228
25.7417 | 59.1032 | 59.1897 | 60.859 | 0.55955 | 0.51358 | 0.13169
25.7459 | 59.084 | 59.1695 | 60.8575 | 0.55875 | 0.51273 | 0.13108
25.75 | 59.0811 | 59.1598 | 60.8629 | 0.55786 | 0.51192 | 0.13048
25.7542 | 59.0781 | 59.1523 | 60.861 | 0.55706 | 0.5111 | 0.12992
25.7584 | 59.0602 | 59.1376 | 60.854 | 0.55627 | 0.51031 | 0.12939
25.7625 | 59.0496 | 59.1166 | 60.8493 | 0.55553 | 0.50965 | 0.12884
25.7667 | 59.0391 | 59.0987 | 60.8454 | 0.55458 | 0.50891 | 0.12823
25.7709 | 59.026 | 59.0932 | 60.8526 | 0.55374 | 0.50804 | 0.12763
25.775 | 59.0231 | 59.0898 | 60.8641 | 0.55293 | 0.50725 | 0.12706
25.7792 | 59.013 | 59.0947 | 60.8674 | 0.55217 | 0.50655 | 0.12652
25.7834 | 58.9869 | 59.0899 | 60.8637 | 0.55133 | 0.50584 | 0.12598
25.7875 | 58.9609 | 59.0542 | 60.854 | 0.55061 | 0.50514 | 0.12539
25.7917 | 58.9461 | 59.0275 | 60.8495 | 0.54975 | 0.50442 | 0.12477
25.7959 | 58.9359 | 59.0261 | 60.8521 | 0.54895 | 0.50353 | 0.12419
25.8 | 58.9265 | 59.0216 | 60.8548 | 0.5482 | 0.50271 | 0.12366
25.8042 | 58.9215 | 59.0165 | 60.8588 | 0.54753 | 0.50218 | 0.12313
25.8084 | 58.9076 | 59.0083 | 60.8579 | 0.54672 | 0.50158 | 0.12256
25.8125 | 58.8895 | 58.9772 | 60.8525 | 0.54596 | 0.5008 | 0.12201
25.8167 | 58.879 | 58.9533 | 60.854 | 0.54518 | 0.50005 | 0.12145
25.8209 | 58.8735 | 58.9632 | 60.8595 | 0.54442 | 0.49933 | 0.12086
25.825 | 58.8578 | 58.9649 | 60.8607 | 0.54369 | 0.49863 | 0.12031
25.8292 | 58.8352 | 58.9382 | 60.8605 | 0.54307 | 0.49816 | 0.11981
25.8334 | 58.8178 | 58.9146 | 60.86 | 0.54235 | 0.49765 | 0.11926
25.8375 | 58.7999 | 58.8991 | 60.8527 | 0.54158 | 0.49682 | 0.1187
25.8417 | 58.7904 | 58.8855 | 60.8504 | 0.54088 | 0.49606 | 0.11817
25.8459 | 58.7951 | 58.8898 | 60.8612 | 0.54019 | 0.4956 | 0.1176
25.85 | 58.7905 | 58.8887 | 60.8657 | 0.53946 | 0.4951 | 0.11703
25.8542 | 58.7689 | 58.8555 | 60.8642 | 0.53881 | 0.4945 | 0.11655
25.8584 | 58.7604 | 58.8292 | 60.866 | 0.53806 | 0.4939 | 0.11604
25.8625 | 58.7476 | 58.8273 | 60.8626 | 0.53724 | 0.49323 | 0.11543
25.8667 | 58.7334 | 58.8237 | 60.8603 | 0.53646 | 0.49258 | 0.11487
25.8709 | 58.7235 | 58.8007 | 60.8671 | 0.53584 | 0.49225 | 0.11436
25.875 | 58.7129 | 58.775 | 60.8698 | 0.53505 | 0.49187 | 0.11383
25.8792 | 58.6871 | 58.7535 | 60.8646 | 0.53431 | 0.4912 | 0.1133
25.8834 | 58.6804 | 58.7336 | 60.8636 | 0.5335 | 0.49055 | 0.11278
25.8875 | 58.6924 | 58.7311 | 60.8656 | 0.53264 | 0.4902 | 0.11222
25.8917 | 58.6765 | 58.7274 | 60.8655 | 0.53184 | 0.48983 | 0.11169
25.8959 | 58.6681 | 58.6987 | 60.8697 | 0.53116 | 0.48936 | 0.11119
25.9 | 58.6494 | 58.6718 | 60.8733 | 0.53032 | 0.48888 | 0.11066
25.9042 | 58.6076 | 58.6732 | 60.8701 | 0.52947 | 0.48829 | 0.11013
25.9084 | 58.5956 | 58.6754 | 60.8699 | 0.52865 | 0.48769 | 0.10961
25.9125 | 58.5824 | 58.6557 | 60.8726 | 0.52788 | 0.48735 | 0.10908
25.9167 | 58.5583 | 58.6382 | 60.8724 | 0.52713 | 0.48697 | 0.10854
25.9209 | 58.5432 | 58.6211 | 60.8724 | 0.52645 | 0.48625 | 0.10805
25.925 | 58.5136 | 58.6003 | 60.8732 | 0.52567 | 0.48554 | 0.10755
25.9292 | 58.4935 | 58.6005 | 60.8714 | 0.52488 | 0.48506 | 0.10703
25.9334 | 58.4797 | 58.5972 | 60.8716 | 0.52413 | 0.48456 | 0.10651
25.9375 | 58.4584 | 58.5646 | 60.877 | 0.52343 | 0.48397 | 0.106
25.9417 | 58.4358 | 58.5314 | 60.8807 | 0.52275 | 0.4834 | 0.10548
25.9459 | 58.41 | 58.5278 | 60.8801 | 0.522 | 0.48267 | 0.10499
25.95 | 58.3794 | 58.5176 | 60.8788 | 0.52128 | 0.48197 | 0.1045
25.9542 | 58.3562 | 58.4917 | 60.8788 | 0.52059 | 0.48153 | 0.10396
25.9584 | 58.3413 | 58.4713 | 60.88 | 0.51986 | 0.48108 | 0.10342
25.9625 | 58.3125 | 58.4391 | 60.881 | 0.51919 | 0.48033 | 0.10295
25.9667 | 58.2896 | 58.4095 | 60.8821 | 0.51853 | 0.47964 | 0.10248
25.9709 | 58.2722 | 58.4011 | 60.8811 | 0.51779 | 0.47914 | 0.10197
25.975 | 58.2461 | 58.3893 | 60.8797 | 0.51701 | 0.4786 | 0.10145
25.9792 | 58.2232 | 58.3501 | 60.8842 | 0.51637 | 0.47809 | 0.10095
25.9834 | 58.2082 | 58.3189 | 60.8908 | 0.5156 | 0.47754 | 0.10045
25.9875 | 58.1776 | 58.3069 | 60.8915 | 0.51486 | 0.47683 | 0.099955
25.9917 | 58.1449 | 58.2898 | 60.8901 | 0.51414 | 0.47616 | 0.099475
25.9959 | 58.1284 | 58.2664 | 60.8918 | 0.51339 | 0.47575 | 0.098938
26 | 58.0942 | 58.2389 | 60.8906 | 0.51259 | 0.47528 | 0.09839
26.0042 | 58.0634 | 58.2061 | 60.888 | 0.51197 | 0.47462 | 0.09792
26.0084 | 58.0396 | 58.1779 | 60.8892 | 0.51132 | 0.47398 | 0.097446
26.0125 | 58.013 | 58.1736 | 60.8886 | 0.51054 | 0.47344 | 0.096903
26.0167 | 57.9865 | 58.1648 | 60.8896 | 0.50985 | 0.4729 | 0.096361
26.0209 | 57.9869 | 58.1425 | 60.8982 | 0.50913 | 0.47239 | 0.095846
26.025 | 57.9744 | 58.1189 | 60.9038 | 0.50843 | 0.47186 | 0.095321
26.0292 | 57.9475 | 58.1035 | 60.9003 | 0.50775 | 0.47118 | 0.094817
26.0334 | 57.9153 | 58.0797 | 60.892 | 0.50717 | 0.47058 | 0.09434
26.0375 | 57.8811 | 58.0441 | 60.882 | 0.50639 | 0.4702 | 0.093842
26.0417 | 57.8552 | 58.0191 | 60.879 | 0.50565 | 0.46974 | 0.0933
26.0459 | 57.8405 | 57.9968 | 60.8849 | 0.50493 | 0.46904 | 0.092778
26.05 | 57.8374 | 57.9924 | 60.9 | 0.50426 | 0.46835 | 0.092247
26.0542 | 57.8251 | 58.0147 | 60.9215 | 0.50347 | 0.46772 | 0.091656
26.0584 | 57.7904 | 58.0056 | 60.9226 | 0.50284 | 0.46717 | 0.091132
26.0625 | 57.7525 | 57.9493 | 60.9077 | 0.50215 | 0.46676 | 0.090686
26.0667 | 57.7113 | 57.89 | 60.8881 | 0.50144 | 0.46623 | 0.090196
26.0709 | 57.6566 | 57.84 | 60.8603 | 0.5008 | 0.46547 | 0.089663
26.075 | 57.6435 | 57.8226 | 60.8571 | 0.50013 | 0.46477 | 0.089155
26.0792 | 57.6381 | 57.8386 | 60.8805 | 0.49937 | 0.46428 | 0.088636
26.0834 | 57.6363 | 57.8451 | 60.9008 | 0.49858 | 0.46378 | 0.088137
26.0875 | 57.6389 | 57.8327 | 60.9182 | 0.49791 | 0.46315 | 0.087683
26.0917 | 57.6245 | 57.8104 | 60.9257 | 0.49702 | 0.46239 | 0.087139
26.0959 | 57.59 | 57.7949 | 60.9218 | 0.49616 | 0.46151 | 0.086464
26.1 | 57.5582 | 57.7775 | 60.9193 | 0.49521 | 0.46069 | 0.085821
26.1042 | 57.5281 | 57.7456 | 60.9197 | 0.49423 | 0.45995 | 0.085219
26.1084 | 57.4899 | 57.7091 | 60.9162 | 0.49327 | 0.45919 | 0.084642
26.1125 | 57.4505 | 57.6684 | 60.9061 | 0.49245 | 0.45831 | 0.084081
26.1167 | 57.4224 | 57.647 | 60.905 | 0.49147 | 0.45733 | 0.083467
26.1209 | 57.3881 | 57.6393 | 60.9171 | 0.4904 | 0.45636 | 0.08276
26.125 | 57.3756 | 57.6438 | 60.9404 | 0.48923 | 0.4553 | 0.082017
26.1292 | 57.3826 | 57.6576 | 60.9732 | 0.48803 | 0.45409 | 0.081267
26.1334 | 57.3735 | 57.6656 | 61.0009 | 0.48672 | 0.45269 | 0.080435
26.1375 | 57.3614 | 57.6738 | 61.0185 | 0.48539 | 0.45118 | 0.07949
26.1417 | 57.3429 | 57.6764 | 61.0294 | 0.48386 | 0.44955 | 0.078473
26.1459 | 57.3196 | 57.6649 | 61.0436 | 0.48219 | 0.44781 | 0.077357
26.15 | 57.3016 | 57.6499 | 61.0554 | 0.4805 | 0.44599 | 0.076222
26.1542 | 57.281 | 57.6382 | 61.0635 | 0.47882 | 0.44405 | 0.075097
26.1584 | 57.2581 | 57.6318 | 61.0747 | 0.47704 | 0.442 | 0.073935
26.1625 | 57.2345 | 57.6309 | 61.0823 | 0.47516 | 0.43993 | 0.072682
26.1667 | 57.2287 | 57.6383 | 61.0965 | 0.4731 | 0.43774 | 0.071376
26.1709 | 57.2277 | 57.6518 | 61.1217 | 0.471 | 0.43537 | 0.070023
26.175 | 57.2371 | 57.6767 | 61.1519 | 0.46876 | 0.43279 | 0.068571
26.1792 | 57.2389 | 57.7109 | 61.1818 | 0.4665 | 0.43008 | 0.067065
26.1834 | 57.2355 | 57.7435 | 61.2119 | 0.46398 | 0.42722 | 0.065457
26.1875 | 57.2326 | 57.7716 | 61.2444 | 0.4614 | 0.42421 | 0.063699
26.1917 | 57.2117 | 57.7659 | 61.2631 | 0.45875 | 0.42119 | 0.061921
26.1959 | 57.1809 | 57.7408 | 61.2743 | 0.4562 | 0.41813 | 0.060156
26.2 | 57.1244 | 57.6963 | 61.2748 | 0.45366 | 0.41511 | 0.0584
26.2042 | 57.071 | 57.6367 | 61.2596 | 0.45124 | 0.41228 | 0.056622
26.2084 | 57.0042 | 57.5707 | 61.242 | 0.44899 | 0.40973 | 0.054974
26.2125 | 56.9353 | 57.4946 | 61.2255 | 0.44688 | 0.40735 | 0.053402
26.2167 | 56.8529 | 57.404 | 61.2025 | 0.44505 | 0.40525 | 0.051977
26.2209 | 56.7805 | 57.3203 | 61.171 | 0.44342 | 0.4035 | 0.050729
26.225 | 56.725 | 57.2573 | 61.151 | 0.44185 | 0.40186 | 0.049529
26.2292 | 56.6732 | 57.2017 | 61.1407 | 0.44039 | 0.40037 | 0.04831
26.2334 | 56.6416 | 57.1608 | 61.1405 | 0.43906 | 0.39907 | 0.047198
26.2375 | 56.6171 | 57.1424 | 61.1551 | 0.43777 | 0.39782 | 0.046201
26.2417 | 56.5881 | 57.1212 | 61.1677 | 0.43641 | 0.39652 | 0.045174
26.2459 | 56.5691 | 57.1032 | 61.1746 | 0.43504 | 0.39525 | 0.044099
26.25 | 56.5679 | 57.106 | 61.1919 | 0.43348 | 0.39387 | 0.042945
26.2542 | 56.5649 | 57.1202 | 61.2232 | 0.43191 | 0.39228 | 0.041674
26.2584 | 56.5594 | 57.126 | 61.2463 | 0.43032 | 0.39072 | 0.040439
26.2625 | 56.5444 | 57.1291 | 61.2597 | 0.42872 | 0.38918 | 0.039284
26.2667 | 56.5198 | 57.1202 | 61.2635 | 0.42691 | 0.38748 | 0.038047
26.2709 | 56.4972 | 57.0977 | 61.2567 | 0.42509 | 0.38564 | 0.036673
26.275 | 56.4766 | 57.0797 | 61.2576 | 0.42326 | 0.38385 | 0.035334
26.2792 | 56.4559 | 57.0687 | 61.2677 | 0.42148 | 0.38204 | 0.034073
26.2834 | 56.4109 | 57.0368 | 61.2667 | 0.41977 | 0.38034 | 0.032895
26.2875 | 56.3618 | 56.985 | 61.2499 | 0.41807 | 0.37877 | 0.031795
26.2917 | 56.3154 | 56.9348 | 61.2359 | 0.4163 | 0.37718 | 0.030641
26.2959 | 56.2811 | 56.8929 | 61.2296 | 0.4145 | 0.37546 | 0.029421
26.3 | 56.2456 | 56.8581 | 61.2323 | 0.4129 | 0.37391 | 0.028295
26.3042 | 56.2211 | 56.8322 | 61.2424 | 0.41139 | 0.37263 | 0.027315
26.3084 | 56.1802 | 56.8014 | 61.2423 | 0.40992 | 0.37136 | 0.026344
26.3125 | 56.134 | 56.7558 | 61.2323 | 0.40838 | 0.37004 | 0.025331
26.3167 | 56.1088 | 56.7268 | 61.2304 | 0.40682 | 0.36866 | 0.02427
26.3209 | 56.0927 | 56.7312 | 61.2418 | 0.40533 | 0.36729 | 0.023185
26.325 | 56.0766 | 56.7351 | 61.2544 | 0.40396 | 0.36596 | 0.022179
26.3292 | 56.0551 | 56.723 | 61.2633 | 0.40262 | 0.3648 | 0.021243
26.3334 | 56.0253 | 56.7082 | 61.2651 | 0.40117 | 0.36351 | 0.020253
26.3375 | 55.9957 | 56.6866 | 61.2632 | 0.3997 | 0.36203 | 0.019163
26.3417 | 55.9778 | 56.6708 | 61.2703 | 0.39823 | 0.36054 | 0.018067
26.3459 | 55.9578 | 56.6755 | 61.2838 | 0.39682 | 0.35913 | 0.01702
26.35 | 55.9342 | 56.667 | 61.2919 | 0.39542 | 0.35774 | 0.016019
26.3542 | 55.9088 | 56.6463 | 61.291 | 0.39401 | 0.35634 | 0.015025
26.3584 | 55.8856 | 56.6231 | 61.2873 | 0.3925 | 0.35491 | 0.013976
26.3625 | 55.8595 | 56.5941 | 61.2873 | 0.39105 | 0.35342 | 0.012894
26.3667 | 55.8332 | 56.568 | 61.2935 | 0.38963 | 0.35201 | 0.01185
26.3709 | 55.8051 | 56.5419 | 61.3021 | 0.38822 | 0.35068 | 0.010867
26.375 | 55.7661 | 56.5122 | 61.3045 | 0.3868 | 0.34936 | 0.0099026
26.3792 | 55.7336 | 56.4935 | 61.3011 | 0.38539 | 0.34797 | 0.008924
26.3834 | 55.7029 | 56.4744 | 61.2994 | 0.38398 | 0.3466 | 0.0079196
26.3875 | 55.6812 | 56.4621 | 61.2996 | 0.38253 | 0.34524 | 0.0069383
26.3917 | 55.6656 | 56.4505 | 61.3035 | 0.38108 | 0.3439 | 0.0059962
26.3959 | 55.6376 | 56.4071 | 61.3138 | 0.37969 | 0.34264 | 0.0050319
26.4 | 55.6073 | 56.3694 | 61.3194 | 0.37829 | 0.34137 | 0.004068
26.4042 | 55.5713 | 56.3463 | 61.3197 | 0.37683 | 0.33994 | 0.0031547
26.4084 | 55.5292 | 56.3216 | 61.3212 | 0.37536 | 0.33852 | 0.0022402
26.4125 | 55.4922 | 56.3175 | 61.3172 | 0.37398 | 0.33724 | 0.0012972
26.4167 | 55.4603 | 56.3091 | 61.3159 | 0.37256 | 0.33592 | 0.00037055
26.4209 | 55.4302 | 56.2809 | 61.3251 | 0.37112 | 0.33454 | -0.00055044
26.425 | 55.3978 | 56.2541 | 61.3326 | 0.36973 | 0.33316 | -0.0014635
26.4292 | 55.371 | 56.2171 | 61.3365 | 0.36831 | 0.33178 | -0.0023237
26.4334 | 55.3398 | 56.1799 | 61.3401 | 0.36685 | 0.33042 | -0.0031783
26.4375 | 55.2929 | 56.1451 | 61.3423 | 0.36547 | 0.32911 | -0.004092
26.4417 | 55.2532 | 56.1111 | 61.3457 | 0.36407 | 0.32779 | -0.0049914
26.4459 | 55.2109 | 56.1044 | 61.3495 | 0.36263 | 0.32635 | -0.0058086
26.45 | 55.1671 | 56.0952 | 61.3522 | 0.36118 | 0.32492 | -0.0066056
26.4542 | 55.1258 | 56.0631 | 61.3523 | 0.35987 | 0.32367 | -0.0074266
26.4584 | 55.0882 | 56.0321 | 61.3542 | 0.35846 | 0.32238 | -0.0082544
26.4625 | 55.0552 | 55.9904 | 61.3645 | 0.357 | 0.3209 | -0.0090722
26.4667 | 55.0201 | 55.9511 | 61.3758 | 0.35557 | 0.31943 | -0.009868
26.4709 | 54.9814 | 55.9283 | 61.3814 | 0.35419 | 0.31809 | -0.010615
26.475 | 54.935 | 55.9009 | 61.3833 | 0.35279 | 0.31676 | -0.011349
26.4792 | 54.8786 | 55.8579 | 61.3838 | 0.35137 | 0.31546 | -0.012126
26.4834 | 54.8247 | 55.8163 | 61.3855 | 0.34996 | 0.31414 | -0.012897
26.4875 | 54.7835 | 55.7934 | 61.3886 | 0.34851 | 0.31266 | -0.013585
26.4917 | 54.7355 | 55.7706 | 61.3916 | 0.34712 | 0.3112 | -0.01423
26.4959 | 54.6825 | 55.736 | 61.3919 | 0.34581 | 0.30993 | -0.014884
26.5 | 54.6305 | 55.7007 | 61.3907 | 0.34446 | 0.30864 | -0.015544
26.5042 | 54.5806 | 55.6558 | 61.3952 | 0.34299 | 0.30718 | -0.016188
26.5084 | 54.5375 | 55.6136 | 61.4026 | 0.34153 | 0.30571 | -0.01683
26.5125 | 54.494 | 55.5805 | 61.4069 | 0.34014 | 0.30436 | -0.017441
26.5167 | 54.4434 | 55.5421 | 61.4088 | 0.33876 | 0.30302 | -0.018028
26.5209 | 54.3828 | 55.4972 | 61.4109 | 0.33734 | 0.30167 | -0.018647
26.525 | 54.321 | 55.4481 | 61.4116 | 0.33588 | 0.30032 | -0.019276
26.5292 | 54.2592 | 55.4135 | 61.413 | 0.33445 | 0.29888 | -0.019856
26.5334 | 54.201 | 55.3769 | 61.4161 | 0.33303 | 0.29747 | -0.02041
26.5375 | 54.1418 | 55.3232 | 61.4142 | 0.33163 | 0.29621 | -0.020958
26.5417 | 54.0843 | 55.268 | 61.4105 | 0.3302 | 0.29495 | -0.021489
26.5459 | 54.0282 | 55.2097 | 61.4089 | 0.32875 | 0.29357 | -0.021999
26.55 | 53.9779 | 55.1535 | 61.4099 | 0.32724 | 0.29219 | -0.022518
26.5542 | 53.911 | 55.1083 | 61.4159 | 0.32583 | 0.29091 | -0.023034
26.5584 | 53.8406 | 55.0619 | 61.4242 | 0.3244 | 0.28964 | -0.023537
26.5625 | 53.7759 | 55.0071 | 61.4335 | 0.32289 | 0.28836 | -0.024046
26.5667 | 53.7074 | 54.9521 | 61.4418 | 0.32132 | 0.28706 | -0.024572
26.5709 | 53.6438 | 54.9001 | 61.4445 | 0.31986 | 0.28571 | -0.02509
26.575 | 53.5793 | 54.8481 | 61.4489 | 0.31839 | 0.28436 | -0.025627
26.5792 | 53.5003 | 54.795 | 61.4569 | 0.31691 | 0.28304 | -0.026203
26.5834 | 53.4192 | 54.7403 | 61.4639 | 0.31543 | 0.28171 | -0.026777
26.5875 | 53.3473 | 54.6881 | 61.4795 | 0.31387 | 0.2803 | -0.027367
26.5917 | 53.2754 | 54.6348 | 61.4925 | 0.31231 | 0.27889 | -0.027966
26.5959 | 53.2094 | 54.5709 | 61.4938 | 0.31077 | 0.27754 | -0.028532
26.6 | 53.1319 | 54.5054 | 61.4959 | 0.30929 | 0.27618 | -0.029096
26.6042 | 53.0536 | 54.4337 | 61.492 | 0.30769 | 0.27479 | -0.029689
26.6084 | 52.9808 | 54.3617 | 61.4876 | 0.30605 | 0.27339 | -0.03027
26.6125 | 52.8921 | 54.3046 | 61.4965 | 0.30444 | 0.27197 | -0.030829
26.6167 | 52.8131 | 54.2428 | 61.5042 | 0.30284 | 0.27057 | -0.031387
26.6209 | 52.7205 | 54.1806 | 61.5098 | 0.30125 | 0.26916 | -0.031906
26.625 | 52.6268 | 54.1165 | 61.5171 | 0.29959 | 0.26774 | -0.032422
26.6292 | 52.5326 | 54.0366 | 61.5175 | 0.29801 | 0.2663 | -0.032965
26.6334 | 52.4449 | 53.9587 | 61.5184 | 0.29631 | 0.26486 | -0.033497
26.6375 | 52.3532 | 53.8782 | 61.5222 | 0.29469 | 0.26341 | -0.033998
26.6417 | 52.2557 | 53.7938 | 61.525 | 0.29304 | 0.26196 | -0.034501
26.6459 | 52.1623 | 53.7203 | 61.5325 | 0.29138 | 0.26051 | -0.035006
26.65 | 52.0712 | 53.647 | 61.5419 | 0.2896 | 0.25901 | -0.035518
26.6542 | 51.97 | 53.5676 | 61.5546 | 0.28788 | 0.25754 | -0.036047
26.6584 | 51.8689 | 53.4853 | 61.5668 | 0.28616 | 0.25608 | -0.03656
26.6625 | 51.7579 | 53.3988 | 61.5693 | 0.28443 | 0.25454 | -0.037034
26.6667 | 51.6389 | 53.3072 | 61.5704 | 0.28265 | 0.25299 | -0.037513
26.6709 | 51.5204 | 53.2122 | 61.5751 | 0.28091 | 0.25147 | -0.038055
26.675 | 51.4115 | 53.1197 | 61.5827 | 0.27908 | 0.24993 | -0.038596
26.6792 | 51.2938 | 53.0259 | 61.5944 | 0.27731 | 0.24836 | -0.039054
26.6834 | 51.1734 | 52.927 | 61.6043 | 0.27554 | 0.2468 | -0.039488
26.6875 | 51.0543 | 52.8269 | 61.6075 | 0.27373 | 0.24525 | -0.039946
26.6917 | 50.9293 | 52.7249 | 61.6107 | 0.27183 | 0.24365 | -0.04042
26.6959 | 50.8032 | 52.6131 | 61.6242 | 0.26996 | 0.24206 | -0.040924
26.7 | 50.6777 | 52.5018 | 61.6411 | 0.26806 | 0.24046 | -0.041412
26.7042 | 50.5384 | 52.3981 | 61.6523 | 0.26616 | 0.23879 | -0.041819
26.7084 | 50.3927 | 52.2871 | 61.6604 | 0.26426 | 0.23711 | -0.04221
26.7125 | 50.2476 | 52.1586 | 61.6646 | 0.26232 | 0.23553 | -0.042664
26.7167 | 50.1031 | 52.0313 | 61.6718 | 0.26032 | 0.23389 | -0.043143
26.7209 | 49.9583 | 51.907 | 61.6882 | 0.25833 | 0.23212 | -0.043574
26.725 | 49.8159 | 51.7777 | 61.7065 | 0.25631 | 0.23036 | -0.043969
26.7292 | 49.6688 | 51.6567 | 61.7233 | 0.25424 | 0.22863 | -0.044361
26.7334 | 49.5186 | 51.5311 | 61.7367 | 0.25213 | 0.22684 | -0.044749
26.7375 | 49.3619 | 51.375 | 61.7482 | 0.24999 | 0.22511 | -0.045135
26.7417 | 49.2 | 51.2225 | 61.7655 | 0.24781 | 0.22334 | -0.045528
26.7459 | 49.0301 | 51.0879 | 61.7877 | 0.24561 | 0.22139 | -0.045928
26.75 | 48.8646 | 50.9445 | 61.8089 | 0.24334 | 0.21943 | -0.04628
26.7542 | 48.6812 | 50.7817 | 61.8285 | 0.24112 | 0.21767 | -0.04659
26.7584 | 48.5135 | 50.6168 | 61.8472 | 0.23878 | 0.21582 | -0.046922
26.7625 | 48.3428 | 50.4461 | 61.8644 | 0.23642 | 0.21383 | -0.047266
26.7667 | 48.1603 | 50.2736 | 61.8873 | 0.23403 | 0.21182 | -0.047589
26.7709 | 47.9942 | 50.1168 | 61.9175 | 0.23157 | 0.20979 | -0.047904
26.775 | 47.8049 | 49.9514 | 61.9442 | 0.22907 | 0.20773 | -0.048184
26.7792 | 47.5971 | 49.7596 | 61.9692 | 0.22659 | 0.20572 | -0.04843
26.7834 | 47.4057 | 49.5694 | 61.9981 | 0.22401 | 0.20364 | -0.048702
26.7875 | 47.1949 | 49.3959 | 62.0268 | 0.22137 | 0.20134 | -0.048994
26.7917 | 46.9849 | 49.2183 | 62.0583 | 0.21875 | 0.19902 | -0.049232
26.7959 | 46.7789 | 49.0222 | 62.0941 | 0.2161 | 0.19681 | -0.049439
26.8 | 46.554 | 48.8225 | 62.1264 | 0.21339 | 0.19454 | -0.04964
26.8042 | 46.3217 | 48.6179 | 62.1584 | 0.21068 | 0.19211 | -0.049818
26.8084 | 46.0964 | 48.4117 | 62.1981 | 0.20787 | 0.18964 | -0.050001
26.8125 | 45.8652 | 48.2132 | 62.2392 | 0.20497 | 0.18714 | -0.050169
26.8167 | 45.6236 | 48.005 | 62.2809 | 0.20211 | 0.1846 | -0.05028
26.8209 | 45.3772 | 47.7749 | 62.3296 | 0.19918 | 0.18207 | -0.050386
26.825 | 45.1197 | 47.5379 | 62.3781 | 0.19618 | 0.17949 | -0.050499
26.8292 | 44.8529 | 47.3183 | 62.4243 | 0.19315 | 0.17673 | -0.050558
26.8334 | 44.5894 | 47.0916 | 62.4772 | 0.19003 | 0.17393 | -0.050588
26.8375 | 44.3174 | 46.8412 | 62.5337 | 0.18687 | 0.1712 | -0.050632
26.8417 | 44.038 | 46.5843 | 62.5896 | 0.18367 | 0.16842 | -0.050626
26.8459 | 43.7512 | 46.3236 | 62.6511 | 0.18042 | 0.16551 | -0.050561
26.85 | 43.4597 | 46.0575 | 62.717 | 0.17707 | 0.16253 | -0.050493
26.8542 | 43.1593 | 45.7933 | 62.7821 | 0.17368 | 0.15952 | -0.050387
26.8584 | 42.8601 | 45.5249 | 62.8554 | 0.17019 | 0.15643 | -0.050241
26.8625 | 42.5467 | 45.2295 | 62.94 | 0.16666 | 0.15335 | -0.050098
26.8667 | 42.2316 | 44.9305 | 63.0274 | 0.16304 | 0.15019 | -0.04992
26.8709 | 41.9023 | 44.6387 | 63.1143 | 0.15937 | 0.14689 | -0.049649
26.875 | 41.555 | 44.3339 | 63.2035 | 0.15565 | 0.14353 | -0.049339
26.8792 | 41.198 | 44.0009 | 63.2981 | 0.15186 | 0.1402 | -0.049028
26.8834 | 40.8319 | 43.6603 | 63.3984 | 0.148 | 0.13678 | -0.048657
26.8875 | 40.4511 | 43.3137 | 63.505 | 0.14407 | 0.13325 | -0.048198
26.8917 | 40.0729 | 42.9694 | 63.6257 | 0.14006 | 0.12963 | -0.047708
26.8959 | 39.7004 | 42.6362 | 63.7578 | 0.13593 | 0.12589 | -0.047184
26.9 | 39.305 | 42.2854 | 63.8946 | 0.13176 | 0.12211 | -0.046583
26.9042 | 38.9045 | 41.9026 | 64.0411 | 0.12748 | 0.11825 | -0.045911
26.9084 | 38.4755 | 41.4954 | 64.1837 | 0.12313 | 0.11433 | -0.045153
26.9125 | 38.0276 | 41.0788 | 64.3166 | 0.11869 | 0.11029 | -0.044267
26.9167 | 37.5771 | 40.6648 | 64.4686 | 0.11416 | 0.10614 | -0.04333
26.9209 | 37.1319 | 40.2418 | 64.6472 | 0.10949 | 0.10191 | -0.042367
26.925 | 36.688 | 39.8262 | 64.8496 | 0.10474 | 0.09757 | -0.041307
26.9292 | 36.2418 | 39.4198 | 65.0726 | 0.099877 | 0.093111 | -0.040123
26.9334 | 35.7626 | 38.9871 | 65.2946 | 0.094937 | 0.088561 | -0.03882
26.9375 | 35.2642 | 38.5259 | 65.5176 | 0.089901 | 0.083927 | -0.037422
26.9417 | 34.736 | 38.0374 | 65.7409 | 0.084759 | 0.079184 | -0.035916
26.9459 | 34.1935 | 37.5153 | 65.9677 | 0.079501 | 0.074347 | -0.034297
26.95 | 33.6582 | 36.998 | 66.2198 | 0.074122 | 0.069388 | -0.032559
26.9542 | 33.1048 | 36.4957 | 66.4943 | 0.068641 | 0.0643 | -0.030688
26.9584 | 32.5558 | 35.989 | 66.7915 | 0.063037 | 0.059101 | -0.028675
26.9625 | 32.0041 | 35.4667 | 67.1177 | 0.057311 | 0.053798 | -0.026534
26.9667 | 31.4518 | 34.9325 | 67.4601 | 0.051439 | 0.048349 | -0.024265
26.9709 | 30.8816 | 34.4026 | 67.8183 | 0.045452 | 0.04275 | -0.021853
26.975 | 30.302 | 33.8586 | 68.1974 | 0.039329 | 0.037015 | -0.019292
26.9792 | 29.7082 | 33.3076 | 68.5999 | 0.033084 | 0.031153 | -0.01657
26.9834 | 29.094 | 32.7306 | 69.0152 | 0.026722 | 0.025178 | -0.013648
26.9875 | 28.467 | 32.1248 | 69.4433 | 0.020233 | 0.019085 | -0.010528
26.9917 | 27.837 | 31.5142 | 69.8963 | 0.013618 | 0.01286 | -0.0072193
26.9959 | 27.1792 | 30.9075 | 70.3831 | 0.0068689 | 0.0064914 | -0.0037081
27 | 26.533 | 30.3088 | 70.9095 | 0 | 0 | 0
27.0042 | 26.744 | 30.5173 | 70.992 | 0 | 0 | 0
27.0084 | 26.9718 | 30.7418 | 71.0836 | 0 | 0 | 0
27.0125 | 26.6407 | 30.4505 | 71.5045 | 0 | 0 | 0
27.0167 | 26.309 | 30.1637 | 71.9474 | 0 | 0 | 0
27.0209 | 26.9209 | 30.7723 | 71.882 | 0 | 0 | 0
27.025 | 27.5511 | 31.3979 | 71.8077 | 0 | 0 | 0
27.0292 | 27.3745 | 31.2572 | 72.1918 | 0 | 0 | 0
27.0334 | 27.1911 | 31.1099 | 72.5895 | 0 | 0 | 0
27.0375 | 27.868 | 31.7864 | 72.5143 | 0 | 0 | 0
27.0417 | 28.5626 | 32.4782 | 72.4301 | 0 | 0 | 0
27.0459 | 28.4185 | 32.3705 | 72.8164 | 0 | 0 | 0
27.05 | 28.2985 | 32.2843 | 73.2308 | 0 | 0 | 0
27.0542 | 29.0346 | 33.0295 | 73.1903 | 0 | 0 | 0
27.0584 | 29.7936 | 33.7995 | 73.1457 | 0 | 0 | 0
27.0625 | 29.6913 | 33.7717 | 73.5744 | 0 | 0 | 0
27.0667 | 29.5979 | 33.7382 | 74.0186 | 0 | 0 | 0
27.0709 | 30.3438 | 34.5 | 74.003 | 0 | 0 | 0
27.075 | 31.0968 | 35.2586 | 73.9685 | 0 | 0 | 0
27.0792 | 30.9774 | 35.2011 | 74.3976 | 0 | 0 | 0
27.0834 | 30.8264 | 35.1096 | 74.8244 | 0 | 0 | 0
27.0875 | 31.5012 | 35.7761 | 74.7694 | 0 | 0 | 0
27.0917 | 32.163 | 36.4228 | 74.6861 | 0 | 0 | 0
27.0959 | 31.9646 | 36.2518 | 75.0613 | 0 | 0 | 0
27.1 | 31.746 | 36.0581 | 75.4397 | 0 | 0 | 0
27.1042 | 32.3579 | 36.6429 | 75.336 | 0 | 0 | 0
27.1084 | 32.9796 | 37.2281 | 75.2154 | 0 | 0 | 0
27.1125 | 32.7499 | 37.0059 | 75.5649 | 0 | 0 | 0
27.1167 | 32.5206 | 36.777 | 75.9314 | 0 | 0 | 0
27.1209 | 33.1459 | 37.3627 | 75.8327 | 0 | 0 | 0
27.125 | 33.7859 | 37.965 | 75.7283 | 0 | 0 | 0
27.1292 | 33.58 | 37.7681 | 76.0976 | 0 | 0 | 0
27.1334 | 33.3868 | 37.5739 | 76.4839 | 0 | 0 | 0
27.1375 | 34.0403 | 38.1986 | 76.412 | 0 | 0 | 0
27.1417 | 34.7102 | 38.8318 | 76.3255 | 0 | 0 | 0
27.1459 | 34.5352 | 38.6699 | 76.6994 | 0 | 0 | 0
27.15 | 34.3581 | 38.5043 | 77.0869 | 0 | 0 | 0
27.1542 | 35.0219 | 39.1326 | 77.0125 | 0 | 0 | 0
27.1584 | 35.6919 | 39.76 | 76.9181 | 0 | 0 | 0
27.1625 | 35.5059 | 39.5925 | 77.279 | 0 | 0 | 0
27.1667 | 35.3099 | 39.4069 | 77.6486 | 0 | 0 | 0
27.1709 | 35.9467 | 39.9946 | 77.5476 | 0 | 0 | 0
27.175 | 36.5853 | 40.5855 | 77.4351 | 0 | 0 | 0
27.1792 | 36.3886 | 40.3833 | 77.7901 | 0 | 0 | 0
27.1834 | 36.1698 | 40.167 | 78.1525 | 0 | 0 | 0
27.1875 | 36.7726 | 40.7191 | 78.0413 | 0 | 0 | 0
27.1917 | 37.3852 | 41.2817 | 77.9184 | 0 | 0 | 0
27.1959 | 37.171 | 41.071 | 78.2648 | 0 | 0 | 0
27.2 | 36.9544 | 40.8589 | 78.6255 | 0 | 0 | 0
27.2042 | 37.5667 | 41.4299 | 78.5239 | 0 | 0 | 0
27.2084 | 38.1793 | 42.0106 | 78.4055 | 0 | 0 | 0
27.2125 | 37.9564 | 41.7888 | 78.7479 | 0 | 0 | 0
27.2167 | 37.7322 | 41.5717 | 79.1085 | 0 | 0 | 0
27.2209 | 38.3456 | 42.1636 | 79.0117 | 0 | 0 | 0
27.225 | 38.9668 | 42.7591 | 78.8999 | 0 | 0 | 0
27.2292 | 38.7486 | 42.5662 | 79.2438 | 0 | 0 | 0
27.2334 | 38.5298 | 42.3617 | 79.5987 | 0 | 0 | 0
27.2375 | 39.1505 | 42.9378 | 79.4912 | 0 | 0 | 0
27.2417 | 39.7878 | 43.5249 | 79.3736 | 0 | 0 | 0
27.2459 | 39.5644 | 43.308 | 79.7256 | 0 | 0 | 0
27.25 | 39.3244 | 43.0794 | 80.0855 | 0 | 0 | 0
27.2542 | 39.9428 | 43.6717 | 79.9651 | 0 | 0 | 0
27.2584 | 40.5706 | 44.2678 | 79.8315 | 0 | 0 | 0
27.2625 | 40.3475 | 44.0612 | 80.1736 | 0 | 0 | 0
27.2667 | 40.1227 | 43.8465 | 80.5312 | 0 | 0 | 0
27.2709 | 40.7624 | 44.4269 | 80.4177 | 0 | 0 | 0
27.275 | 41.4067 | 45.0168 | 80.2857 | 0 | 0 | 0
27.2792 | 41.1785 | 44.7824 | 80.6249 | 0 | 0 | 0
27.2834 | 40.9469 | 44.5455 | 80.9778 | 0 | 0 | 0
27.2875 | 41.5742 | 45.1569 | 80.8526 | 0 | 0 | 0
27.2917 | 42.2077 | 45.772 | 80.7129 | 0 | 0 | 0
27.2959 | 41.9873 | 45.5682 | 81.0438 | 0 | 0 | 0
27.3 | 41.765 | 45.3588 | 81.3867 | 0 | 0 | 0
27.3042 | 42.4024 | 45.9355 | 81.2648 | 0 | 0 | 0
27.3084 | 43.0437 | 46.5219 | 81.1288 | 0 | 0 | 0
27.3125 | 42.8372 | 46.3178 | 81.4531 | 0 | 0 | 0
27.3167 | 42.6247 | 46.106 | 81.7878 | 0 | 0 | 0
27.3209 | 43.2395 | 46.6921 | 81.6567 | 0 | 0 | 0
27.325 | 43.8669 | 47.2863 | 81.5106 | 0 | 0 | 0
27.3292 | 43.6617 | 47.1013 | 81.8239 | 0 | 0 | 0
27.3334 | 43.4511 | 46.9101 | 82.1496 | 0 | 0 | 0
27.3375 | 44.08 | 47.494 | 82.0114 | 0 | 0 | 0
27.3417 | 44.7214 | 48.0879 | 81.8596 | 0 | 0 | 0
27.3459 | 44.524 | 47.8914 | 82.1753 | 0 | 0 | 0
27.35 | 44.3202 | 47.6893 | 82.5021 | 0 | 0 | 0
27.3542 | 44.9557 | 48.2841 | 82.3541 | 0 | 0 | 0
27.3584 | 45.6009 | 48.8853 | 82.1909 | 0 | 0 | 0
27.3625 | 45.3971 | 48.6843 | 82.4978 | 0 | 0 | 0
27.3667 | 45.1821 | 48.4775 | 82.8171 | 0 | 0 | 0
27.3709 | 45.8234 | 49.0928 | 82.6605 | 0 | 0 | 0
27.375 | 46.4731 | 49.7157 | 82.4888 | 0 | 0 | 0
27.3792 | 46.2661 | 49.5117 | 82.7887 | 0 | 0 | 0
27.3834 | 46.0588 | 49.3053 | 83.1026 | 0 | 0 | 0
27.3875 | 46.7199 | 49.9106 | 82.9448 | 0 | 0 | 0
27.3917 | 47.3901 | 50.5255 | 82.7727 | 0 | 0 | 0
27.3959 | 47.1944 | 50.3359 | 83.0689 | 0 | 0 | 0
27.4 | 46.9917 | 50.1374 | 83.3768 | 0 | 0 | 0
27.4042 | 47.6425 | 50.7484 | 83.2196 | 0 | 0 | 0
27.4084 | 48.2995 | 51.3656 | 83.0483 | 0 | 0 | 0
27.4125 | 48.1153 | 51.1849 | 83.3356 | 0 | 0 | 0
27.4167 | 47.9302 | 50.9954 | 83.6335 | 0 | 0 | 0
27.4209 | 48.5891 | 51.5935 | 83.4624 | 0 | 0 | 0
27.425 | 49.2585 | 52.1994 | 83.2778 | 0 | 0 | 0
27.4292 | 49.0804 | 52.0206 | 83.5648 | 0 | 0 | 0
27.4334 | 48.9067 | 51.8365 | 83.866 | 0 | 0 | 0
27.4375 | 49.5773 | 52.4456 | 83.7021 | 0 | 0 | 0
27.4417 | 50.2517 | 53.062 | 83.5249 | 0 | 0 | 0
27.4459 | 50.0908 | 52.8769 | 83.8054 | 0 | 0 | 0
27.45 | 49.9263 | 52.6892 | 84.1021 | 0 | 0 | 0
27.4542 | 50.5991 | 53.3133 | 83.939 | 0 | 0 | 0
27.4584 | 51.2886 | 53.9455 | 83.7631 | 0 | 0 | 0
27.4625 | 51.1266 | 53.781 | 84.0616 | 0 | 0 | 0
27.4667 | 50.9559 | 53.6105 | 84.3728 | 0 | 0 | 0
27.4709 | 51.6521 | 54.2426 | 84.2129 | 0 | 0 | 0
27.475 | 52.3566 | 54.8866 | 84.0405 | 0 | 0 | 0
27.4792 | 52.2163 | 54.7125 | 84.3247 | 0 | 0 | 0
27.4834 | 52.0635 | 54.5332 | 84.6209 | 0 | 0 | 0
27.4875 | 52.7723 | 55.1777 | 84.4573 | 0 | 0 | 0
27.4917 | 53.4961 | 55.8305 | 84.2789 | 0 | 0 | 0
27.4959 | 53.36 | 55.6853 | 84.5692 | 0 | 0 | 0
27.5 | 53.2262 | 55.5354 | 84.8731 | 0 | 0 | 0
27.5042 | 53.9394 | 56.1855 | 84.7033 | 0 | 0 | 0
27.5084 | 54.6631 | 56.8437 | 84.5185 | 0 | 0 | 0
27.5125 | 54.5378 | 56.698 | 84.7944 | 0 | 0 | 0
27.5167 | 54.4175 | 56.551 | 85.0838 | 0 | 0 | 0
27.5209 | 55.1526 | 57.2105 | 84.9172 | 0 | 0 | 0
27.525 | 55.9009 | 57.8806 | 84.7371 | 0 | 0 | 0
27.5292 | 55.8015 | 57.7605 | 85.0148 | 0 | 0 | 0
27.5334 | 55.7006 | 57.6359 | 85.3047 | 0 | 0 | 0
27.5375 | 56.4534 | 58.3073 | 85.1374 | 0 | 0 | 0
27.5417 | 57.2157 | 58.9904 | 84.9564 | 0 | 0 | 0
27.5459 | 57.1266 | 58.8814 | 85.2278 | 0 | 0 | 0
27.55 | 57.038 | 58.7674 | 85.5115 | 0 | 0 | 0
27.5542 | 57.8015 | 59.4605 | 85.339 | 0 | 0 | 0
27.5584 | 58.5814 | 60.1657 | 85.1514 | 0 | 0 | 0
27.5625 | 58.519 | 60.0624 | 85.4174 | 0 | 0 | 0
27.5667 | 58.4548 | 59.9568 | 85.6963 | 0 | 0 | 0
27.5709 | 59.25 | 60.6796 | 85.5202 | 0 | 0 | 0
27.575 | 60.0594 | 61.4126 | 85.3289 | 0 | 0 | 0
27.5792 | 60.0205 | 61.3298 | 85.5968 | 0 | 0 | 0
27.5834 | 59.9767 | 61.2484 | 85.8768 | 0 | 0 | 0
27.5875 | 60.7868 | 61.9831 | 85.684 | 0 | 0 | 0
27.5917 | 61.6077 | 62.7291 | 85.4764 | 0 | 0 | 0
27.5959 | 61.589 | 62.6817 | 85.7414 | 0 | 0 | 0
27.6 | 61.5782 | 62.6325 | 86.0169 | 0 | 0 | 0
27.6042 | 62.4191 | 63.3823 | 85.816 | 0 | 0 | 0
27.6084 | 63.2759 | 64.1473 | 85.5995 | 0 | 0 | 0
27.6125 | 63.3063 | 64.1356 | 85.8552 | 0 | 0 | 0
27.6167 | 63.32 | 64.1236 | 86.1215 | 0 | 0 | 0
27.6209 | 64.1913 | 64.9023 | 85.9137 | 0 | 0 | 0
27.625 | 65.0791 | 65.6976 | 85.6911 | 0 | 0 | 0
27.6292 | 65.1074 | 65.7095 | 85.9379 | 0 | 0 | 0
27.6334 | 65.1602 | 65.7228 | 86.1946 | 0 | 0 | 0
27.6375 | 66.0714 | 66.541 | 85.9738 | 0 | 0 | 0
27.6417 | 66.9889 | 67.3747 | 85.737 | 0 | 0 | 0
27.6459 | 67.0793 | 67.409 | 85.9726 | 0 | 0 | 0
27.65 | 67.1645 | 67.4451 | 86.2185 | 0 | 0 | 0
27.6542 | 68.1092 | 68.3087 | 85.9888 | 0 | 0 | 0
27.6584 | 69.076 | 69.1865 | 85.7428 | 0 | 0 | 0
27.6625 | 69.1994 | 69.2585 | 85.9632 | 0 | 0 | 0
27.6667 | 69.3232 | 69.3324 | 86.1934 | 0 | 0 | 0
27.6709 | 70.308 | 70.2299 | 85.9528 | 0 | 0 | 0
27.675 | 71.3115 | 71.1442 | 85.6931 | 0 | 0 | 0
27.6792 | 71.4776 | 71.2652 | 85.8916 | 0 | 0 | 0
27.6834 | 71.6497 | 71.3924 | 86.1 | 0 | 0 | 0
27.6875 | 72.6851 | 72.3224 | 85.8415 | 0 | 0 | 0
27.6917 | 73.739 | 73.2718 | 85.5645 | 0 | 0 | 0
27.6959 | 73.957 | 73.4463 | 85.7443 | 0 | 0 | 0
27.7 | 74.1786 | 73.6256 | 85.9312 | 0 | 0 | 0
27.7042 | 75.2634 | 74.6097 | 85.6505 | 0 | 0 | 0
27.7084 | 76.3718 | 75.6153 | 85.3514 | 0 | 0 | 0
27.7125 | 76.6423 | 75.8354 | 85.5082 | 0 | 0 | 0
27.7167 | 76.9169 | 76.0604 | 85.6687 | 0 | 0 | 0
27.7209 | 78.0596 | 77.1063 | 85.3542 | 0 | 0 | 0
27.725 | 79.2149 | 78.1695 | 85.0154 | 0 | 0 | 0
27.7292 | 79.5404 | 78.435 | 85.1362 | 0 | 0 | 0
27.7334 | 79.8835 | 78.7136 | 85.2653 | 0 | 0 | 0
27.7375 | 81.093 | 79.8286 | 84.9138 | 0 | 0 | 0
27.7417 | 82.3308 | 80.9701 | 84.5413 | 0 | 0 | 0
27.7459 | 82.7477 | 81.3257 | 84.635 | 0 | 0 | 0
27.75 | 83.1632 | 81.6809 | 84.7217 | 0 | 0 | 0
27.7542 | 84.4356 | 82.8423 | 84.3128 | 0 | 0 | 0
27.7584 | 85.7345 | 84.0286 | 83.8759 | 0 | 0 | 0
27.7625 | 86.1985 | 84.4416 | 83.8942 | 0 | 0 | 0
27.7667 | 86.6931 | 84.8832 | 83.9219 | 0 | 0 | 0
27.7709 | 88.0703 | 86.1557 | 83.4765 | 0 | 0 | 0
27.775 | 89.4769 | 87.4547 | 83.0004 | 0 | 0 | 0
27.7792 | 90.0471 | 87.9813 | 82.9694 | 0 | 0 | 0
27.7834 | 90.6129 | 88.4994 | 82.9158 | 0 | 0 | 0
27.7875 | 92.0418 | 89.8167 | 82.3607 | 0 | 0 | 0
27.7917 | 93.5089 | 91.1664 | 81.7711 | 0 | 0 | 0
27.7959 | 94.1493 | 91.7434 | 81.6243 | 0 | 0 | 0
27.8 | 94.8329 | 92.3581 | 81.4829 | 0 | 0 | 0
27.8042 | 96.3937 | 93.8256 | 80.8662 | 0 | 0 | 0
27.8084 | 97.9828 | 95.3193 | 80.2056 | 0 | 0 | 0
27.8125 | 98.7562 | 96.021 | 79.9821 | 0 | 0 | 0
27.8167 | 99.5357 | 96.7327 | 79.7345 | 0 | 0 | 0
27.8209 | 101.1824 | 98.2755 | 78.9787 | 0 | 0 | 0
27.825 | 102.8481 | 99.8473 | 78.1744 | 0 | 0 | 0
27.8292 | 103.6933 | 100.6291 | 77.8006 | 0 | 0 | 0
27.8334 | 104.5508 | 101.4301 | 77.4015 | 0 | 0 | 0
27.8375 | 106.2864 | 103.0487 | 76.4934 | 0 | 0 | 0
27.8417 | 108.064 | 104.7159 | 75.5387 | 0 | 0 | 0
27.8459 | 109.0164 | 105.6234 | 75.0183 | 0 | 0 | 0
27.85 | 109.9904 | 106.5557 | 74.4718 | 0 | 0 | 0
27.8542 | 111.8595 | 108.3118 | 73.4099 | 0 | 0 | 0
27.8584 | 113.7446 | 110.0885 | 72.2786 | 0 | 0 | 0
27.8625 | 114.0461 | 110.3681 | 71.9825 | 0 | 0 | 0
27.8667 | 114.3359 | 110.6401 | 71.6615 | 0 | 0 | 0
27.8709 | 114.9717 | 111.2277 | 71.12 | 0 | 0 | 0
27.875 | 115.6105 | 111.814 | 70.5454 | 0 | 0 | 0
27.8792 | 115.1522 | 111.355 | 70.5583 | 0 | 0 | 0
27.8834 | 114.6742 | 110.8761 | 70.5736 | 0 | 0 | 0
27.8875 | 114.9241 | 111.0897 | 70.1687 | 0 | 0 | 0
27.8917 | 115.18 | 111.3082 | 69.7481 | 0 | 0 | 0
27.8959 | 114.5388 | 110.6674 | 69.8172 | 0 | 0 | 0
27.9 | 113.8899 | 110.0201 | 69.8993 | 0 | 0 | 0
27.9042 | 114.0659 | 110.1629 | 69.5226 | 0 | 0 | 0
27.9084 | 114.223 | 110.2904 | 69.1207 | 0 | 0 | 0
27.9125 | 113.512 | 109.584 | 69.1786 | 0 | 0 | 0
27.9167 | 112.7747 | 108.8458 | 69.2374 | 0 | 0 | 0
27.9209 | 112.8891 | 108.8926 | 68.8228 | 0 | 0 | 0
27.925 | 112.9882 | 108.9333 | 68.3868 | 0 | 0 | 0
27.9292 | 112.2411 | 108.1684 | 68.4073 | 0 | 0 | 0
27.9334 | 111.4713 | 107.3934 | 68.4389 | 0 | 0 | 0
27.9375 | 111.5671 | 107.4185 | 67.9983 | 0 | 0 | 0
27.9417 | 111.6825 | 107.4678 | 67.5544 | 0 | 0 | 0
27.9459 | 110.9738 | 106.7529 | 67.5877 | 0 | 0 | 0
27.95 | 110.2779 | 106.0584 | 67.6491 | 0 | 0 | 0
27.9542 | 110.4444 | 106.1864 | 67.2505 | 0 | 0 | 0
27.9584 | 110.6385 | 106.3439 | 66.8525 | 0 | 0 | 0
27.9625 | 110.0058 | 105.7278 | 66.9398 | 0 | 0 | 0
27.9667 | 109.3726 | 105.1191 | 67.05 | 0 | 0 | 0
27.9709 | 109.6001 | 105.3314 | 66.6968 | 0 | 0 | 0
27.975 | 109.8319 | 105.5582 | 66.3322 | 0 | 0 | 0
27.9792 | 109.214 | 104.9779 | 66.4363 | 0 | 0 | 0
27.9834 | 108.5872 | 104.3867 | 66.548 | 0 | 0 | 0
27.9875 | 108.8051 | 104.5985 | 66.1894 | 0 | 0 | 0
27.9917 | 109.013 | 104.807 | 65.8115 | 0 | 0 | 0
27.9959 | 108.3741 | 104.1992 | 65.8886 | 0 | 0 | 0
28 | 107.7147 | 103.5805 | 65.9784 | 0 | 0 | 0
28.0042 | 107.8983 | 103.7495 | 65.6054 | 0 | 0 | 0
28.0084 | 108.0793 | 103.9183 | 65.2164 | 0 | 0 | 0
28.0125 | 107.4151 | 103.2908 | 65.287 | 0 | 0 | 0
28.0167 | 106.7403 | 102.658 | 65.3749 | 0 | 0 | 0
28.0209 | 106.9175 | 102.8125 | 65.0039 | 0 | 0 | 0
28.025 | 107.1017 | 102.9844 | 64.6261 | 0 | 0 | 0
28.0292 | 106.4587 | 102.381 | 64.7218 | 0 | 0 | 0
28.0334 | 105.8088 | 101.7755 | 64.8292 | 0 | 0 | 0
28.0375 | 105.9924 | 101.9609 | 64.4692 | 0 | 0 | 0
28.0417 | 106.199 | 102.163 | 64.1017 | 0 | 0 | 0
28.0459 | 105.5862 | 101.6026 | 64.2083 | 0 | 0 | 0
28.05 | 104.9705 | 101.0369 | 64.329 | 0 | 0 | 0
28.0542 | 105.1848 | 101.2513 | 63.9844 | 0 | 0 | 0
28.0584 | 105.4006 | 101.4686 | 63.6244 | 0 | 0 | 0
28.0625 | 104.7856 | 100.8953 | 63.7253 | 0 | 0 | 0
28.0667 | 104.1705 | 100.3149 | 63.8439 | 0 | 0 | 0
28.0709 | 104.3931 | 100.5431 | 63.5029 | 0 | 0 | 0
28.075 | 104.6194 | 100.7653 | 63.1447 | 0 | 0 | 0
28.0792 | 104.0078 | 100.1854 | 63.2425 | 0 | 0 | 0
28.0834 | 103.3894 | 99.596 | 63.3533 | 0 | 0 | 0
28.0875 | 103.6107 | 99.7878 | 63.0062 | 0 | 0 | 0
28.0917 | 103.8361 | 99.9918 | 62.649 | 0 | 0 | 0
28.0959 | 103.215 | 99.4075 | 62.7582 | 0 | 0 | 0
28.1 | 102.573 | 98.8125 | 62.8767 | 0 | 0 | 0
28.1042 | 102.7958 | 99.0322 | 62.5211 | 0 | 0 | 0
28.1084 | 103.0312 | 99.2612 | 62.1562 | 0 | 0 | 0
28.1125 | 102.4129 | 98.6735 | 62.2721 | 0 | 0 | 0
28.1167 | 101.7888 | 98.0824 | 62.4033 | 0 | 0 | 0
28.1209 | 102.0193 | 98.2867 | 62.0621 | 0 | 0 | 0
28.125 | 102.251 | 98.5012 | 61.7043 | 0 | 0 | 0
28.1292 | 101.6124 | 97.911 | 61.8172 | 0 | 0 | 0
28.1334 | 100.9685 | 97.3138 | 61.9476 | 0 | 0 | 0
28.1375 | 101.193 | 97.5554 | 61.6042 | 0 | 0 | 0
28.1417 | 101.4213 | 97.7983 | 61.2483 | 0 | 0 | 0
28.1459 | 100.7956 | 97.1998 | 61.3694 | 0 | 0 | 0
28.15 | 100.1643 | 96.5961 | 61.5048 | 0 | 0 | 0
28.1542 | 100.3889 | 96.7928 | 61.1737 | 0 | 0 | 0
28.1584 | 100.6147 | 96.9966 | 60.8306 | 0 | 0 | 0
28.1625 | 99.9835 | 96.4176 | 60.9503 | 0 | 0 | 0
28.1667 | 99.347 | 95.8287 | 61.0836 | 0 | 0 | 0
28.1709 | 99.5482 | 96.0354 | 60.7554 | 0 | 0 | 0
28.175 | 99.7579 | 96.2492 | 60.4165 | 0 | 0 | 0
28.1792 | 99.1419 | 95.6704 | 60.5428 | 0 | 0 | 0
28.1834 | 98.5145 | 95.0839 | 60.6845 | 0 | 0 | 0
28.1875 | 98.7242 | 95.2708 | 60.3672 | 0 | 0 | 0
28.1917 | 98.9397 | 95.4646 | 60.0383 | 0 | 0 | 0
28.1959 | 98.3151 | 94.8778 | 60.1759 | 0 | 0 | 0
28.2 | 97.6778 | 94.2813 | 60.327 | 0 | 0 | 0
28.2042 | 97.879 | 94.4806 | 60.0079 | 0 | 0 | 0
28.2084 | 98.0857 | 94.6844 | 59.6771 | 0 | 0 | 0
28.2125 | 97.4496 | 94.0893 | 59.8211 | 0 | 0 | 0
28.2167 | 96.8018 | 93.4872 | 59.9805 | 0 | 0 | 0
28.2209 | 97.0075 | 93.6952 | 59.6694 | 0 | 0 | 0
28.225 | 97.2234 | 93.909 | 59.3461 | 0 | 0 | 0
28.2292 | 96.5819 | 93.2953 | 59.499 | 0 | 0 | 0
28.2334 | 95.9353 | 92.675 | 59.6675 | 0 | 0 | 0
28.2375 | 96.149 | 92.8764 | 59.366 | 0 | 0 | 0
28.2417 | 96.3643 | 93.0812 | 59.051 | 0 | 0 | 0
28.2459 | 95.7095 | 92.4799 | 59.2071 | 0 | 0 | 0
28.25 | 95.0438 | 91.8674 | 59.3768 | 0 | 0 | 0
28.2542 | 95.2383 | 92.0604 | 59.0802 | 0 | 0 | 0
28.2584 | 95.4383 | 92.2605 | 58.7718 | 0 | 0 | 0
28.2625 | 94.7912 | 91.6539 | 58.926 | 0 | 0 | 0
28.2667 | 94.1394 | 91.0404 | 59.0938 | 0 | 0 | 0
28.2709 | 94.3278 | 91.2185 | 58.801 | 0 | 0 | 0
28.275 | 94.519 | 91.4056 | 58.4975 | 0 | 0 | 0
28.2792 | 93.8637 | 90.8074 | 58.6666 | 0 | 0 | 0
28.2834 | 93.2004 | 90.2027 | 58.8505 | 0 | 0 | 0
28.2875 | 93.3838 | 90.3853 | 58.5653 | 0 | 0 | 0
28.2917 | 93.5614 | 90.5735 | 58.2663 | 0 | 0 | 0
28.2959 | 92.8986 | 89.9638 | 58.4287 | 0 | 0 | 0
28.3 | 92.2288 | 89.3477 | 58.6051 | 0 | 0 | 0
28.3042 | 92.3932 | 89.5377 | 58.3244 | 0 | 0 | 0
28.3084 | 92.5645 | 89.7309 | 58.0279 | 0 | 0 | 0
28.3125 | 91.8928 | 89.1156 | 58.1969 | 0 | 0 | 0
28.3167 | 91.2038 | 88.4912 | 58.3778 | 0 | 0 | 0
28.3209 | 91.3741 | 88.6614 | 58.0823 | 0 | 0 | 0
28.325 | 91.5501 | 88.8386 | 57.774 | 0 | 0 | 0
28.3292 | 90.8643 | 88.2054 | 57.9302 | 0 | 0 | 0
28.3334 | 90.1678 | 87.5609 | 58.0985 | 0 | 0 | 0
28.3375 | 90.3159 | 87.7389 | 57.812 | 0 | 0 | 0
28.3417 | 90.4781 | 87.9212 | 57.5125 | 0 | 0 | 0
28.3459 | 89.7736 | 87.2878 | 57.6773 | 0 | 0 | 0
28.35 | 89.0594 | 86.646 | 57.8571 | 0 | 0 | 0
28.3542 | 89.1988 | 86.797 | 57.5652 | 0 | 0 | 0
28.3584 | 89.336 | 86.9525 | 57.2598 | 0 | 0 | 0
28.3625 | 88.6277 | 86.3044 | 57.4242 | 0 | 0 | 0
28.3667 | 87.9099 | 85.6492 | 57.6037 | 0 | 0 | 0
28.3709 | 88.0444 | 85.7989 | 57.3271 | 0 | 0 | 0
28.375 | 88.1751 | 85.9511 | 57.0375 | 0 | 0 | 0
28.3792 | 87.452 | 85.3016 | 57.2046 | 0 | 0 | 0
28.3834 | 86.7139 | 84.641 | 57.3848 | 0 | 0 | 0
28.3875 | 86.8235 | 84.7685 | 57.107 | 0 | 0 | 0
28.3917 | 86.9327 | 84.9008 | 56.8169 | 0 | 0 | 0
28.3959 | 86.187 | 84.2359 | 56.982 | 0 | 0 | 0
28.4 | 85.4319 | 83.5591 | 57.1609 | 0 | 0 | 0
28.4042 | 85.5272 | 83.6777 | 56.8871 | 0 | 0 | 0
28.4084 | 85.6244 | 83.8013 | 56.6006 | 0 | 0 | 0
28.4125 | 84.8721 | 83.1136 | 56.7705 | 0 | 0 | 0
28.4167 | 84.1035 | 82.4146 | 56.9555 | 0 | 0 | 0
28.4209 | 84.1805 | 82.5298 | 56.6875 | 0 | 0 | 0
28.425 | 84.2586 | 82.647 | 56.4066 | 0 | 0 | 0
28.4292 | 83.4764 | 81.9352 | 56.5826 | 0 | 0 | 0
28.4334 | 82.6787 | 81.2144 | 56.7736 | 0 | 0 | 0
28.4375 | 82.7273 | 81.305 | 56.5002 | 0 | 0 | 0
28.4417 | 82.7791 | 81.395 | 56.2147 | 0 | 0 | 0
28.4459 | 81.9793 | 80.675 | 56.4046 | 0 | 0 | 0
28.45 | 81.1724 | 79.9428 | 56.6089 | 0 | 0 | 0
28.4542 | 81.2051 | 80.0004 | 56.3403 | 0 | 0 | 0
28.4584 | 81.2329 | 80.0609 | 56.0607 | 0 | 0 | 0
28.4625 | 80.4133 | 79.3266 | 56.2574 | 0 | 0 | 0
28.4667 | 79.5707 | 78.5779 | 56.4694 | 0 | 0 | 0
28.4709 | 79.5579 | 78.6047 | 56.2101 | 0 | 0 | 0
28.475 | 79.5596 | 78.6326 | 55.9402 | 0 | 0 | 0
28.4792 | 78.6939 | 77.8671 | 56.1438 | 0 | 0 | 0
28.4834 | 77.8246 | 77.0857 | 56.3621 | 0 | 0 | 0
28.4875 | 77.8118 | 77.0917 | 56.1096 | 0 | 0 | 0
28.4917 | 77.7754 | 77.0961 | 55.8467 | 0 | 0 | 0
28.4959 | 76.8905 | 76.2916 | 56.0619 | 0 | 0 | 0
28.5 | 75.9897 | 75.4718 | 56.293 | 0 | 0 | 0
28.5042 | 75.9196 | 75.4575 | 56.0526 | 0 | 0 | 0
28.5084 | 75.8567 | 75.441 | 55.8018 | 0 | 0 | 0
28.5125 | 74.9303 | 74.5969 | 56.0247 | 0 | 0 | 0
28.5167 | 73.9842 | 73.7386 | 56.2639 | 0 | 0 | 0
28.5209 | 73.8806 | 73.6847 | 56.0376 | 0 | 0 | 0
28.525 | 73.7764 | 73.6297 | 55.8006 | 0 | 0 | 0
28.5292 | 72.8129 | 72.7551 | 56.0319 | 0 | 0 | 0
28.5334 | 71.8325 | 71.8652 | 56.2821 | 0 | 0 | 0
28.5375 | 71.6908 | 71.7629 | 56.0745 | 0 | 0 | 0
28.5417 | 71.5436 | 71.6559 | 55.8571 | 0 | 0 | 0
28.5459 | 70.5342 | 70.7504 | 56.1063 | 0 | 0 | 0
28.55 | 69.5056 | 69.8255 | 56.3731 | 0 | 0 | 0
28.5542 | 69.3132 | 69.6775 | 56.1828 | 0 | 0 | 0
28.5584 | 69.1186 | 69.5255 | 55.9852 | 0 | 0 | 0
28.5625 | 68.0604 | 68.5659 | 56.2547 | 0 | 0 | 0
28.5667 | 66.9793 | 67.585 | 56.5413 | 0 | 0 | 0
28.5709 | 66.7375 | 67.3941 | 56.3696 | 0 | 0 | 0
28.575 | 66.4881 | 67.197 | 56.1916 | 0 | 0 | 0
28.5792 | 65.3739 | 66.1764 | 56.4891 | 0 | 0 | 0
28.5834 | 64.2504 | 65.1408 | 56.8116 | 0 | 0 | 0
28.5875 | 63.9573 | 64.9073 | 56.6727 | 0 | 0 | 0
28.5917 | 63.6528 | 64.6644 | 56.5269 | 0 | 0 | 0
28.5959 | 62.4852 | 63.5906 | 56.8633 | 0 | 0 | 0
28.6 | 61.2851 | 62.487 | 57.216 | 0 | 0 | 0
28.6042 | 60.9037 | 62.1612 | 57.0981 | 0 | 0 | 0
28.6084 | 60.5218 | 61.8342 | 56.9833 | 0 | 0 | 0
28.6125 | 59.2777 | 60.7023 | 57.359 | 0 | 0 | 0
28.6167 | 58.0172 | 59.5548 | 57.7667 | 0 | 0 | 0
28.6209 | 57.5982 | 59.1892 | 57.7251 | 0 | 0 | 0
28.625 | 57.1529 | 58.7987 | 57.6745 | 0 | 0 | 0
28.6292 | 55.827 | 57.5805 | 58.0956 | 0 | 0 | 0
28.6334 | 54.4615 | 56.3247 | 58.537 | 0 | 0 | 0
28.6375 | 53.9264 | 55.8319 | 58.5232 | 0 | 0 | 0
28.6417 | 53.3952 | 55.3458 | 58.5272 | 0 | 0 | 0
28.6459 | 52.0024 | 54.0573 | 59.0287 | 0 | 0 | 0
28.65 | 50.5871 | 52.7512 | 59.5724 | 0 | 0 | 0
28.6542 | 50.0035 | 52.2345 | 59.6806 | 0 | 0 | 0
28.6584 | 49.3789 | 51.6832 | 59.7829 | 0 | 0 | 0
28.6625 | 47.8825 | 50.2783 | 60.3611 | 0 | 0 | 0
28.6667 | 46.346 | 48.839 | 60.9731 | 0 | 0 | 0
28.6709 | 45.6239 | 48.1842 | 61.1373 | 0 | 0 | 0
28.675 | 44.8887 | 47.5177 | 61.3206 | 0 | 0 | 0
28.6792 | 43.2843 | 46.0183 | 62.0064 | 0 | 0 | 0
28.6834 | 41.6607 | 44.4925 | 62.7386 | 0 | 0 | 0
28.6875 | 40.8605 | 43.7514 | 63.0382 | 0 | 0 | 0
28.6917 | 40.0558 | 42.9987 | 63.3629 | 0 | 0 | 0
28.6959 | 38.3727 | 41.4372 | 64.1971 | 0 | 0 | 0
28.7 | 36.6534 | 39.8315 | 65.0776 | 0 | 0 | 0
28.7042 | 35.765 | 38.9905 | 65.5216 | 0 | 0 | 0
28.7084 | 34.8483 | 38.117 | 65.9841 | 0 | 0 | 0
28.7125 | 32.7864 | 36.1763 | 67.0949 | 0 | 0 | 0
28.7167 | 30.6952 | 34.2015 | 68.2729 | 0 | 0 | 0
28.7209 | 29.9197 | 33.4721 | 68.7585 | 0 | 0 | 0
28.725 | 29.1471 | 32.7384 | 69.2803 | 0 | 0 | 0
28.7292 | 28.1002 | 31.7548 | 69.9878 | 0 | 0 | 0
28.7334 | 27.0449 | 30.7646 | 70.7414 | 0 | 0 | 0
28.7375 | 27.2371 | 30.9665 | 70.8295 | 0 | 0 | 0
28.7417 | 27.4483 | 31.1878 | 70.9251 | 0 | 0 | 0
28.7459 | 27.0484 | 30.8275 | 71.3824 | 0 | 0 | 0
28.75 | 26.6462 | 30.4668 | 71.8623 | 0 | 0 | 0
28.7542 | 27.2124 | 31.0347 | 71.82 | 0 | 0 | 0
28.7584 | 27.7793 | 31.6039 | 71.7639 | 0 | 0 | 0
28.7625 | 27.5547 | 31.4147 | 72.1458 | 0 | 0 | 0
28.7667 | 27.3405 | 31.2306 | 72.5485 | 0 | 0 | 0
28.7709 | 28.0143 | 31.8891 | 72.4797 | 0 | 0 | 0
28.775 | 28.7128 | 32.5791 | 72.4097 | 0 | 0 | 0
28.7792 | 28.5736 | 32.4964 | 72.8081 | 0 | 0 | 0
28.7834 | 28.4503 | 32.4269 | 73.2313 | 0 | 0 | 0
28.7875 | 29.1824 | 33.1721 | 73.1967 | 0 | 0 | 0
28.7917 | 29.9491 | 33.9398 | 73.1581 | 0 | 0 | 0
28.7959 | 29.8606 | 33.9243 | 73.5981 | 0 | 0 | 0
28.8 | 29.7684 | 33.899 | 74.0496 | 0 | 0 | 0
28.8042 | 30.5026 | 34.6509 | 74.03 | 0 | 0 | 0
28.8084 | 31.2321 | 35.3891 | 73.9863 | 0 | 0 | 0
28.8125 | 31.0991 | 35.306 | 74.4075 | 0 | 0 | 0
28.8167 | 30.9368 | 35.1914 | 74.8275 | 0 | 0 | 0
28.8209 | 31.6006 | 35.8502 | 74.7628 | 0 | 0 | 0
28.825 | 32.2567 | 36.4961 | 74.6712 | 0 | 0 | 0
28.8292 | 32.0443 | 36.3098 | 75.0375 | 0 | 0 | 0
28.8334 | 31.8221 | 36.101 | 75.4087 | 0 | 0 | 0
28.8375 | 32.4416 | 36.6897 | 75.3071 | 0 | 0 | 0
28.8417 | 33.0633 | 37.2805 | 75.1932 | 0 | 0 | 0
28.8459 | 32.8387 | 37.0622 | 75.5435 | 0 | 0 | 0
28.85 | 32.6181 | 36.8442 | 75.9133 | 0 | 0 | 0
28.8542 | 33.243 | 37.4353 | 75.8287 | 0 | 0 | 0
28.8584 | 33.8888 | 38.0374 | 75.7324 | 0 | 0 | 0
28.8625 | 33.6918 | 37.856 | 76.1006 | 0 | 0 | 0
28.8667 | 33.5009 | 37.6767 | 76.4868 | 0 | 0 | 0
28.8709 | 34.1582 | 38.295 | 76.4153 | 0 | 0 | 0
28.875 | 34.8304 | 38.925 | 76.33 | 0 | 0 | 0
28.8792 | 34.6577 | 38.7752 | 76.7091 | 0 | 0 | 0
28.8834 | 34.4807 | 38.6113 | 77.0942 | 0 | 0 | 0
28.8875 | 35.127 | 39.2262 | 77.0048 | 0 | 0 | 0
28.8917 | 35.7864 | 39.8443 | 76.9032 | 0 | 0 | 0
28.8959 | 35.6137 | 39.6769 | 77.269 | 0 | 0 | 0
28.9 | 35.4215 | 39.4919 | 77.6427 | 0 | 0 | 0
28.9042 | 36.0479 | 40.0678 | 77.5431 | 0 | 0 | 0
28.9084 | 36.6712 | 40.6442 | 77.427 | 0 | 0 | 0
28.9125 | 36.4605 | 40.4304 | 77.772 | 0 | 0 | 0
28.9167 | 36.2471 | 40.2117 | 78.1328 | 0 | 0 | 0
28.9209 | 36.8659 | 40.7895 | 78.0332 | 0 | 0 | 0
28.925 | 37.4851 | 41.3709 | 77.9154 | 0 | 0 | 0
28.9292 | 37.2647 | 41.1419 | 78.2557 | 0 | 0 | 0
28.9334 | 37.0384 | 40.9168 | 78.6115 | 0 | 0 | 0
28.9375 | 37.6501 | 41.4841 | 78.5114 | 0 | 0 | 0
28.9417 | 38.2679 | 42.0663 | 78.4002 | 0 | 0 | 0
28.9459 | 38.0432 | 41.8686 | 78.7503 | 0 | 0 | 0
28.95 | 37.8096 | 41.6602 | 79.1098 | 0 | 0 | 0
28.9542 | 38.4299 | 42.2515 | 78.9987 | 0 | 0 | 0
28.9584 | 39.0721 | 42.8533 | 78.8784 | 0 | 0 | 0
28.9625 | 38.8499 | 42.6346 | 79.2356 | 0 | 0 | 0
28.9667 | 38.6203 | 42.409 | 79.604 | 0 | 0 | 0
28.9709 | 39.2411 | 42.9917 | 79.4934 | 0 | 0 | 0
28.975 | 39.8656 | 43.5789 | 79.3657 | 0 | 0 | 0
28.9792 | 39.629 | 43.3719 | 79.7076 | 0 | 0 | 0
28.9834 | 39.3907 | 43.1539 | 80.0663 | 0 | 0 | 0
28.9875 | 40.025 | 43.7554 | 79.9529 | 0 | 0 | 0
28.9917 | 40.6653 | 44.3607 | 79.8234 | 0 | 0 | 0
28.9959 | 40.4435 | 44.12 | 80.1692 | 0 | 0 | 0
29 | 40.218 | 43.8775 | 80.5271 | 0 | 0 | 0
29.0042 | 40.8443 | 44.4612 | 80.4109 | 0 | 0 | 0
29.0084 | 41.4755 | 45.0517 | 80.2803 | 0 | 0 | 0
29.0125 | 41.2492 | 44.8564 | 80.6125 | 0 | 0 | 0
29.0167 | 41.0214 | 44.653 | 80.9565 | 0 | 0 | 0
29.0209 | 41.6439 | 45.2356 | 80.8381 | 0 | 0 | 0
29.025 | 42.2742 | 45.8277 | 80.7065 | 0 | 0 | 0
29.0292 | 42.075 | 45.6222 | 81.0372 | 0 | 0 | 0
29.0334 | 41.866 | 45.4101 | 81.3794 | 0 | 0 | 0
29.0375 | 42.4852 | 45.9825 | 81.2577 | 0 | 0 | 0
29.0417 | 43.1146 | 46.5628 | 81.1203 | 0 | 0 | 0
29.0459 | 42.9029 | 46.3708 | 81.4428 | 0 | 0 | 0
29.05 | 42.6846 | 46.1714 | 81.7763 | 0 | 0 | 0
29.0542 | 43.3055 | 46.7605 | 81.6398 | 0 | 0 | 0
29.0584 | 43.9387 | 47.3583 | 81.4896 | 0 | 0 | 0
29.0625 | 43.7322 | 47.1568 | 81.8111 | 0 | 0 | 0
29.0667 | 43.5204 | 46.9515 | 82.1449 | 0 | 0 | 0
29.0709 | 44.156 | 47.5485 | 82.0044 | 0 | 0 | 0
29.075 | 44.8049 | 48.1532 | 81.8485 | 0 | 0 | 0
29.0792 | 44.597 | 47.9396 | 82.1636 | 0 | 0 | 0
29.0834 | 44.3818 | 47.7204 | 82.4911 | 0 | 0 | 0
29.0875 | 45.0249 | 48.3298 | 82.3428 | 0 | 0 | 0
29.0917 | 45.6713 | 48.945 | 82.1784 | 0 | 0 | 0
29.0959 | 45.4536 | 48.7463 | 82.4824 | 0 | 0 | 0
29.1 | 45.2316 | 48.5422 | 82.7991 | 0 | 0 | 0
29.1042 | 45.8784 | 49.1413 | 82.6455 | 0 | 0 | 0
29.1084 | 46.5365 | 49.7524 | 82.4786 | 0 | 0 | 0
29.1125 | 46.3417 | 49.5567 | 82.7753 | 0 | 0 | 0
29.1167 | 46.1436 | 49.3556 | 83.0839 | 0 | 0 | 0
29.1209 | 46.7884 | 49.9562 | 82.931 | 0 | 0 | 0
29.125 | 47.4376 | 50.5648 | 82.7649 | 0 | 0 | 0
29.1292 | 47.2456 | 50.3873 | 83.0631 | 0 | 0 | 0
29.1334 | 47.0495 | 50.2014 | 83.3725 | 0 | 0 | 0
29.1375 | 47.7016 | 50.8011 | 83.2077 | 0 | 0 | 0
29.1417 | 48.3585 | 51.4063 | 83.0272 | 0 | 0 | 0
29.1459 | 48.1714 | 51.2202 | 83.3116 | 0 | 0 | 0
29.15 | 47.9892 | 51.0283 | 83.6092 | 0 | 0 | 0
29.1542 | 48.6442 | 51.6391 | 83.4481 | 0 | 0 | 0
29.1584 | 49.3102 | 52.2555 | 83.272 | 0 | 0 | 0
29.1625 | 49.1399 | 52.0638 | 83.5553 | 0 | 0 | 0
29.1667 | 48.9608 | 51.8677 | 83.8533 | 0 | 0 | 0
29.1709 | 49.6322 | 52.4757 | 83.6802 | 0 | 0 | 0
29.175 | 50.3199 | 53.0937 | 83.4959 | 0 | 0 | 0
29.1792 | 50.1446 | 52.9148 | 83.7857 | 0 | 0 | 0
29.1834 | 49.9655 | 52.7286 | 84.0887 | 0 | 0 | 0
29.1875 | 50.642 | 53.3614 | 83.9335 | 0 | 0 | 0
29.1917 | 51.3325 | 54.0043 | 83.7663 | 0 | 0 | 0
29.1959 | 51.1749 | 53.8259 | 84.056 | 0 | 0 | 0
29.2 | 51.0047 | 53.6439 | 84.3598 | 0 | 0 | 0
29.2042 | 51.7027 | 54.2679 | 84.1942 | 0 | 0 | 0
29.2084 | 52.4056 | 54.9007 | 84.0138 | 0 | 0 | 0
29.2125 | 52.2626 | 54.7415 | 84.3052 | 0 | 0 | 0
29.2167 | 52.1202 | 54.5784 | 84.6103 | 0 | 0 | 0
29.2209 | 52.8255 | 55.2231 | 84.4509 | 0 | 0 | 0
29.225 | 53.539 | 55.8744 | 84.2765 | 0 | 0 | 0
29.2292 | 53.3983 | 55.723 | 84.5556 | 0 | 0 | 0
29.2334 | 53.2593 | 55.5674 | 84.8471 | 0 | 0 | 0
29.2375 | 53.9717 | 56.2088 | 84.6805 | 0 | 0 | 0
29.2417 | 54.6995 | 56.8615 | 84.5007 | 0 | 0 | 0
29.2459 | 54.5786 | 56.7258 | 84.778 | 0 | 0 | 0
29.25 | 54.4601 | 56.5854 | 85.0677 | 0 | 0 | 0
29.2542 | 55.1969 | 57.2444 | 84.9037 | 0 | 0 | 0
29.2584 | 55.9446 | 57.9153 | 84.7259 | 0 | 0 | 0
29.2625 | 55.8439 | 57.787 | 85.0016 | 0 | 0 | 0
29.2667 | 55.7395 | 57.6538 | 85.2905 | 0 | 0 | 0
29.2709 | 56.4835 | 58.3369 | 85.1232 | 0 | 0 | 0
29.275 | 57.2431 | 59.0303 | 84.9408 | 0 | 0 | 0
29.2792 | 57.1531 | 58.9054 | 85.2117 | 0 | 0 | 0
29.2834 | 57.0621 | 58.7789 | 85.4955 | 0 | 0 | 0
29.2875 | 57.8302 | 59.479 | 85.3186 | 0 | 0 | 0
29.2917 | 58.6144 | 60.1873 | 85.127 | 0 | 0 | 0
29.2959 | 58.555 | 60.0899 | 85.4047 | 0 | 0 | 0
29.3 | 58.4953 | 59.9918 | 85.6944 | 0 | 0 | 0
29.3042 | 59.2859 | 60.6983 | 85.5075 | 0 | 0 | 0
29.3084 | 60.0818 | 61.4176 | 85.3066 | 0 | 0 | 0
29.3125 | 60.0392 | 61.3505 | 85.5784 | 0 | 0 | 0
29.3167 | 59.9955 | 61.2801 | 85.8617 | 0 | 0 | 0
29.3209 | 60.7963 | 62.0007 | 85.6692 | 0 | 0 | 0
29.325 | 61.6245 | 62.7349 | 85.4616 | 0 | 0 | 0
29.3292 | 61.6154 | 62.6929 | 85.7246 | 0 | 0 | 0
29.3334 | 61.5997 | 62.649 | 85.998 | 0 | 0 | 0
29.3375 | 62.4577 | 63.4023 | 85.7979 | 0 | 0 | 0
29.3417 | 63.3092 | 64.1702 | 85.5832 | 0 | 0 | 0
29.3459 | 63.3127 | 64.1469 | 85.8406 | 0 | 0 | 0
29.35 | 63.3324 | 64.1249 | 86.1089 | 0 | 0 | 0
29.3542 | 64.1947 | 64.9165 | 85.8995 | 0 | 0 | 0
29.3584 | 65.0807 | 65.7232 | 85.6741 | 0 | 0 | 0
29.3625 | 65.1291 | 65.7198 | 85.9191 | 0 | 0 | 0
29.3667 | 65.1715 | 65.7188 | 86.1745 | 0 | 0 | 0
29.3709 | 66.0792 | 66.5434 | 85.9577 | 0 | 0 | 0
29.375 | 67.0042 | 67.3828 | 85.7247 | 0 | 0 | 0
29.3792 | 67.0888 | 67.4197 | 85.9559 | 0 | 0 | 0
29.3834 | 67.1741 | 67.4575 | 86.1986 | 0 | 0 | 0
29.3875 | 68.1182 | 68.31 | 85.9752 | 0 | 0 | 0
29.3917 | 69.0775 | 69.1765 | 85.7334 | 0 | 0 | 0
29.3959 | 69.197 | 69.2608 | 85.9496 | 0 | 0 | 0
29.4 | 69.3207 | 69.348 | 86.1754 | 0 | 0 | 0
29.4042 | 70.3054 | 70.2319 | 85.9348 | 0 | 0 | 0
29.4084 | 71.3098 | 71.1348 | 85.6774 | 0 | 0 | 0
29.4125 | 71.4773 | 71.2573 | 85.8773 | 0 | 0 | 0
29.4167 | 71.6458 | 71.3829 | 86.0847 | 0 | 0 | 0
29.4209 | 72.6787 | 72.3192 | 85.8246 | 0 | 0 | 0
29.425 | 73.7324 | 73.2759 | 85.5478 | 0 | 0 | 0
29.4292 | 73.9466 | 73.4383 | 85.732 | 0 | 0 | 0
29.4334 | 74.1722 | 73.6088 | 85.9252 | 0 | 0 | 0
29.4375 | 75.2595 | 74.6053 | 85.643 | 0 | 0 | 0
29.4417 | 76.3562 | 75.6162 | 85.3363 | 0 | 0 | 0
29.4459 | 76.622 | 75.8236 | 85.4932 | 0 | 0 | 0
29.45 | 76.8915 | 76.0352 | 85.6545 | 0 | 0 | 0
29.4542 | 78.02 | 77.069 | 85.3311 | 0 | 0 | 0
29.4584 | 79.182 | 78.1335 | 84.9939 | 0 | 0 | 0
29.4625 | 79.5242 | 78.4262 | 85.1292 | 0 | 0 | 0
29.4667 | 79.8726 | 78.7251 | 85.2676 | 0 | 0 | 0
29.4709 | 81.0904 | 79.8321 | 84.9233 | 0 | 0 | 0
29.475 | 82.318 | 80.9486 | 84.5448 | 0 | 0 | 0
29.4792 | 82.7003 | 81.2766 | 84.6121 | 0 | 0 | 0
29.4834 | 83.0989 | 81.6201 | 84.6837 | 0 | 0 | 0
29.4875 | 84.3731 | 82.7827 | 84.2805 | 0 | 0 | 0
29.4917 | 85.6937 | 83.9904 | 83.8645 | 0 | 0 | 0
29.4959 | 86.1884 | 84.4405 | 83.9111 | 0 | 0 | 0
29.5 | 86.6872 | 84.8931 | 83.9497 | 0 | 0 | 0
29.5042 | 88.0496 | 86.1588 | 83.4999 | 0 | 0 | 0
29.5084 | 89.4221 | 87.4313 | 83.0034 | 0 | 0 | 0
29.5125 | 89.9602 | 87.9009 | 82.938 | 0 | 0 | 0
29.5167 | 90.5293 | 88.396 | 82.8743 | 0 | 0 | 0
29.5209 | 91.9633 | 89.7383 | 82.3292 | 0 | 0 | 0
29.525 | 93.4434 | 91.1196 | 81.7572 | 0 | 0 | 0
29.5292 | 94.1077 | 91.7211 | 81.64 | 0 | 0 | 0
29.5334 | 94.7939 | 92.3386 | 81.5103 | 0 | 0 | 0
29.5375 | 96.3518 | 93.7905 | 80.8854 | 0 | 0 | 0
29.5417 | 97.9347 | 95.2702 | 80.2184 | 0 | 0 | 0
29.5459 | 98.6921 | 95.9738 | 79.9887 | 0 | 0 | 0
29.55 | 99.4502 | 96.6835 | 79.7352 | 0 | 0 | 0
29.5542 | 101.0881 | 98.1981 | 78.9727 | 0 | 0 | 0
29.5584 | 102.753 | 99.7479 | 78.1622 | 0 | 0 | 0
29.5625 | 103.4985 | 100.4455 | 77.8345 | 0 | 0 | 0
29.5667 | 104.2715 | 101.1758 | 77.4947 | 0 | 0 | 0
29.5709 | 106.3205 | 103.1035 | 76.4371 | 0 | 0 | 0
29.575 | 108.4088 | 105.0745 | 75.3204 | 0 | 0 | 0
29.5792 | 109.5162 | 106.1168 | 74.7184 | 0 | 0 | 0
29.5834 | 110.6309 | 107.1754 | 74.0759 | 0 | 0 | 0
29.5875 | 112.1098 | 108.5728 | 73.1974 | 0 | 0 | 0
29.5917 | 113.6059 | 109.9886 | 72.2618 | 0 | 0 | 0
29.5959 | 113.7732 | 110.1323 | 72.0333 | 0 | 0 | 0
29.6 | 113.9266 | 110.2626 | 71.7858 | 0 | 0 | 0
29.6042 | 114.5713 | 110.8604 | 71.2383 | 0 | 0 | 0
29.6084 | 115.2138 | 111.4545 | 70.6572 | 0 | 0 | 0
29.6125 | 114.788 | 111.0232 | 70.6443 | 0 | 0 | 0
29.6167 | 114.3641 | 110.591 | 70.641 | 0 | 0 | 0
29.6209 | 114.6716 | 110.8561 | 70.2319 | 0 | 0 | 0
29.625 | 114.9776 | 111.1264 | 69.8047 | 0 | 0 | 0
29.6292 | 114.3603 | 110.529 | 69.87 | 0 | 0 | 0
29.6334 | 113.7231 | 109.9062 | 69.9387 | 0 | 0 | 0
29.6375 | 113.9008 | 110.0386 | 69.5506 | 0 | 0 | 0
29.6417 | 114.0677 | 110.1569 | 69.1375 | 0 | 0 | 0
29.6459 | 113.3658 | 109.4511 | 69.1895 | 0 | 0 | 0
29.65 | 112.6246 | 108.7148 | 69.241 | 0 | 0 | 0
29.6542 | 112.7243 | 108.7462 | 68.8118 | 0 | 0 | 0
29.6584 | 112.8131 | 108.7726 | 68.363 | 0 | 0 | 0
29.6625 | 112.0683 | 108.004 | 68.3799 | 0 | 0 | 0
29.6667 | 111.3147 | 107.2369 | 68.4141 | 0 | 0 | 0
29.6709 | 111.4211 | 107.2838 | 67.9771 | 0 | 0 | 0
29.675 | 111.5513 | 107.3583 | 67.538 | 0 | 0 | 0
29.6792 | 110.8525 | 106.6534 | 67.5792 | 0 | 0 | 0
29.6834 | 110.1661 | 105.9631 | 67.6483 | 0 | 0 | 0
29.6875 | 110.3523 | 106.1108 | 67.2619 | 0 | 0 | 0
29.6917 | 110.5532 | 106.2867 | 66.8758 | 0 | 0 | 0
29.6959 | 109.9211 | 105.6747 | 66.9654 | 0 | 0 | 0
29.7 | 109.2931 | 105.0701 | 67.0739 | 0 | 0 | 0
29.7042 | 109.5156 | 105.2816 | 66.7252 | 0 | 0 | 0
29.7084 | 109.7423 | 105.4989 | 66.3595 | 0 | 0 | 0
29.7125 | 109.1262 | 104.9181 | 66.4508 | 0 | 0 | 0
29.7167 | 108.4926 | 104.3289 | 66.5539 | 0 | 0 | 0
29.7209 | 108.7036 | 104.523 | 66.1923 | 0 | 0 | 0
29.725 | 108.9076 | 104.7161 | 65.8122 | 0 | 0 | 0
29.7292 | 108.2634 | 104.1129 | 65.8896 | 0 | 0 | 0
29.7334 | 107.6005 | 103.4928 | 65.9765 | 0 | 0 | 0
29.7375 | 107.7742 | 103.6468 | 65.5935 | 0 | 0 | 0
29.7417 | 107.9504 | 103.8103 | 65.2036 | 0 | 0 | 0
29.7459 | 107.3047 | 103.1912 | 65.2873 | 0 | 0 | 0
29.75 | 106.6402 | 102.5662 | 65.3836 | 0 | 0 | 0
29.7542 | 106.8068 | 102.7195 | 65.0126 | 0 | 0 | 0
29.7584 | 106.9856 | 102.8885 | 64.6322 | 0 | 0 | 0
29.7625 | 106.3448 | 102.2926 | 64.7232 | 0 | 0 | 0
29.7667 | 105.7102 | 101.6999 | 64.8328 | 0 | 0 | 0
29.7709 | 105.9138 | 101.9078 | 64.4849 | 0 | 0 | 0
29.775 | 106.1223 | 102.123 | 64.1215 | 0 | 0 | 0
29.7792 | 105.4982 | 101.5383 | 64.2187 | 0 | 0 | 0
29.7834 | 104.8732 | 100.9538 | 64.334 | 0 | 0 | 0
29.7875 | 105.0897 | 101.1772 | 63.9927 | 0 | 0 | 0
29.7917 | 105.3139 | 101.4017 | 63.6383 | 0 | 0 | 0
29.7959 | 104.6997 | 100.843 | 63.7414 | 0 | 0 | 0
29.8 | 104.0789 | 100.2665 | 63.8543 | 0 | 0 | 0
29.8042 | 104.3058 | 100.4753 | 63.5016 | 0 | 0 | 0
29.8084 | 104.5468 | 100.6922 | 63.1397 | 0 | 0 | 0
29.8125 | 103.9283 | 100.0978 | 63.2523 | 0 | 0 | 0
29.8167 | 103.2901 | 99.4934 | 63.3749 | 0 | 0 | 0
29.8209 | 103.5134 | 99.7083 | 63.0184 | 0 | 0 | 0
29.825 | 103.7386 | 99.9284 | 62.6483 | 0 | 0 | 0
29.8292 | 103.1136 | 99.3485 | 62.7541 | 0 | 0 | 0
29.8334 | 102.4849 | 98.7622 | 62.878 | 0 | 0 | 0
29.8375 | 102.7249 | 98.9765 | 62.5336 | 0 | 0 | 0
29.8417 | 102.9673 | 99.201 | 62.1731 | 0 | 0 | 0
29.8459 | 102.3392 | 98.591 | 62.287 | 0 | 0 | 0
29.85 | 101.7048 | 97.9799 | 62.4157 | 0 | 0 | 0
29.8542 | 101.9262 | 98.2119 | 62.0692 | 0 | 0 | 0
29.8584 | 102.1508 | 98.4478 | 61.7108 | 0 | 0 | 0
29.8625 | 101.5232 | 97.8765 | 61.8222 | 0 | 0 | 0
29.8667 | 100.8911 | 97.297 | 61.9479 | 0 | 0 | 0
29.8709 | 101.116 | 97.4962 | 61.6135 | 0 | 0 | 0
29.875 | 101.3434 | 97.704 | 61.2676 | 0 | 0 | 0
29.8792 | 100.7296 | 97.1195 | 61.3848 | 0 | 0 | 0
29.8834 | 100.1057 | 96.5261 | 61.5152 | 0 | 0 | 0
29.8875 | 100.3069 | 96.7278 | 61.183 | 0 | 0 | 0
29.8917 | 100.518 | 96.9357 | 60.8385 | 0 | 0 | 0
29.8959 | 99.8955 | 96.3667 | 60.9571 | 0 | 0 | 0
29.9 | 99.2639 | 95.7894 | 61.0909 | 0 | 0 | 0
29.9042 | 99.4753 | 95.9883 | 60.7624 | 0 | 0 | 0
29.9084 | 99.6943 | 96.1947 | 60.4234 | 0 | 0 | 0
29.9125 | 99.0753 | 95.6049 | 60.5577 | 0 | 0 | 0
29.9167 | 98.4447 | 95.0076 | 60.7062 | 0 | 0 | 0
29.9209 | 98.6569 | 95.2117 | 60.3826 | 0 | 0 | 0
29.925 | 98.875 | 95.4197 | 60.0464 | 0 | 0 | 0
29.9292 | 98.2411 | 94.8197 | 60.1842 | 0 | 0 | 0
29.9334 | 97.5934 | 94.2115 | 60.3372 | 0 | 0 | 0
29.9375 | 97.8046 | 94.4284 | 60.0186 | 0 | 0 | 0
29.9417 | 98.0196 | 94.65 | 59.6873 | 0 | 0 | 0
29.9459 | 97.3745 | 94.0469 | 59.8308 | 0 | 0 | 0
29.95 | 96.726 | 93.4377 | 59.9904 | 0 | 0 | 0
29.9542 | 96.9445 | 93.6353 | 59.6831 | 0 | 0 | 0
29.9584 | 97.1698 | 93.8401 | 59.364 | 0 | 0 | 0
29.9625 | 96.5312 | 93.2418 | 59.514 | 0 | 0 | 0
29.9667 | 95.8824 | 92.6322 | 59.6775 | 0 | 0 | 0
29.9709 | 96.0795 | 92.8288 | 59.3799 | 0 | 0 | 0
29.975 | 96.2778 | 93.0297 | 59.0704 | 0 | 0 | 0
29.9792 | 95.6351 | 92.4357 | 59.2235 | 0 | 0 | 0
29.9834 | 94.9868 | 91.8323 | 59.3896 | 0 | 0 | 0
29.9875 | 95.1822 | 92.0118 | 59.0875 | 0 | 0 | 0
29.9917 | 95.3813 | 92.1986 | 58.7734 | 0 | 0 | 0
29.9959 | 94.7322 | 91.5969 | 58.9323 | 0 | 0 | 0
1
2
3