## 4QBEP, 4QOP, MC, System Curves
Interpolated Suter Data |  |  |  | Dimensionless |  |  |  | Dimensionalized Curves |  |  |  | Dimensionalized Curves |  |  |  | Manufacturer Curve |  | System Curve |  | System Curve
For MC Region |  |  |  | Flow and Head |  |  |  | at BEP (4QBEP) (2 Parallel) |  |  |  | at OP (4QOP) (2 Parallel) |  |  |  | (2 Parallel) |  | Initial |  | Final
[9 empty] | QBEP (m3/s) | 0.3895 |  |  | QOP (m3/s) | 0.1618 | [7 empty] | Initial Curve Comparison for Ns = 0.79 (41.9 Metric, 2160 US)
All data in θ=atan(α/ν) form |  |  |  |  | Speed (α) = | 1 |  |  | HBEP (m) | 23.62 |  |  | HOP (m) | 29.34
Ns = | 0.42 | 0.46 | 0.79 | Ns = | 0.42 | 0.46 | 0.79 | Ns = | 0.42 | 0.46 | 0.79 | Ns = | 0.42 | 0.46 | 0.79
θ | FH | FH | FH | ν | h | h | h | Q | H | H | H | Q | H | H | H | Q (m3/s) | H (m) | Q (m3/s) | H (m) | Q (m3/s) | H (m) |  | Graphing Points and Lines
20 | -0.06 | -0.17768 | -0.14 | 2.7475 | -0.51292 | -1.5189 | -1.1968 | 2.1403 | -12.1151 | -35.8761 | -28.2686 | 0.88908 | -15.049 | -44.5642 | -35.1144 | 0 | 28.8581 | 0.034483 | 15.1629 | 0.034483 | 15.0222 |  | BEP | 0.779 | 0
20.5 | -0.05155 | -0.16716 | -0.13 | 2.6746 | -0.42032 | -1.363 | -1.06 | 2.0835 | -9.9279 | -32.193 | -25.0364 | 0.86551 | -12.3321 | -39.9891 | -31.0995 | 0.02 | 28.9986 | 0.067776 | 15.6294 | 0.067776 | 15.0858 |  |  | 0.779 | 100
21 | -0.0432 | -0.158 | -0.12 | 2.6051 | -0.33638 | -1.2302 | -0.93438 | 2.0294 | -7.9452 | -29.058 | -22.07 | 0.84301 | -9.8693 | -36.0949 | -27.4147 | 0.04 | 29.1245 | 0.10107 | 16.3997 | 0.10107 | 15.1909 |  | Initial OP | 0.3236 | 29.34
21.5 | -0.03495 | -0.14914 | -0.11 | 2.5386 | -0.26019 | -1.1103 | -0.81892 | 1.9776 | -6.1458 | -26.2262 | -19.3429 | 0.82151 | -7.6341 | -32.5773 | -24.0271 | 0.06 | 29.2357 | 0.13436 | 17.4737 | 0.13436 | 15.3374 |  | Initial 4QBEP | 0.3506 | 31.83
22 | -0.0268 | -0.14061 | -0.1 | 2.4751 | -0.19098 | -1.002 | -0.71261 | 1.9281 | -4.5109 | -23.6666 | -16.8317 | 0.80094 | -5.6033 | -29.3978 | -20.9078 | 0.08 | 29.3323 | 0.16766 | 18.8515 | 0.16766 | 15.5253 |  | Final MC | 0.727 | 24.8
22.5 | -0.01875 | -0.13238 | -0.09 | 2.4142 | -0.12803 | -0.90397 | -0.61456 | 1.8807 | -3.0241 | -21.3517 | -14.5159 | 0.78124 | -3.7565 | -26.5224 | -18.0311 | 0.1 | 29.4143 | 0.20095 | 20.5331 | 0.20095 | 15.7546 |  | Final 4QOP | 0.416 | 18.23
23 | -0.0108 | -0.12447 | -0.08 | 2.3559 | -0.07074 | -0.8153 | -0.524 | 1.8352 | -1.6709 | -19.2575 | -12.377 | 0.76235 | -2.0755 | -23.921 | -15.3743 | 0.12 | 29.4816 | 0.23424 | 22.5184 | 0.23424 | 16.0254 |  | Final 4QBEP | 0.72 | 24.5
23.5 | -0.00295 | -0.11688 | -0.07 | 2.2998 | -0.018553 | -0.73507 | -0.44025 | 1.7916 | -0.43823 | -17.3624 | -10.3987 | 0.74423 | -0.54436 | -21.567 | -12.9169 | 0.14 | 29.5344 | 0.26754 | 24.8076 | 0.26754 | 16.3376
24 | 0.0048 | -0.10959 | -0.06 | 2.246 | 0.029014 | -0.66246 | -0.36268 | 1.7497 | 0.68532 | -15.6474 | -8.5665 | 0.72682 | 0.85128 | -19.4366 | -10.6411 | 0.16 | 29.5726 | 0.30083 | 27.4004 | 0.30083 | 16.6912
24.5 | 0.01245 | -0.10263 | -0.05 | 2.1943 | 0.072396 | -0.59676 | -0.29075 | 1.7094 | 1.71 | -14.0955 | -6.8675 | 0.71008 | 2.1241 | -17.509 | -8.5305 | 0.18 | 29.5963 | 0.33413 | 30.2971 | 0.33413 | 17.0863 | Final Curve Comparison for Ns = 0.79 (41.9 Metric, 2160 US)
25 | 0.02 | -0.091778 | -0.04 | 2.1445 | 0.11198 | -0.51386 | -0.22396 | 1.6706 | 2.6449 | -12.1373 | -5.2899 | 0.69396 | 3.2854 | -15.0766 | -6.5709 | 0.2 | 29.6054 | 0.36742 | 33.4975 | 0.36742 | 17.5228
25.5 | 0.0324 | -0.079851 | -0.03165 | 2.0965 | 0.17481 | -0.43084 | -0.17077 | 1.6332 | 4.1291 | -10.1764 | -4.0335 | 0.67844 | 5.129 | -12.6407 | -5.0103 | 0.22 | 29.6 | 0.40071 | 37.0017 | 0.40071 | 18.0007
26 | 0.0456 | -0.067222 | -0.0236 | 2.0503 | 0.23729 | -0.34981 | -0.12281 | 1.5972 | 5.6048 | -8.2624 | -2.9007 | 0.66348 | 6.9621 | -10.2633 | -3.6032 | 0.24 | 29.58 | 0.43401 | 40.8096 | 0.43401 | 18.52
26.5 | 0.0596 | -0.053891 | -0.01585 | 2.0057 | 0.29936 | -0.27068 | -0.079611 | 1.5624 | 7.0708 | -6.3935 | -1.8804 | 0.64904 | 8.7832 | -7.9418 | -2.3358 | 0.26 | 29.5456 | 0.4673 | 44.9213 | 0.4673 | 19.0808
27 | 0.0744 | -0.039857 | -0.0084 | 1.9626 | 0.36098 | -0.19338 | -0.040755 | 1.5289 | 8.5263 | -4.5677 | -0.96264 | 0.6351 | 10.5911 | -5.6738 | -1.1958 | 0.28 | 29.4966 | 0.50059 | 49.3368 | 0.50059 | 19.683
27.5 | 0.09 | -0.025122 | -0.00125 | 1.921 | 0.42212 | -0.11783 | -0.0058627 | 1.4964 | 9.9704 | -2.783 | -0.13848 | 0.62163 | 12.3849 | -3.457 | -0.17201 | 0.3 | 29.4332 | 0.53389 | 54.056 | 0.53389 | 20.3266
28 | 0.1064 | -0.0096843 | 0.0056 | 1.8807 | 0.48275 | -0.043939 | 0.025408 | 1.4651 | 11.4026 | -1.0378 | 0.60014 | 0.6086 | 14.1639 | -1.2892 | 0.74547 | 0.32 | 29.3553 | 0.56718 | 59.0791 | 0.56718 | 21.0117
28.5 | 0.1236 | 0.0064552 | 0.01215 | 1.8418 | 0.54287 | 0.028352 | 0.053364 | 1.4347 | 12.8225 | 0.66968 | 1.2605 | 0.596 | 15.9277 | 0.83185 | 1.5657 | 0.34 | 29.2629 | 0.60048 | 64.4058 | 0.60048 | 21.7382
29 | 0.1416 | 0.021075 | 0.0184 | 1.804 | 0.60245 | 0.089665 | 0.078284 | 1.4054 | 14.2299 | 2.1179 | 1.8491 | 0.58379 | 17.6759 | 2.6308 | 2.2969 | 0.36 | 29.1561 | 0.63377 | 70.0364 | 0.63377 | 22.5061
29.5 | 0.1604 | 0.034965 | 0.02435 | 1.7675 | 0.6615 | 0.1442 | 0.10042 | 1.3769 | 15.6245 | 3.4059 | 2.3719 | 0.57196 | 19.4083 | 4.2308 | 2.9463 | 0.38 | 29.0349 | 0.66706 | 75.9707 | 0.66706 | 23.3154
30 | 0.18 | 0.04887 | 0.03 | 1.7321 | 0.72 | 0.19548 | 0.12 | 1.3493 | 17.0064 | 4.6173 | 2.8344 | 0.56049 | 21.1248 | 5.7354 | 3.5208 | 0.4 | 28.8993 | 0.70036 | 82.2088 | 0.70036 | 24.1662
30.5 | 0.19435 | 0.06279 | 0.0403 | 1.6977 | 0.75448 | 0.24376 | 0.15645 | 1.3225 | 17.8208 | 5.7575 | 3.6953 | 0.54936 | 22.1364 | 7.1518 | 4.5902 | 0.42 | 28.7492 | 0.73365 | 88.7507 | 0.73365 | 25.0584
31 | 0.2084 | 0.076725 | 0.0512 | 1.6643 | 0.78563 | 0.28924 | 0.19302 | 1.2965 | 18.5566 | 6.8319 | 4.559 | 0.53856 | 23.0504 | 8.4864 | 5.6631 | 0.44 | 28.5848 | 0.76694 | 95.5963 | 0.76694 | 25.9921
31.5 | 0.22215 | 0.090675 | 0.0627 | 1.6319 | 0.81372 | 0.33214 | 0.22967 | 1.2712 | 19.2201 | 7.8451 | 5.4247 | 0.52807 | 23.8746 | 9.745 | 6.7384 | 0.46 | 28.4059 | 0.80024 | 102.7457 | 0.80024 | 26.9671
32 | 0.2356 | 0.10464 | 0.0748 | 1.6003 | 0.83899 | 0.37263 | 0.26637 | 1.2467 | 19.8169 | 8.8016 | 6.2916 | 0.51787 | 24.6159 | 10.933 | 7.8152 | 0.48 | 28.2128 | 0.83353 | 110.1988 | 0.83353 | 27.9836
32.5 | 0.24875 | 0.11862 | 0.0875 | 1.5697 | 0.86165 | 0.41089 | 0.30309 | 1.2228 | 20.3521 | 9.7052 | 7.159 | 0.50795 | 25.2808 | 12.0555 | 8.8927 | 0.5 | 28.0052 | 0.86683 | 117.9557 | 0.86683 | 29.0415
33 | 0.2616 | 0.13262 | 0.1008 | 1.5399 | 0.8819 | 0.44707 | 0.33982 | 1.1996 | 20.8305 | 10.5598 | 8.0264 | 0.4983 | 25.875 | 13.117 | 9.9702 | 0.52 | 27.7833 | 0.90012 | 126.0164 | 0.90012 | 30.1409
33.5 | 0.27415 | 0.14662 | 0.1147 | 1.5108 | 0.89993 | 0.48131 | 0.37652 | 1.1769 | 21.2564 | 11.3686 | 8.8933 | 0.48891 | 26.404 | 14.1217 | 11.047 | 0.54 | 27.5471 | 0.93341 | 134.3809 | 0.93341 | 31.2817
34 | 0.2864 | 0.16065 | 0.1292 | 1.4826 | 0.9159 | 0.51375 | 0.41318 | 1.1549 | 21.6336 | 12.1349 | 9.7593 | 0.47976 | 26.8726 | 15.0736 | 12.1227 | 0.56 | 27.2966 | 0.96671 | 143.0491 | 0.96671 | 32.4639
34.5 | 0.29835 | 0.17469 | 0.1443 | 1.455 | 0.92997 | 0.54451 | 0.44979 | 1.1335 | 21.9659 | 12.8614 | 10.6241 | 0.47084 | 27.2854 | 15.9761 | 13.1969 | 0.58 | 27.0318 | 1 | 152.0211 | 1 | 33.6875
35 | 0.31 | 0.18874 | 0.16 | 1.4281 | 0.94228 | 0.57371 | 0.48634 | 1.1125 | 22.2566 | 13.5509 | 11.4873 | 0.46215 | 27.6464 | 16.8325 | 14.2691 | 0.6 | 26.7527
35.5 | 0.32135 | 0.20281 | 0.173 | 1.4019 | 0.95295 | 0.60143 | 0.51302 | 1.0921 | 22.5087 | 14.2059 | 12.1176 | 0.45367 | 27.9596 | 17.6461 | 15.0521 | 0.62 | 26.4593
36 | 0.3324 | 0.2169 | 0.186 | 1.3764 | 0.96211 | 0.62779 | 0.53836 | 1.0722 | 22.725 | 14.8285 | 12.7161 | 0.4454 | 28.2282 | 18.4195 | 15.7956 | 0.64 | 26.1517
36.5 | 0.34315 | 0.231 | 0.199 | 1.3514 | 0.96986 | 0.65288 | 0.56244 | 1.0528 | 22.9081 | 15.4209 | 13.2849 | 0.43732 | 28.4557 | 19.1554 | 16.5021 | 0.66 | 25.8298
37 | 0.3536 | 0.24539 | 0.212 | 1.327 | 0.97631 | 0.67753 | 0.58534 | 1.0338 | 23.0604 | 16.0032 | 13.8258 | 0.42943 | 28.6448 | 19.8787 | 17.1739 | 0.68 | 25.4937
37.5 | 0.36375 | 0.26041 | 0.225 | 1.3032 | 0.98154 | 0.70268 | 0.60714 | 1.0152 | 23.184 | 16.5972 | 14.3406 | 0.42172 | 28.7984 | 20.6165 | 17.8135 | 0.7 | 25.1433
38 | 0.3736 | 0.27562 | 0.238 | 1.2799 | 0.98565 | 0.72715 | 0.6279 | 0.99707 | 23.2811 | 17.1752 | 14.8311 | 0.41419 | 28.919 | 21.3345 | 18.4227 | 0.72 | 24.7788
38.5 | 0.38315 | 0.29102 | 0.251 | 1.2572 | 0.98871 | 0.75098 | 0.6477 | 0.97934 | 23.3534 | 17.7381 | 15.2987 | 0.40682 | 29.0088 | 22.0337 | 19.0035 | 0.74 | 24.4
39 | 0.3924 | 0.30662 | 0.264 | 1.2349 | 0.9908 | 0.77421 | 0.66659 | 0.96198 | 23.4027 | 18.2869 | 15.7449 | 0.39961 | 29.07 | 22.7153 | 19.5578 | 0.76 | 24.0071
39.5 | 0.40135 | 0.32242 | 0.277 | 1.2131 | 0.99198 | 0.79688 | 0.68463 | 0.945 | 23.4305 | 18.8224 | 16.1711 | 0.39256 | 29.1046 | 23.3806 | 20.0872 | 0.78 | 23.6
40 | 0.41 | 0.3384 | 0.29 | 1.1918 | 0.99231 | 0.81903 | 0.70188 | 0.92838 | 23.4384 | 19.3455 | 16.5784 | 0.38565 | 29.1145 | 24.0303 | 20.5932 | 0.8 | 23.1787
40.5 | 0.41945 | 0.35459 | 0.3074 | 1.1708 | 0.99447 | 0.84068 | 0.72881 | 0.91209 | 23.4894 | 19.8569 | 17.2145 | 0.37889 | 29.1777 | 24.6656 | 21.3833 | 0.82 | 22.7433
41 | 0.4288 | 0.37086 | 0.3256 | 1.1504 | 0.99625 | 0.86164 | 0.75648 | 0.89614 | 23.5315 | 20.3519 | 17.8681 | 0.37226 | 29.23 | 25.2805 | 22.1952 | 0.84 | 22.2938
41.5 | 0.43805 | 0.38679 | 0.3446 | 1.1303 | 0.99769 | 0.88094 | 0.78485 | 0.8805 | 23.5654 | 20.8078 | 18.5381 | 0.36576 | 29.2722 | 25.8468 | 23.0275 | 0.86 | 21.8301
42 | 0.4472 | 0.40278 | 0.3644 | 1.1106 | 0.9988 | 0.89959 | 0.81387 | 0.86517 | 23.5917 | 21.2483 | 19.2237 | 0.35939 | 29.3049 | 26.394 | 23.879 | 0.88 | 21.3524
42.5 | 0.45625 | 0.41883 | 0.385 | 1.0913 | 0.99962 | 0.91763 | 0.84352 | 0.85013 | 23.6111 | 21.6745 | 19.9239 | 0.35315 | 29.3289 | 26.9233 | 24.7488 | 0.9 | 20.8605
43 | 0.4652 | 0.43494 | 0.4064 | 1.0724 | 1.0002 | 0.9351 | 0.87375 | 0.83538 | 23.624 | 22.0871 | 20.638 | 0.34702 | 29.3449 | 27.4359 | 25.6358 | 0.92 | 20.3546
43.5 | 0.47405 | 0.4511 | 0.4286 | 1.0538 | 1.0005 | 0.95203 | 0.90454 | 0.82089 | 23.6309 | 22.487 | 21.3652 | 0.341 | 29.3535 | 27.9327 | 26.5392 | 0.94 | 19.8346
44 | 0.4828 | 0.46733 | 0.4516 | 1.0355 | 1.0005 | 0.96846 | 0.93586 | 0.80668 | 23.6322 | 22.8751 | 22.105 | 0.3351 | 29.3552 | 28.4147 | 27.4582 | 0.96 | 19.3006
44.5 | 0.49145 | 0.48362 | 0.4754 | 1.0176 | 1.0004 | 0.98442 | 0.96769 | 0.79272 | 23.6285 | 23.252 | 22.8568 | 0.3293 | 29.3505 | 28.8829 | 28.392 | 0.98 | 18.7525
45 | 0.5 | 0.49997 | 0.5 | 1 | 1 | 0.99993 | 1 | 0.779 | 23.62 | 23.6185 | 23.62 | 0.3236 | 29.34 | 29.3381 | 29.34 | 1 | 18.1904
45.5 | 0.5101 | 0.51507 | 0.51605 | 0.9827 | 1.0027 | 1.0125 | 1.0144 | 0.76552 | 23.6838 | 23.9147 | 23.96 | 0.318 | 29.4192 | 29.7061 | 29.7624
46 | 0.5204 | 0.52995 | 0.5312 | 0.96569 | 1.0057 | 1.0242 | 1.0266 | 0.75227 | 23.7547 | 24.1908 | 24.2477 | 0.3125 | 29.5073 | 30.0491 | 30.1197
46.5 | 0.5309 | 0.54461 | 0.54545 | 0.94896 | 1.009 | 1.0351 | 1.0366 | 0.73924 | 23.8324 | 24.4479 | 24.4856 | 0.30708 | 29.6039 | 30.3684 | 30.4152
47 | 0.5416 | 0.55904 | 0.5588 | 0.93252 | 1.0126 | 1.0452 | 1.0447 | 0.72643 | 23.9168 | 24.6872 | 24.6764 | 0.30176 | 29.7087 | 30.6656 | 30.6522
47.5 | 0.5525 | 0.57325 | 0.57125 | 0.91633 | 1.0164 | 1.0546 | 1.0509 | 0.71382 | 24.0077 | 24.9095 | 24.8224 | 0.29652 | 29.8216 | 30.9417 | 30.8336
48 | 0.5636 | 0.58724 | 0.5828 | 0.9004 | 1.0205 | 1.0633 | 1.0553 | 0.70141 | 24.1048 | 25.1158 | 24.926 | 0.29137 | 29.9422 | 31.198 | 30.9623
48.5 | 0.5749 | 0.601 | 0.59345 | 0.88473 | 1.0249 | 1.0714 | 1.058 | 0.6892 | 24.2081 | 25.307 | 24.9892 | 0.2863 | 30.0705 | 31.4355 | 31.0407
49 | 0.5864 | 0.61453 | 0.6032 | 0.86929 | 1.0295 | 1.0789 | 1.059 | 0.67717 | 24.3172 | 25.4839 | 25.0139 | 0.2813 | 30.2061 | 31.6553 | 31.0715
49.5 | 0.5981 | 0.62861 | 0.61205 | 0.85408 | 1.0344 | 1.0872 | 1.0585 | 0.66533 | 24.4322 | 25.6787 | 25.0021 | 0.27638 | 30.3489 | 31.8972 | 31.0567
50 | 0.61 | 0.64283 | 0.62 | 0.8391 | 1.0395 | 1.0954 | 1.0565 | 0.65366 | 24.5528 | 25.8744 | 24.9553 | 0.27153 | 30.4987 | 32.1403 | 30.9987
50.5 | 0.6199 | 0.65704 | 0.6331 | 0.82434 | 1.0411 | 1.1035 | 1.0633 | 0.64216 | 24.5917 | 26.065 | 25.1154 | 0.26676 | 30.5471 | 32.3771 | 31.1975
51 | 0.6296 | 0.67123 | 0.6464 | 0.80978 | 1.0425 | 1.1114 | 1.0703 | 0.63082 | 24.6229 | 26.2508 | 25.2799 | 0.26205 | 30.5858 | 32.6079 | 31.4019
51.5 | 0.6391 | 0.6854 | 0.6599 | 0.79544 | 1.0435 | 1.1191 | 1.0774 | 0.61964 | 24.6468 | 26.4323 | 25.4489 | 0.2574 | 30.6154 | 32.8334 | 31.6118
52 | 0.6484 | 0.69956 | 0.6736 | 0.78129 | 1.0442 | 1.1266 | 1.0848 | 0.60862 | 24.6637 | 26.6097 | 25.6223 | 0.25282 | 30.6365 | 33.0537 | 31.8272
52.5 | 0.6575 | 0.7137 | 0.6875 | 0.76733 | 1.0446 | 1.1339 | 1.0923 | 0.59775 | 24.6742 | 26.7833 | 25.8 | 0.24831 | 30.6494 | 33.2694 | 32.0479
53 | 0.6664 | 0.72783 | 0.7016 | 0.75355 | 1.0448 | 1.1411 | 1.1 | 0.58702 | 24.6784 | 26.9534 | 25.982 | 0.24385 | 30.6548 | 33.4807 | 32.274
53.5 | 0.6751 | 0.7417 | 0.7159 | 0.73996 | 1.0447 | 1.1478 | 1.1079 | 0.57643 | 24.6769 | 27.1112 | 26.1683 | 0.23945 | 30.6528 | 33.6766 | 32.5054
54 | 0.6836 | 0.75533 | 0.7304 | 0.72654 | 1.0444 | 1.154 | 1.116 | 0.56598 | 24.6699 | 27.2584 | 26.3588 | 0.23511 | 30.6441 | 33.8595 | 32.742
54.5 | 0.6919 | 0.76885 | 0.7451 | 0.71329 | 1.0439 | 1.16 | 1.1242 | 0.55566 | 24.6576 | 27.4001 | 26.5535 | 0.23082 | 30.6289 | 34.0355 | 32.9839
55 | 0.7 | 0.78228 | 0.76 | 0.70021 | 1.0432 | 1.1658 | 1.1326 | 0.54546 | 24.6405 | 27.5366 | 26.7525 | 0.22659 | 30.6076 | 34.2051 | 33.2311
55.5 | 0.71175 | 0.79559 | 0.7773 | 0.68728 | 1.0479 | 1.1714 | 1.1445 | 0.53539 | 24.7525 | 27.6684 | 27.0322 | 0.2224 | 30.7468 | 34.3688 | 33.5785
56 | 0.724 | 0.80881 | 0.7952 | 0.67451 | 1.0534 | 1.1768 | 1.157 | 0.52544 | 24.8811 | 27.7956 | 27.328 | 0.21827 | 30.9065 | 34.5268 | 33.946
56.5 | 0.73675 | 0.82191 | 0.8137 | 0.66189 | 1.0595 | 1.182 | 1.1702 | 0.51561 | 25.0257 | 27.9186 | 27.6396 | 0.21419 | 31.0862 | 34.6796 | 34.333
57 | 0.75 | 0.83492 | 0.8328 | 0.64941 | 1.0663 | 1.187 | 1.184 | 0.50589 | 25.186 | 28.0376 | 27.9665 | 0.21015 | 31.2852 | 34.8274 | 34.7391
57.5 | 0.76375 | 0.84776 | 0.8525 | 0.63707 | 1.0737 | 1.1918 | 1.1985 | 0.49628 | 25.3614 | 28.151 | 28.3084 | 0.20616 | 31.5031 | 34.9683 | 35.1638
58 | 0.778 | 0.8604 | 0.8728 | 0.62487 | 1.0818 | 1.1964 | 1.2136 | 0.48677 | 25.5516 | 28.258 | 28.6651 | 0.20221 | 31.7394 | 35.1011 | 35.6069
58.5 | 0.79275 | 0.87291 | 0.8937 | 0.6128 | 1.0904 | 1.2007 | 1.2293 | 0.47737 | 25.7564 | 28.3608 | 29.0362 | 0.1983 | 31.9937 | 35.2289 | 36.0679
59 | 0.808 | 0.88529 | 0.9152 | 0.60086 | 1.0997 | 1.2049 | 1.2456 | 0.46807 | 25.9753 | 28.4599 | 29.4215 | 0.19444 | 32.2656 | 35.3519 | 36.5464
59.5 | 0.82375 | 0.89753 | 0.9373 | 0.58905 | 1.1096 | 1.2089 | 1.2625 | 0.45887 | 26.208 | 28.5553 | 29.8207 | 0.19061 | 32.5548 | 35.4705 | 37.0423
60 | 0.84 | 0.90963 | 0.96 | 0.57735 | 1.12 | 1.2128 | 1.28 | 0.44976 | 26.4544 | 28.6474 | 30.2336 | 0.18683 | 32.8608 | 35.5849 | 37.5552
60.5 | 0.8518 | 0.92161 | 0.9767 | 0.56577 | 1.1245 | 1.2166 | 1.2893 | 0.44074 | 26.5597 | 28.7364 | 30.4542 | 0.18308 | 32.9917 | 35.6954 | 37.8293
61 | 0.8632 | 0.93344 | 0.9928 | 0.55431 | 1.1284 | 1.2203 | 1.2978 | 0.43181 | 26.6534 | 28.8224 | 30.6551 | 0.17937 | 33.108 | 35.8022 | 38.0788
61.5 | 0.8742 | 0.94511 | 1.0083 | 0.54296 | 1.1319 | 1.2237 | 1.3055 | 0.42296 | 26.7358 | 28.9046 | 30.837 | 0.1757 | 33.2104 | 35.9043 | 38.3048
62 | 0.8848 | 0.95654 | 1.0232 | 0.53171 | 1.1349 | 1.227 | 1.3125 | 0.4142 | 26.8074 | 28.9809 | 31.0006 | 0.17206 | 33.2993 | 35.9991 | 38.508
62.5 | 0.895 | 0.96779 | 1.0375 | 0.52057 | 1.1375 | 1.2301 | 1.3187 | 0.40552 | 26.8686 | 29.054 | 31.1466 | 0.16846 | 33.3753 | 36.0899 | 38.6893
63 | 0.9048 | 0.97889 | 1.0512 | 0.50953 | 1.1397 | 1.233 | 1.3241 | 0.39692 | 26.9197 | 29.124 | 31.2754 | 0.16488 | 33.4388 | 36.1769 | 38.8493
63.5 | 0.9142 | 0.98982 | 1.0643 | 0.49858 | 1.1415 | 1.2359 | 1.3289 | 0.3884 | 26.9612 | 29.1913 | 31.3879 | 0.16134 | 33.4903 | 36.2605 | 38.989
64 | 0.9232 | 1.0006 | 1.0768 | 0.48773 | 1.1428 | 1.2386 | 1.333 | 0.37994 | 26.9933 | 29.2559 | 31.4843 | 0.15783 | 33.5302 | 36.3408 | 39.1088
64.5 | 0.9318 | 1.0112 | 1.0887 | 0.47698 | 1.1438 | 1.2412 | 1.3364 | 0.37156 | 27.0163 | 29.318 | 31.5654 | 0.15435 | 33.5588 | 36.4179 | 39.2095
65 | 0.94 | 1.0216 | 1.1 | 0.46631 | 1.1444 | 1.2438 | 1.3392 | 0.36325 | 27.0306 | 29.3778 | 31.6316 | 0.1509 | 33.5766 | 36.4922 | 39.2917
65.5 | 0.9522 | 1.0319 | 1.1135 | 0.45573 | 1.15 | 1.2462 | 1.3447 | 0.35501 | 27.162 | 29.4351 | 31.7618 | 0.14747 | 33.7398 | 36.5634 | 39.4535
66 | 0.9648 | 1.0419 | 1.1268 | 0.44523 | 1.1561 | 1.2484 | 1.3502 | 0.34683 | 27.3059 | 29.4868 | 31.8909 | 0.14408 | 33.9185 | 36.6275 | 39.6138
66.5 | 0.9778 | 1.0516 | 1.1401 | 0.43481 | 1.1627 | 1.2505 | 1.3556 | 0.33872 | 27.4621 | 29.5357 | 32.019 | 0.14071 | 34.1126 | 36.6883 | 39.773
67 | 0.9912 | 1.0612 | 1.1532 | 0.42447 | 1.1698 | 1.2524 | 1.361 | 0.33067 | 27.6305 | 29.5821 | 32.1464 | 0.13736 | 34.3217 | 36.746 | 39.9312
67.5 | 1.005 | 1.0706 | 1.1663 | 0.41421 | 1.1774 | 1.2543 | 1.3663 | 0.32267 | 27.8109 | 29.6262 | 32.2731 | 0.13404 | 34.5458 | 36.8007 | 40.0886
68 | 1.0192 | 1.0798 | 1.1792 | 0.40403 | 1.1856 | 1.2561 | 1.3717 | 0.31474 | 28.0032 | 29.6679 | 32.3993 | 0.13074 | 34.7847 | 36.8525 | 40.2454
68.5 | 1.0338 | 1.0888 | 1.1921 | 0.39391 | 1.1942 | 1.2577 | 1.377 | 0.30686 | 28.2072 | 29.7076 | 32.5251 | 0.12747 | 35.0381 | 36.9018 | 40.4016
69 | 1.0488 | 1.0976 | 1.2048 | 0.38386 | 1.2033 | 1.2593 | 1.3823 | 0.29903 | 28.4229 | 29.7452 | 32.6506 | 0.12422 | 35.3061 | 36.9485 | 40.5575
69.5 | 1.0642 | 1.1062 | 1.2175 | 0.37388 | 1.213 | 1.2608 | 1.3876 | 0.29126 | 28.6502 | 29.781 | 32.776 | 0.12099 | 35.5884 | 36.9929 | 40.7133
70 | 1.08 | 1.1147 | 1.23 | 0.36397 | 1.2231 | 1.2624 | 1.3929 | 0.28353 | 28.889 | 29.8182 | 32.9013 | 0.11778 | 35.8849 | 37.0392 | 40.869
70.5 | 1.0929 | 1.1231 | 1.2463 | 0.35412 | 1.2299 | 1.264 | 1.4026 | 0.27586 | 29.0514 | 29.8548 | 33.1291 | 0.11459 | 36.0867 | 37.0847 | 41.1519
71 | 1.1056 | 1.1313 | 1.2632 | 0.34433 | 1.2367 | 1.2655 | 1.413 | 0.26823 | 29.2104 | 29.8906 | 33.3743 | 0.11142 | 36.2842 | 37.1292 | 41.4564
71.5 | 1.1181 | 1.1394 | 1.2807 | 0.3346 | 1.2433 | 1.267 | 1.4241 | 0.26065 | 29.3662 | 29.9257 | 33.6368 | 0.10828 | 36.4777 | 37.1727 | 41.7825
72 | 1.1304 | 1.1473 | 1.2988 | 0.32492 | 1.2497 | 1.2684 | 1.4359 | 0.25311 | 29.5188 | 29.96 | 33.9164 | 0.10514 | 36.6674 | 37.2154 | 42.1298
72.5 | 1.1425 | 1.155 | 1.3175 | 0.3153 | 1.2561 | 1.2698 | 1.4485 | 0.24562 | 29.6686 | 29.9938 | 34.213 | 0.10203 | 36.8534 | 37.2573 | 42.4983
73 | 1.1544 | 1.1626 | 1.3368 | 0.30573 | 1.2623 | 1.2713 | 1.4618 | 0.23816 | 29.8156 | 30.0271 | 34.5266 | 0.098934 | 37.036 | 37.2986 | 42.8878
73.5 | 1.1661 | 1.17 | 1.3567 | 0.29621 | 1.2684 | 1.2726 | 1.4757 | 0.23075 | 29.96 | 30.0599 | 34.857 | 0.095855 | 37.2153 | 37.3394 | 43.2982
74 | 1.1776 | 1.1772 | 1.3772 | 0.28675 | 1.2744 | 1.274 | 1.4904 | 0.22337 | 30.1019 | 30.091 | 35.2041 | 0.092791 | 37.3917 | 37.3781 | 43.7294
74.5 | 1.1889 | 1.1842 | 1.3983 | 0.27732 | 1.2803 | 1.2752 | 1.5058 | 0.21604 | 30.2416 | 30.1211 | 35.568 | 0.089742 | 37.5651 | 37.4155 | 44.1814
75 | 1.2 | 1.191 | 1.42 | 0.26795 | 1.2862 | 1.2765 | 1.522 | 0.20873 | 30.379 | 30.1506 | 35.9485 | 0.086708 | 37.7358 | 37.4521 | 44.6541
75.5 | 1.2103 | 1.1976 | 1.4362 | 0.25862 | 1.2913 | 1.2777 | 1.5323 | 0.20146 | 30.5006 | 30.1795 | 36.1932 | 0.083689 | 37.8868 | 37.488 | 44.958
76 | 1.2204 | 1.2041 | 1.452 | 0.24933 | 1.2963 | 1.2789 | 1.5423 | 0.19423 | 30.6178 | 30.208 | 36.4282 | 0.080683 | 38.0324 | 37.5233 | 45.25
76.5 | 1.2302 | 1.2103 | 1.4673 | 0.24008 | 1.3011 | 1.2801 | 1.5518 | 0.18702 | 30.7309 | 30.236 | 36.654 | 0.077689 | 38.1729 | 37.5581 | 45.5304
77 | 1.2396 | 1.2164 | 1.482 | 0.23087 | 1.3057 | 1.2813 | 1.561 | 0.17985 | 30.8399 | 30.2636 | 36.8706 | 0.074709 | 38.3084 | 37.5925 | 45.7995
77.5 | 1.2488 | 1.2224 | 1.4962 | 0.22169 | 1.3101 | 1.2824 | 1.5698 | 0.1727 | 30.9451 | 30.2909 | 37.0784 | 0.07174 | 38.439 | 37.6264 | 46.0576
78 | 1.2576 | 1.2279 | 1.51 | 0.21256 | 1.3144 | 1.2834 | 1.5782 | 0.16558 | 31.0466 | 30.3127 | 37.2776 | 0.068783 | 38.565 | 37.6535 | 46.305
78.5 | 1.2661 | 1.233 | 1.5232 | 0.20345 | 1.3186 | 1.284 | 1.5863 | 0.15849 | 31.1444 | 30.3283 | 37.4684 | 0.065837 | 38.6865 | 37.6728 | 46.5421
79 | 1.2744 | 1.2378 | 1.536 | 0.19438 | 1.3226 | 1.2846 | 1.594 | 0.15142 | 31.2387 | 30.3415 | 37.6511 | 0.062901 | 38.8037 | 37.6893 | 46.769
79.5 | 1.2824 | 1.2424 | 1.5483 | 0.18534 | 1.3264 | 1.285 | 1.6014 | 0.14438 | 31.3296 | 30.3526 | 37.8259 | 0.059976 | 38.9166 | 37.703 | 46.9861
80 | 1.29 | 1.2467 | 1.56 | 0.17633 | 1.3301 | 1.2854 | 1.6085 | 0.13736 | 31.4171 | 30.3614 | 37.9928 | 0.057059 | 39.0254 | 37.714 | 47.1935
80.5 | 1.2974 | 1.2507 | 1.5735 | 0.16734 | 1.3337 | 1.2857 | 1.6175 | 0.13036 | 31.5015 | 30.3682 | 38.2056 | 0.054152 | 39.1302 | 37.7224 | 47.4578
81 | 1.3044 | 1.2544 | 1.5868 | 0.15838 | 1.3371 | 1.2859 | 1.6266 | 0.12338 | 31.5828 | 30.3728 | 38.4204 | 0.051253 | 39.2312 | 37.7282 | 47.7246
81.5 | 1.3112 | 1.2579 | 1.6001 | 0.14945 | 1.3404 | 1.286 | 1.6358 | 0.11642 | 31.6611 | 30.3755 | 38.6373 | 0.048362 | 39.3284 | 37.7315 | 47.994
82 | 1.3176 | 1.2612 | 1.6132 | 0.14054 | 1.3436 | 1.2861 | 1.6451 | 0.10948 | 31.7364 | 30.3784 | 38.8564 | 0.045479 | 39.422 | 37.735 | 48.2662
82.5 | 1.3237 | 1.2645 | 1.6262 | 0.13165 | 1.3467 | 1.2864 | 1.6544 | 0.10256 | 31.8089 | 30.3842 | 39.0778 | 0.042603 | 39.512 | 37.7423 | 48.5412
83 | 1.3296 | 1.2675 | 1.6392 | 0.12278 | 1.3496 | 1.2866 | 1.6639 | 0.095649 | 31.8786 | 30.3896 | 39.3016 | 0.039733 | 39.5986 | 37.7489 | 48.8192
83.5 | 1.3352 | 1.2703 | 1.6521 | 0.11394 | 1.3525 | 1.2868 | 1.6735 | 0.088756 | 31.9456 | 30.3944 | 39.528 | 0.03687 | 39.6818 | 37.755 | 49.1004
84 | 1.3404 | 1.2729 | 1.6648 | 0.1051 | 1.3552 | 1.287 | 1.6832 | 0.081876 | 32.01 | 30.3988 | 39.757 | 0.034012 | 39.7618 | 37.7604 | 49.3848
84.5 | 1.3453 | 1.2753 | 1.6774 | 0.096289 | 1.3578 | 1.2872 | 1.693 | 0.075009 | 32.0718 | 30.4028 | 39.9887 | 0.031159 | 39.8385 | 37.7654 | 49.6727
85 | 1.35 | 1.2775 | 1.69 | 0.087489 | 1.3603 | 1.2873 | 1.7029 | 0.068154 | 32.1311 | 30.4064 | 40.2233 | 0.028311 | 39.9122 | 37.7698 | 49.9641
85.5 | 1.3544 | 1.2795 | 1.703 | 0.078702 | 1.3627 | 1.2874 | 1.7135 | 0.061309 | 32.1879 | 30.4095 | 40.474 | 0.025468 | 39.9828 | 37.7737 | 50.2755
86 | 1.3584 | 1.2813 | 1.716 | 0.069927 | 1.365 | 1.2876 | 1.7244 | 0.054473 | 32.2423 | 30.4123 | 40.7301 | 0.022628 | 40.0503 | 37.7772 | 50.5936
86.5 | 1.3622 | 1.2829 | 1.729 | 0.061163 | 1.3672 | 1.2877 | 1.7355 | 0.047646 | 32.2943 | 30.4148 | 40.9918 | 0.019792 | 40.115 | 37.7802 | 50.9186
87 | 1.3656 | 1.2842 | 1.742 | 0.052408 | 1.3694 | 1.2878 | 1.7468 | 0.040826 | 32.3441 | 30.4168 | 41.2591 | 0.016959 | 40.1768 | 37.7828 | 51.2507
87.5 | 1.3687 | 1.2854 | 1.755 | 0.043661 | 1.3714 | 1.2878 | 1.7583 | 0.034012 | 32.3915 | 30.4186 | 41.5321 | 0.014129 | 40.2357 | 37.785 | 51.5899
88 | 1.3716 | 1.2863 | 1.768 | 0.034921 | 1.3733 | 1.2879 | 1.7702 | 0.027203 | 32.4367 | 30.42 | 41.8111 | 0.0113 | 40.2918 | 37.7868 | 51.9364
88.5 | 1.3741 | 1.2871 | 1.781 | 0.026186 | 1.3751 | 1.2879 | 1.7822 | 0.020399 | 32.4797 | 30.4211 | 42.0961 | 0.0084738 | 40.3452 | 37.7881 | 52.2904
89 | 1.3764 | 1.2876 | 1.794 | 0.017455 | 1.3768 | 1.288 | 1.7945 | 0.013597 | 32.5205 | 30.4219 | 42.3872 | 0.0056485 | 40.3959 | 37.7891 | 52.652
89.5 | 1.3783 | 1.2879 | 1.807 | 0.0087269 | 1.3785 | 1.288 | 1.8071 | 0.0067982 | 32.5591 | 30.4224 | 42.6846 | 0.002824 | 40.4439 | 37.7897 | 53.0214
90 | 1.38 | 1.288 | 1.82 | 6.1257e-17 | 1.38 | 1.288 | 1.82 | 4.772e-17 | 32.5956 | 30.4226 | 42.9884 | 1.9823e-17 | 40.4892 | 37.7899 | 53.3988

## Check Valve Transient (Ns=0.79)
Transient conditions at Check Valve
| Exit Pressure (m H20 std) |  | Inlet Pressure (m H20 std) |  | Velocity (m/s)
Time (s) | 4QBEP | 4QOP | 4QBEP | 4QOP | 4QBEP | 4QOP | Times
0 | 106.4871 | 104.0439 | 106.7043 | 104.2289 | 1.3947 | 1.2872 | 7 | -10
0.0041667 | 106.4871 | 104.0439 | 106.7043 | 104.2289 | 1.3947 | 1.2872 | 7 | 200
0.0083333 | 106.491 | 104.0479 | 106.7082 | 104.2329 | 1.3947 | 1.2872
0.0125 | 106.491 | 104.0479 | 106.7082 | 104.2329 | 1.3947 | 1.2872 | 10 | -10
0.016667 | 106.4911 | 104.0483 | 106.7083 | 104.2333 | 1.3947 | 1.2872 | 10 | 200
0.020833 | 106.4911 | 104.0483 | 106.7083 | 104.2333 | 1.3947 | 1.2872
0.025 | 106.4873 | 104.0449 | 106.7045 | 104.2299 | 1.3946 | 1.2872 | 11.9 | -10
0.029167 | 106.4873 | 104.0452 | 106.7045 | 104.2302 | 1.3946 | 1.2872 | 11.9 | 200
0.033333 | 106.4869 | 104.0445 | 106.7041 | 104.2295 | 1.3946 | 1.2872
0.0375 | 106.4869 | 104.0449 | 106.7041 | 104.2299 | 1.3946 | 1.2872
0.041667 | 106.4869 | 104.0446 | 106.7041 | 104.2296 | 1.3946 | 1.2872 | Atmosphere
0.045833 | 106.4869 | 104.0447 | 106.7041 | 104.2297 | 1.3946 | 1.2872 | 0 | 10.3326
0.05 | 106.4873 | 104.045 | 106.7045 | 104.23 | 1.3946 | 1.2872 | 30 | 10.3326
0.054167 | 106.4873 | 104.0449 | 106.7045 | 104.23 | 1.3946 | 1.2872
0.058333 | 106.4874 | 104.045 | 106.7046 | 104.23 | 1.3946 | 1.2872
0.0625 | 106.4874 | 104.0449 | 106.7046 | 104.2299 | 1.3946 | 1.2872
0.066667 | 106.4874 | 104.045 | 106.7046 | 104.23 | 1.3946 | 1.2872
0.070833 | 106.4874 | 104.045 | 106.7046 | 104.23 | 1.3946 | 1.2872
0.075 | 106.4873 | 104.045 | 106.7045 | 104.23 | 1.3946 | 1.2872
0.079167 | 106.4873 | 104.045 | 106.7045 | 104.23 | 1.3946 | 1.2872
0.083333 | 106.4873 | 104.045 | 106.7045 | 104.23 | 1.3946 | 1.2872
0.0875 | 106.4873 | 104.045 | 106.7045 | 104.23 | 1.3946 | 1.2872
0.091667 | 106.4873 | 104.045 | 106.7045 | 104.23 | 1.3946 | 1.2872
0.095833 | 106.0781 | 103.6685 | 106.2963 | 103.8544 | 1.398 | 1.2902
0.1 | 105.7008 | 103.3238 | 105.92 | 103.5105 | 1.401 | 1.293
0.10417 | 105.4336 | 103.0314 | 105.6534 | 103.2185 | 1.4031 | 1.2945
0.10833 | 105.1813 | 102.7595 | 105.4017 | 102.947 | 1.4051 | 1.2959
0.1125 | 105.2345 | 102.6818 | 105.4568 | 102.8707 | 1.411 | 1.3004
0.11667 | 105.2559 | 102.5844 | 105.48 | 102.7745 | 1.4167 | 1.3047
0.12083 | 105.4013 | 102.5727 | 105.6263 | 102.7632 | 1.4194 | 1.3062
0.125 | 105.5185 | 102.542 | 105.7443 | 102.733 | 1.4221 | 1.3078
0.12917 | 105.8501 | 102.7367 | 106.0768 | 102.9282 | 1.4246 | 1.3093
0.13333 | 106.1675 | 102.9229 | 106.395 | 103.1148 | 1.4272 | 1.3111
0.1375 | 106.2304 | 102.9361 | 106.4581 | 103.1282 | 1.4281 | 1.3116
0.14167 | 106.3119 | 102.966 | 106.54 | 103.1583 | 1.429 | 1.3122
0.14583 | 106.2537 | 102.9123 | 106.4818 | 103.1046 | 1.4293 | 1.3124
0.15 | 106.2145 | 102.8759 | 106.4427 | 103.0683 | 1.4296 | 1.3127
0.15417 | 106.1278 | 102.7926 | 106.3564 | 102.9853 | 1.4306 | 1.3136
0.15833 | 106.0423 | 102.713 | 106.2711 | 102.9059 | 1.4316 | 1.3144
0.1625 | 106.0387 | 102.6934 | 106.2678 | 102.8865 | 1.4322 | 1.3148
0.16667 | 106.027 | 102.6624 | 106.2563 | 102.8556 | 1.4329 | 1.3152
0.17083 | 106.1507 | 102.7455 | 106.3802 | 102.9388 | 1.4335 | 1.3156
0.175 | 106.2561 | 102.8075 | 106.4858 | 103.0009 | 1.4343 | 1.316
0.17917 | 106.2273 | 102.7631 | 106.4573 | 102.9566 | 1.4351 | 1.3166
0.18333 | 106.2101 | 102.7324 | 106.4404 | 102.9261 | 1.436 | 1.3173
0.1875 | 106.1134 | 102.6397 | 106.3438 | 102.8336 | 1.4364 | 1.3176
0.19167 | 106.0375 | 102.5698 | 106.268 | 102.7638 | 1.4368 | 1.3179
0.19583 | 106.0791 | 102.5897 | 106.3098 | 102.7838 | 1.4376 | 1.3184
0.2 | 106.1094 | 102.5973 | 106.3404 | 102.7915 | 1.4383 | 1.3188
0.20417 | 106.1404 | 102.6003 | 106.3717 | 102.7948 | 1.4391 | 1.3194
0.20833 | 106.1583 | 102.5914 | 106.3898 | 102.786 | 1.44 | 1.32
0.2125 | 106.1344 | 102.5549 | 106.3662 | 102.7496 | 1.4405 | 1.3204
0.21667 | 106.1163 | 102.5244 | 106.3482 | 102.7192 | 1.4411 | 1.3207
0.22083 | 106.1146 | 102.5115 | 106.3467 | 102.7064 | 1.4417 | 1.3212
0.225 | 106.122 | 102.5055 | 106.3543 | 102.7006 | 1.4423 | 1.3216
0.22917 | 106.1162 | 102.4843 | 106.3487 | 102.6795 | 1.443 | 1.3221
0.23333 | 106.1104 | 102.4641 | 106.3432 | 102.6595 | 1.4437 | 1.3226
0.2375 | 106.1066 | 102.4429 | 106.3395 | 102.6383 | 1.4443 | 1.323
0.24167 | 106.0977 | 102.4191 | 106.3309 | 102.6147 | 1.4449 | 1.3233
0.24583 | 106.1081 | 102.4133 | 106.3415 | 102.609 | 1.4455 | 1.3238
0.25 | 106.1169 | 102.4051 | 106.3505 | 102.6009 | 1.4461 | 1.3242
0.25417 | 106.1104 | 102.3848 | 106.3442 | 102.5807 | 1.4468 | 1.3246
0.25833 | 106.106 | 102.3653 | 106.3399 | 102.5613 | 1.4474 | 1.3251
0.2625 | 106.0877 | 102.3327 | 106.3218 | 102.5289 | 1.4481 | 1.3256
0.26667 | 106.0711 | 102.3022 | 106.3055 | 102.4985 | 1.4488 | 1.326
0.27083 | 106.0795 | 102.2922 | 106.314 | 102.4887 | 1.4494 | 1.3264
0.275 | 106.0873 | 102.2812 | 106.3221 | 102.4778 | 1.45 | 1.3268
0.27917 | 106.0934 | 102.2804 | 106.3284 | 102.4772 | 1.4507 | 1.3272
0.28333 | 106.0981 | 102.2766 | 106.3334 | 102.4734 | 1.4514 | 1.3277
0.2875 | 105.973 | 102.1661 | 106.2088 | 102.3632 | 1.453 | 1.3288
0.29167 | 105.8568 | 102.0643 | 106.093 | 102.2618 | 1.4544 | 1.3298
0.29583 | 105.8458 | 102.0308 | 106.0822 | 102.2284 | 1.4552 | 1.3301
0.3 | 105.8358 | 101.9953 | 106.0725 | 102.193 | 1.4559 | 1.3304
0.30417 | 105.8888 | 102.0225 | 106.1262 | 102.2205 | 1.458 | 1.3316
0.30833 | 105.933 | 102.0332 | 106.171 | 102.2315 | 1.46 | 1.3327
0.3125 | 105.7382 | 101.8783 | 105.977 | 102.077 | 1.4623 | 1.3341
0.31667 | 105.5556 | 101.7322 | 105.7951 | 101.9313 | 1.4646 | 1.3354
0.32083 | 105.4427 | 101.6487 | 105.6831 | 101.8481 | 1.467 | 1.3364
0.325 | 105.3447 | 101.5726 | 105.5858 | 101.7723 | 1.4694 | 1.3374
0.32917 | 105.3409 | 101.5138 | 105.5832 | 101.7142 | 1.4732 | 1.3395
0.33333 | 105.3336 | 101.4424 | 105.5772 | 101.6434 | 1.4769 | 1.3415
0.3375 | 105.4611 | 101.4359 | 105.7054 | 101.6371 | 1.4791 | 1.3422
0.34167 | 105.5714 | 101.4157 | 105.8164 | 101.6171 | 1.4812 | 1.343
0.34583 | 105.7825 | 101.4879 | 106.0282 | 101.6896 | 1.4832 | 1.344
0.35 | 105.9808 | 101.5546 | 106.2271 | 101.7567 | 1.4853 | 1.3452
0.35417 | 106.0247 | 101.5436 | 106.2713 | 101.7458 | 1.486 | 1.3455
0.35833 | 106.0756 | 101.5449 | 106.3224 | 101.7472 | 1.4867 | 1.3459
0.3625 | 106.0239 | 101.5148 | 106.271 | 101.7172 | 1.4874 | 1.3463
0.36667 | 105.9801 | 101.5006 | 106.2274 | 101.7032 | 1.4881 | 1.3468
0.37083 | 105.848 | 101.4052 | 106.0958 | 101.608 | 1.4895 | 1.3477
0.375 | 105.7222 | 101.3226 | 105.9704 | 101.5257 | 1.4908 | 1.3485
0.37917 | 105.6906 | 101.2762 | 105.9392 | 101.4794 | 1.4921 | 1.3492
0.38333 | 105.656 | 101.2197 | 105.905 | 101.4232 | 1.4934 | 1.3499
0.3875 | 105.7894 | 101.2787 | 106.0388 | 101.4823 | 1.4947 | 1.3504
0.39167 | 105.9042 | 101.309 | 106.1541 | 101.5128 | 1.496 | 1.3511
0.39583 | 105.9321 | 101.2948 | 106.1825 | 101.4989 | 1.4973 | 1.3517
0.4 | 105.963 | 101.2877 | 106.2138 | 101.4919 | 1.4985 | 1.3525
0.40417 | 105.8795 | 101.212 | 106.1306 | 101.4164 | 1.4994 | 1.3529
0.40833 | 105.8144 | 101.1602 | 106.0657 | 101.3648 | 1.5003 | 1.3535
0.4125 | 105.8052 | 101.142 | 106.0569 | 101.3467 | 1.5013 | 1.3541
0.41667 | 105.7956 | 101.1222 | 106.0476 | 101.3271 | 1.5024 | 1.3546
0.42083 | 105.8235 | 101.1163 | 106.076 | 101.3214 | 1.5036 | 1.3553
0.425 | 105.8387 | 101.0983 | 106.0916 | 101.3036 | 1.5048 | 1.356
0.42917 | 105.8449 | 101.0767 | 106.0981 | 101.2822 | 1.5059 | 1.3565
0.43333 | 105.8483 | 101.0523 | 106.1019 | 101.258 | 1.5069 | 1.3571
0.4375 | 105.8462 | 101.0338 | 106.1001 | 101.2396 | 1.5079 | 1.3576
0.44167 | 105.8521 | 101.0206 | 106.1064 | 101.2265 | 1.5089 | 1.3581
0.44583 | 105.838 | 100.9932 | 106.0926 | 101.1994 | 1.5099 | 1.3587
0.45 | 105.828 | 100.971 | 106.083 | 101.1774 | 1.511 | 1.3593
0.45417 | 105.8147 | 100.9402 | 106.07 | 101.1468 | 1.512 | 1.3599
0.45833 | 105.798 | 100.9088 | 106.0536 | 101.1155 | 1.5131 | 1.3605
0.4625 | 105.8106 | 100.8979 | 106.0666 | 101.1048 | 1.5141 | 1.361
0.46667 | 105.8193 | 100.8825 | 106.0757 | 101.0895 | 1.5151 | 1.3615
0.47083 | 105.8222 | 100.8721 | 106.0789 | 101.0793 | 1.5161 | 1.3621
0.475 | 105.8245 | 100.8613 | 106.0815 | 101.0686 | 1.5172 | 1.3626
0.47917 | 105.7629 | 100.8005 | 106.0204 | 101.008 | 1.5186 | 1.3634
0.48333 | 105.7068 | 100.7459 | 105.9648 | 100.9538 | 1.5199 | 1.3642
0.4875 | 105.7129 | 100.7281 | 105.9711 | 100.936 | 1.5209 | 1.3646
0.49167 | 105.7199 | 100.708 | 105.9785 | 100.9161 | 1.5218 | 1.365
0.49583 | 105.7484 | 100.7231 | 106.0076 | 100.9314 | 1.5234 | 1.3657
0.5 | 105.77 | 100.7333 | 106.0296 | 100.9418 | 1.5249 | 1.3664
0.50417 | 105.6266 | 100.6278 | 105.8869 | 100.8367 | 1.5269 | 1.3674
0.50833 | 105.4888 | 100.5347 | 105.7498 | 100.7438 | 1.5288 | 1.3684
0.5125 | 105.4544 | 100.5016 | 105.7159 | 100.7108 | 1.5303 | 1.3689
0.51667 | 105.426 | 100.4681 | 105.688 | 100.6774 | 1.5318 | 1.3693
0.52083 | 105.4729 | 100.4763 | 105.7359 | 100.6861 | 1.5345 | 1.3705
0.525 | 105.5129 | 100.4715 | 105.7767 | 100.6816 | 1.5371 | 1.3717
0.52917 | 105.4482 | 100.4013 | 105.7128 | 100.6116 | 1.5393 | 1.3725
0.53333 | 105.3817 | 100.334 | 105.647 | 100.5446 | 1.5415 | 1.3732
0.5375 | 105.3485 | 100.3116 | 105.6147 | 100.5225 | 1.5439 | 1.3741
0.54167 | 105.3222 | 100.2946 | 105.5892 | 100.5057 | 1.5463 | 1.3749
0.54583 | 105.3002 | 100.244 | 105.5682 | 100.4555 | 1.549 | 1.376
0.55 | 105.2841 | 100.1912 | 105.5529 | 100.403 | 1.5517 | 1.3772
0.55417 | 105.3807 | 100.1908 | 105.6502 | 100.4027 | 1.5534 | 1.3776
0.55833 | 105.4705 | 100.1797 | 105.7406 | 100.3918 | 1.5552 | 1.3781
0.5625 | 105.5965 | 100.1932 | 105.8672 | 100.4056 | 1.5569 | 1.3791
0.56667 | 105.715 | 100.2018 | 105.9863 | 100.4145 | 1.5586 | 1.38
0.57083 | 105.7424 | 100.1824 | 106.0139 | 100.3951 | 1.5593 | 1.3802
0.575 | 105.7723 | 100.1687 | 106.044 | 100.3815 | 1.5599 | 1.3806
0.57917 | 105.7398 | 100.1647 | 106.0119 | 100.3777 | 1.5609 | 1.3811
0.58333 | 105.7066 | 100.1668 | 105.979 | 100.38 | 1.5618 | 1.3817
0.5875 | 105.5638 | 100.0901 | 105.8367 | 100.3036 | 1.5634 | 1.3824
0.59167 | 105.4266 | 100.029 | 105.7001 | 100.2426 | 1.5649 | 1.3831
0.59583 | 105.3632 | 99.9746 | 105.6372 | 100.1885 | 1.5665 | 1.3838
0.6 | 105.3041 | 99.9187 | 105.5787 | 100.1327 | 1.5681 | 1.3844
0.60417 | 105.4234 | 99.9508 | 105.6986 | 100.1651 | 1.5697 | 1.385
0.60833 | 105.5305 | 99.9576 | 105.8062 | 100.172 | 1.5714 | 1.3856
0.6125 | 105.6049 | 99.9615 | 105.8811 | 100.1761 | 1.5728 | 1.3863
0.61667 | 105.6751 | 99.9626 | 105.9518 | 100.1774 | 1.5742 | 1.3869
0.62083 | 105.6181 | 99.9127 | 105.8952 | 100.1276 | 1.5752 | 1.3874
0.625 | 105.5731 | 99.8806 | 105.8506 | 100.0957 | 1.5763 | 1.3879
0.62917 | 105.5212 | 99.8482 | 105.7991 | 100.0635 | 1.5774 | 1.3885
0.63333 | 105.4758 | 99.8233 | 105.754 | 100.0387 | 1.5786 | 1.389
0.6375 | 105.4748 | 99.8064 | 105.7536 | 100.022 | 1.58 | 1.3897
0.64167 | 105.4657 | 99.7825 | 105.7449 | 99.9984 | 1.5814 | 1.3903
0.64583 | 105.4845 | 99.7671 | 105.7642 | 99.9831 | 1.5828 | 1.3909
0.65 | 105.4962 | 99.7442 | 105.7764 | 99.9604 | 1.5841 | 1.3915
0.65417 | 105.51 | 99.7318 | 105.7906 | 99.9481 | 1.5853 | 1.392
0.65833 | 105.5278 | 99.7198 | 105.8089 | 99.9363 | 1.5865 | 1.3925
0.6625 | 105.5127 | 99.6993 | 105.7942 | 99.916 | 1.5878 | 1.3931
0.66667 | 105.503 | 99.6846 | 105.7849 | 99.9015 | 1.589 | 1.3936
0.67083 | 105.4592 | 99.642 | 105.7417 | 99.859 | 1.5904 | 1.3943
0.675 | 105.4165 | 99.6034 | 105.6994 | 99.8207 | 1.5917 | 1.3949
0.67917 | 105.4272 | 99.5904 | 105.7105 | 99.8078 | 1.5929 | 1.3954
0.68333 | 105.4335 | 99.5724 | 105.7173 | 99.79 | 1.5941 | 1.3959
0.6875 | 105.4519 | 99.5773 | 105.7362 | 99.795 | 1.5956 | 1.3964
0.69167 | 105.4648 | 99.5787 | 105.7497 | 99.7966 | 1.5971 | 1.397
0.69583 | 105.3672 | 99.5061 | 105.6527 | 99.7243 | 1.5989 | 1.3979
0.7 | 105.2757 | 99.4424 | 105.5618 | 99.6608 | 1.6007 | 1.3987
0.70417 | 105.2633 | 99.4181 | 105.5499 | 99.6367 | 1.602 | 1.3991
0.70833 | 105.2558 | 99.3927 | 105.5428 | 99.6115 | 1.6033 | 1.3995
0.7125 | 105.2895 | 99.4036 | 105.5773 | 99.6226 | 1.6055 | 1.4004
0.71667 | 105.3152 | 99.4079 | 105.6038 | 99.6271 | 1.6077 | 1.4012
0.72083 | 105.2024 | 99.3278 | 105.4918 | 99.5474 | 1.6099 | 1.4021
0.725 | 105.0897 | 99.2564 | 105.3799 | 99.4762 | 1.6121 | 1.4029
0.72917 | 105.0551 | 99.2354 | 105.3461 | 99.4554 | 1.6141 | 1.4035
0.73333 | 105.027 | 99.2162 | 105.3187 | 99.4364 | 1.6162 | 1.404
0.7375 | 105.051 | 99.202 | 105.3437 | 99.4225 | 1.6189 | 1.4051
0.74167 | 105.0738 | 99.1804 | 105.3674 | 99.4012 | 1.6217 | 1.4062
0.74583 | 105.0893 | 99.1524 | 105.3838 | 99.3733 | 1.6237 | 1.4067
0.75 | 105.0998 | 99.1212 | 105.3949 | 99.3424 | 1.6257 | 1.4072
0.75417 | 105.11 | 99.1129 | 105.406 | 99.3342 | 1.628 | 1.408
0.75833 | 105.122 | 99.1072 | 105.4187 | 99.3288 | 1.6303 | 1.4088
0.7625 | 105.0903 | 99.0601 | 105.3878 | 99.282 | 1.6323 | 1.4095
0.76667 | 105.0662 | 99.016 | 105.3644 | 99.2381 | 1.6342 | 1.4103
0.77083 | 105.1279 | 99.0201 | 105.4267 | 99.2423 | 1.6358 | 1.4107
0.775 | 105.186 | 99.0178 | 105.4854 | 99.2402 | 1.6373 | 1.4112
0.77917 | 105.237 | 98.9989 | 105.5369 | 99.2216 | 1.639 | 1.4121
0.78333 | 105.2836 | 98.9799 | 105.5842 | 99.2028 | 1.6406 | 1.4129
0.7875 | 105.2918 | 98.9548 | 105.5927 | 99.1778 | 1.6415 | 1.4132
0.79167 | 105.3018 | 98.932 | 105.603 | 99.1551 | 1.6424 | 1.4136
0.79583 | 105.2664 | 98.9185 | 105.5682 | 99.1419 | 1.6438 | 1.4143
0.8 | 105.2279 | 98.9029 | 105.5302 | 99.1265 | 1.6453 | 1.4151
0.80417 | 105.0864 | 98.833 | 105.3894 | 99.0569 | 1.6472 | 1.4159
0.80833 | 104.9493 | 98.7745 | 105.253 | 98.9985 | 1.649 | 1.4165
0.8125 | 104.8472 | 98.701 | 105.1518 | 98.9254 | 1.6515 | 1.4176
0.81667 | 104.7525 | 98.6332 | 105.0579 | 98.8579 | 1.6539 | 1.4187
0.82083 | 104.827 | 98.6206 | 105.1333 | 98.8456 | 1.6561 | 1.4195
0.825 | 104.8947 | 98.5945 | 105.2018 | 98.8197 | 1.6583 | 1.4203
0.82917 | 105.0071 | 98.6001 | 105.315 | 98.8257 | 1.6604 | 1.4213
0.83333 | 105.1111 | 98.5987 | 105.4198 | 98.8246 | 1.6625 | 1.4223
0.8375 | 105.0975 | 98.5665 | 105.4067 | 98.7927 | 1.6641 | 1.423
0.84167 | 105.0898 | 98.5425 | 105.3996 | 98.7689 | 1.6656 | 1.4237
0.84583 | 105.0232 | 98.5088 | 105.3336 | 98.7354 | 1.6672 | 1.4245
0.85 | 104.9664 | 98.484 | 105.2774 | 98.7109 | 1.6688 | 1.4253
0.85417 | 104.9274 | 98.4543 | 105.2391 | 98.6814 | 1.6707 | 1.4261
0.85833 | 104.8849 | 98.4237 | 105.1973 | 98.6511 | 1.6725 | 1.4268
0.8625 | 104.891 | 98.3966 | 105.2041 | 98.6243 | 1.6744 | 1.4276
0.86667 | 104.8884 | 98.3639 | 105.2022 | 98.5917 | 1.6764 | 1.4285
0.87083 | 104.9246 | 98.3505 | 105.2391 | 98.5786 | 1.6781 | 1.4291
0.875 | 104.9599 | 98.3337 | 105.2749 | 98.562 | 1.6797 | 1.4298
0.87917 | 104.9615 | 98.3227 | 105.2773 | 98.5513 | 1.6815 | 1.4305
0.88333 | 104.9676 | 98.3149 | 105.2839 | 98.5437 | 1.6832 | 1.4312
0.8875 | 104.887 | 98.2586 | 105.2041 | 98.4876 | 1.6851 | 1.4321
0.89167 | 104.8124 | 98.2098 | 105.1302 | 98.4391 | 1.687 | 1.4329
0.89583 | 104.8152 | 98.1941 | 105.1336 | 98.4236 | 1.6885 | 1.4334
0.9 | 104.8152 | 98.1756 | 105.1342 | 98.4052 | 1.6901 | 1.434
0.90417 | 104.8521 | 98.1891 | 105.1719 | 98.419 | 1.6922 | 1.4347
0.90833 | 104.879 | 98.1969 | 105.1996 | 98.427 | 1.6942 | 1.4355
0.9125 | 104.7849 | 98.135 | 105.1063 | 98.3653 | 1.6964 | 1.4363
0.91667 | 104.6945 | 98.0794 | 105.0167 | 98.31 | 1.6985 | 1.437
0.92083 | 104.677 | 98.063 | 104.9998 | 98.2937 | 1.7002 | 1.4375
0.925 | 104.6665 | 98.0474 | 104.9899 | 98.2783 | 1.702 | 1.4379
0.92917 | 104.6918 | 98.0468 | 105.0162 | 98.2779 | 1.7045 | 1.4388
0.93333 | 104.7118 | 98.0411 | 105.0372 | 98.2725 | 1.7069 | 1.4397
0.9375 | 104.6499 | 97.9907 | 104.9761 | 98.2224 | 1.7091 | 1.4403
0.94167 | 104.5848 | 97.9431 | 104.9119 | 98.175 | 1.7113 | 1.4409
0.94583 | 104.5603 | 97.9316 | 104.8882 | 98.1636 | 1.7136 | 1.4415
0.95 | 104.5395 | 97.9224 | 104.8683 | 98.1546 | 1.7158 | 1.4421
0.95417 | 104.5359 | 97.8924 | 104.8656 | 98.1249 | 1.7183 | 1.443
0.95833 | 104.5349 | 97.8606 | 104.8656 | 98.0934 | 1.7208 | 1.4438
0.9625 | 104.5864 | 97.8543 | 104.9177 | 98.0872 | 1.7226 | 1.4442
0.96667 | 104.6324 | 97.8431 | 104.9645 | 98.0761 | 1.7244 | 1.4446
0.97083 | 104.6549 | 97.8318 | 104.9878 | 98.0651 | 1.7265 | 1.4455
0.975 | 104.677 | 97.8221 | 105.0107 | 98.0556 | 1.7286 | 1.4463
0.97917 | 104.6401 | 97.7813 | 104.9744 | 98.015 | 1.7301 | 1.4467
0.98333 | 104.6115 | 97.744 | 104.9463 | 97.9779 | 1.7317 | 1.4472
0.9875 | 104.6335 | 97.7455 | 104.969 | 97.9796 | 1.7332 | 1.4478
0.99167 | 104.6531 | 97.7426 | 104.9892 | 97.9769 | 1.7348 | 1.4484
0.99583 | 104.6331 | 97.703 | 104.9699 | 97.9375 | 1.7366 | 1.4492
1 | 104.6111 | 97.666 | 104.9486 | 97.9008 | 1.7384 | 1.4499
1.0042 | 104.5857 | 97.6308 | 104.9238 | 97.8657 | 1.7399 | 1.4504
1.0083 | 104.5628 | 97.5981 | 104.9014 | 97.8332 | 1.7413 | 1.451
1.0125 | 104.5412 | 97.5805 | 104.8805 | 97.8159 | 1.7433 | 1.4518
1.0167 | 104.5155 | 97.5584 | 104.8557 | 97.7941 | 1.7453 | 1.4527
1.0208 | 104.4267 | 97.5186 | 104.7676 | 97.7545 | 1.7475 | 1.4534
1.025 | 104.3396 | 97.4834 | 104.6815 | 97.7195 | 1.7496 | 1.4541
1.0292 | 104.2508 | 97.4304 | 104.5937 | 97.6669 | 1.7523 | 1.4551
1.0333 | 104.1681 | 97.3834 | 104.5121 | 97.6202 | 1.7549 | 1.4561
1.0375 | 104.2158 | 97.3649 | 104.5606 | 97.6019 | 1.7572 | 1.4569
1.0417 | 104.2584 | 97.3431 | 104.6041 | 97.5804 | 1.7594 | 1.4576
1.0458 | 104.3702 | 97.3465 | 104.7168 | 97.584 | 1.7616 | 1.4584
1.05 | 104.4712 | 97.3446 | 104.8186 | 97.5824 | 1.7638 | 1.4594
1.0542 | 104.4815 | 97.3238 | 104.8295 | 97.5618 | 1.7653 | 1.46
1.0583 | 104.4951 | 97.304 | 104.8437 | 97.5422 | 1.7669 | 1.4606
1.0625 | 104.4268 | 97.2792 | 104.7761 | 97.5177 | 1.7686 | 1.4613
1.0667 | 104.3718 | 97.2593 | 104.7217 | 97.4979 | 1.7702 | 1.462
1.0708 | 104.3005 | 97.2332 | 104.6512 | 97.4721 | 1.7721 | 1.4626
1.075 | 104.2309 | 97.2086 | 104.5823 | 97.4477 | 1.774 | 1.4633
1.0792 | 104.2019 | 97.1732 | 104.5542 | 97.4125 | 1.7762 | 1.4641
1.0833 | 104.1639 | 97.1366 | 104.5171 | 97.3762 | 1.7784 | 1.4649
1.0875 | 104.2168 | 97.1251 | 104.5707 | 97.3649 | 1.7802 | 1.4655
1.0917 | 104.2615 | 97.1103 | 104.6161 | 97.3502 | 1.782 | 1.466
1.0958 | 104.2976 | 97.1178 | 104.653 | 97.358 | 1.784 | 1.4667
1.1 | 104.3348 | 97.1244 | 104.691 | 97.3649 | 1.786 | 1.4674
1.1042 | 104.235 | 97.0725 | 104.592 | 97.3132 | 1.7879 | 1.4681
1.1083 | 104.1476 | 97.0267 | 104.5054 | 97.2676 | 1.7899 | 1.4688
1.1125 | 104.1292 | 97.0135 | 104.4876 | 97.2546 | 1.7915 | 1.4692
1.1167 | 104.1069 | 97.0006 | 104.4659 | 97.2417 | 1.7931 | 1.4696
1.1208 | 104.1363 | 97.0117 | 104.4962 | 97.2531 | 1.7953 | 1.4704
1.125 | 104.1474 | 97.0177 | 104.5083 | 97.2594 | 1.7975 | 1.4711
1.1292 | 104.0635 | 96.9699 | 104.4252 | 97.2118 | 1.7996 | 1.4717
1.1333 | 103.979 | 96.9241 | 104.3415 | 97.1661 | 1.8016 | 1.4723
1.1375 | 103.9478 | 96.9137 | 104.311 | 97.1559 | 1.8035 | 1.4727
1.1417 | 103.924 | 96.9053 | 104.288 | 97.1477 | 1.8054 | 1.4731
1.1458 | 103.9191 | 96.8909 | 104.284 | 97.1335 | 1.8077 | 1.4739
1.15 | 103.9143 | 96.8747 | 104.2801 | 97.1176 | 1.8101 | 1.4747
1.1542 | 103.8911 | 96.8498 | 104.2578 | 97.0928 | 1.812 | 1.4751
1.1583 | 103.8635 | 96.8239 | 104.231 | 97.067 | 1.8139 | 1.4755
1.1625 | 103.8421 | 96.8167 | 104.2104 | 97.06 | 1.8161 | 1.4761
1.1667 | 103.8218 | 96.8113 | 104.1909 | 97.0549 | 1.8182 | 1.4768
1.1708 | 103.7873 | 96.7759 | 104.1572 | 97.0196 | 1.8202 | 1.4774
1.175 | 103.7577 | 96.7417 | 104.1285 | 96.9855 | 1.8221 | 1.478
1.1792 | 103.8032 | 96.7459 | 104.1746 | 96.99 | 1.8237 | 1.4784
1.1833 | 103.8432 | 96.7461 | 104.2153 | 96.9903 | 1.8253 | 1.4788
1.1875 | 103.8444 | 96.7268 | 104.2172 | 96.9712 | 1.8272 | 1.4795
1.1917 | 103.845 | 96.7085 | 104.2186 | 96.9532 | 1.8291 | 1.4803
1.1958 | 103.7905 | 96.671 | 104.1646 | 96.9158 | 1.8304 | 1.4806
1.2 | 103.7444 | 96.6362 | 104.1191 | 96.8812 | 1.8318 | 1.481
1.2042 | 103.725 | 96.6296 | 104.1004 | 96.8748 | 1.8335 | 1.4817
1.2083 | 103.7043 | 96.6199 | 104.0804 | 96.8653 | 1.8352 | 1.4824
1.2125 | 103.6409 | 96.5802 | 104.0178 | 96.8258 | 1.8372 | 1.4831
1.2167 | 103.5773 | 96.5428 | 103.955 | 96.7887 | 1.8392 | 1.4838
1.2208 | 103.5266 | 96.509 | 103.9051 | 96.7551 | 1.8411 | 1.4844
1.225 | 103.4777 | 96.4783 | 103.8571 | 96.7246 | 1.8431 | 1.4851
1.2292 | 103.4689 | 96.4613 | 103.8491 | 96.7078 | 1.8453 | 1.4859
1.2333 | 103.4553 | 96.442 | 103.8365 | 96.6888 | 1.8474 | 1.4866
1.2375 | 103.4219 | 96.4274 | 103.804 | 96.6745 | 1.8497 | 1.4873
1.2417 | 103.3879 | 96.413 | 103.7709 | 96.6603 | 1.8519 | 1.488
1.2458 | 103.3147 | 96.3773 | 103.6986 | 96.6248 | 1.8543 | 1.4888
1.25 | 103.2474 | 96.3442 | 103.6324 | 96.592 | 1.8568 | 1.4896
1.2542 | 103.2551 | 96.3253 | 103.641 | 96.5733 | 1.8588 | 1.4902
1.2583 | 103.2614 | 96.308 | 103.6481 | 96.5562 | 1.8608 | 1.4908
1.2625 | 103.3341 | 96.3056 | 103.7216 | 96.554 | 1.8628 | 1.4915
1.2667 | 103.3956 | 96.3011 | 103.784 | 96.5498 | 1.8648 | 1.4923
1.2708 | 103.4029 | 96.2825 | 103.7919 | 96.5313 | 1.8663 | 1.4928
1.275 | 103.41 | 96.2625 | 103.7995 | 96.5115 | 1.8679 | 1.4933
1.2792 | 103.3534 | 96.2456 | 103.7437 | 96.4949 | 1.8695 | 1.494
1.2833 | 103.3097 | 96.23 | 103.7007 | 96.4794 | 1.8711 | 1.4946
1.2875 | 103.2268 | 96.216 | 103.6186 | 96.4656 | 1.873 | 1.4951
1.2917 | 103.1526 | 96.2021 | 103.5451 | 96.4518 | 1.8748 | 1.4956
1.2958 | 103.0822 | 96.1641 | 103.4757 | 96.4141 | 1.8771 | 1.4964
1.3 | 103.0083 | 96.1274 | 103.4028 | 96.3778 | 1.8794 | 1.4971
1.3042 | 103.0617 | 96.1174 | 103.4568 | 96.3678 | 1.8811 | 1.4975
1.3083 | 103.0996 | 96.1075 | 103.4954 | 96.3581 | 1.8828 | 1.4979
1.3125 | 103.1622 | 96.1239 | 103.5589 | 96.3746 | 1.8847 | 1.4985
1.3167 | 103.2231 | 96.1377 | 103.6206 | 96.3886 | 1.8867 | 1.4992
1.3208 | 103.1263 | 96.0945 | 103.5245 | 96.3457 | 1.8885 | 1.4998
1.325 | 103.0495 | 96.0528 | 103.4484 | 96.3042 | 1.8902 | 1.5003
1.3292 | 103.0099 | 96.0424 | 103.4095 | 96.2938 | 1.8917 | 1.5006
1.3333 | 102.9741 | 96.0343 | 103.3743 | 96.2859 | 1.8932 | 1.501
1.3375 | 102.9838 | 96.0331 | 103.385 | 96.2849 | 1.8953 | 1.5016
1.3417 | 102.9778 | 96.0295 | 103.3798 | 96.2815 | 1.8974 | 1.5023
1.3458 | 102.9349 | 95.9984 | 103.3378 | 96.2505 | 1.8993 | 1.5027
1.35 | 102.8845 | 95.9661 | 103.2881 | 96.2184 | 1.9011 | 1.5032
1.3542 | 102.8666 | 95.9612 | 103.2709 | 96.2136 | 1.903 | 1.5036
1.3583 | 102.8544 | 95.9583 | 103.2596 | 96.2109 | 1.9049 | 1.5041
1.3625 | 102.8344 | 95.9338 | 103.2405 | 96.1866 | 1.9069 | 1.5047
1.3667 | 102.821 | 95.9097 | 103.228 | 96.1628 | 1.9089 | 1.5053
1.3708 | 102.835 | 95.9025 | 103.2426 | 96.1557 | 1.9105 | 1.5056
1.375 | 102.8448 | 95.8936 | 103.253 | 96.1468 | 1.9121 | 1.5059
1.3792 | 102.8334 | 95.8848 | 103.2425 | 96.1383 | 1.914 | 1.5066
1.3833 | 102.8209 | 95.8768 | 103.2308 | 96.1305 | 1.9159 | 1.5072
1.3875 | 102.7765 | 95.8425 | 103.187 | 96.0963 | 1.9175 | 1.5077
1.3917 | 102.7372 | 95.8096 | 103.1485 | 96.0636 | 1.919 | 1.5081
1.3958 | 102.7684 | 95.8152 | 103.1802 | 96.0693 | 1.9205 | 1.5085
1.4 | 102.7945 | 95.8185 | 103.207 | 96.0728 | 1.922 | 1.5089
1.4042 | 102.7779 | 95.7947 | 103.1912 | 96.0491 | 1.9237 | 1.5096
1.4083 | 102.7614 | 95.7708 | 103.1753 | 96.0255 | 1.9255 | 1.5102
1.4125 | 102.7118 | 95.7434 | 103.1265 | 95.9982 | 1.9269 | 1.5106
1.4167 | 102.6696 | 95.7177 | 103.0848 | 95.9726 | 1.9282 | 1.511
1.4208 | 102.6451 | 95.7087 | 103.0611 | 95.9638 | 1.9301 | 1.5116
1.425 | 102.6199 | 95.6982 | 103.0367 | 95.9536 | 1.9319 | 1.5122
1.4292 | 102.5666 | 95.6739 | 102.9842 | 95.9295 | 1.9338 | 1.5128
1.4333 | 102.5135 | 95.6501 | 102.932 | 95.9058 | 1.9357 | 1.5133
1.4375 | 102.4672 | 95.6253 | 102.8865 | 95.8812 | 1.9377 | 1.5139
1.4417 | 102.4224 | 95.6025 | 102.8425 | 95.8587 | 1.9398 | 1.5146
1.4458 | 102.4279 | 95.5863 | 102.8489 | 95.8427 | 1.9418 | 1.5151
1.45 | 102.4291 | 95.5711 | 102.851 | 95.8277 | 1.9437 | 1.5157
1.4542 | 102.4447 | 95.5697 | 102.8675 | 95.8265 | 1.9457 | 1.5162
1.4583 | 102.4565 | 95.5677 | 102.8801 | 95.8245 | 1.9476 | 1.5168
1.4625 | 102.4107 | 95.543 | 102.8351 | 95.8001 | 1.9496 | 1.5174
1.4667 | 102.3697 | 95.5176 | 102.795 | 95.7749 | 1.9516 | 1.518
1.4708 | 102.358 | 95.5033 | 102.784 | 95.7608 | 1.9532 | 1.5184
1.475 | 102.3496 | 95.4912 | 102.7764 | 95.7488 | 1.9548 | 1.5188
1.4792 | 102.3835 | 95.4869 | 102.811 | 95.7447 | 1.9566 | 1.5194
1.4833 | 102.4108 | 95.4823 | 102.8391 | 95.7403 | 1.9584 | 1.52
1.4875 | 102.4075 | 95.4632 | 102.8364 | 95.7213 | 1.9598 | 1.5204
1.4917 | 102.4017 | 95.4429 | 102.8313 | 95.7011 | 1.9613 | 1.5209
1.4958 | 102.3815 | 95.434 | 102.8117 | 95.6925 | 1.9627 | 1.5213
1.5 | 102.3669 | 95.426 | 102.7977 | 95.6846 | 1.9641 | 1.5218
1.5042 | 102.3143 | 95.4281 | 102.7459 | 95.6868 | 1.9658 | 1.5221
1.5083 | 102.2717 | 95.4284 | 102.704 | 95.6873 | 1.9675 | 1.5225
1.5125 | 102.1843 | 95.3948 | 102.6175 | 95.6539 | 1.9695 | 1.5231
1.5167 | 102.1014 | 95.3613 | 102.5355 | 95.6206 | 1.9715 | 1.5237
1.5208 | 102.148 | 95.3547 | 102.5826 | 95.614 | 1.9729 | 1.5239
1.525 | 102.1792 | 95.3517 | 102.6145 | 95.611 | 1.9743 | 1.5241
1.5292 | 102.2572 | 95.3661 | 102.6933 | 95.6257 | 1.9761 | 1.5246
1.5333 | 102.3251 | 95.3789 | 102.762 | 95.6386 | 1.9779 | 1.5252
1.5375 | 102.2564 | 95.3477 | 102.6939 | 95.6076 | 1.9793 | 1.5255
1.5417 | 102.2019 | 95.3138 | 102.64 | 95.5738 | 1.9807 | 1.5258
1.5458 | 102.1507 | 95.3094 | 102.5894 | 95.5695 | 1.982 | 1.5261
1.55 | 102.1099 | 95.3077 | 102.5492 | 95.5679 | 1.9834 | 1.5264
1.5542 | 102.0903 | 95.2952 | 102.5304 | 95.5556 | 1.9852 | 1.5269
1.5583 | 102.0626 | 95.2824 | 102.5035 | 95.5429 | 1.987 | 1.5274
1.5625 | 102.0594 | 95.2683 | 102.501 | 95.5289 | 1.9886 | 1.5277
1.5667 | 102.0434 | 95.2527 | 102.4857 | 95.5134 | 1.9901 | 1.5279
1.5708 | 102.0431 | 95.2513 | 102.4862 | 95.5121 | 1.9919 | 1.5283
1.575 | 102.0444 | 95.251 | 102.4882 | 95.512 | 1.9936 | 1.5288
1.5792 | 102.0158 | 95.2242 | 102.4604 | 95.4853 | 1.9951 | 1.5292
1.5833 | 101.9978 | 95.1981 | 102.443 | 95.4593 | 1.9967 | 1.5296
1.5875 | 102.0258 | 95.2019 | 102.4716 | 95.4632 | 1.998 | 1.5298
1.5917 | 102.0518 | 95.2051 | 102.4982 | 95.4665 | 1.9993 | 1.5301
1.5958 | 102.0341 | 95.1916 | 102.4812 | 95.4533 | 2.0009 | 1.5306
1.6 | 102.0145 | 95.1774 | 102.4623 | 95.4392 | 2.0026 | 1.5312
1.6042 | 101.9643 | 95.1486 | 102.4127 | 95.4105 | 2.0038 | 1.5314
1.6083 | 101.9178 | 95.1208 | 102.3668 | 95.3828 | 2.0051 | 1.5317
1.6125 | 101.9278 | 95.1219 | 102.3774 | 95.384 | 2.0066 | 1.5322
1.6167 | 101.9337 | 95.1229 | 102.3839 | 95.3852 | 2.0081 | 1.5326
1.6208 | 101.9061 | 95.1003 | 102.3572 | 95.3628 | 2.0098 | 1.5331
1.625 | 101.8793 | 95.077 | 102.3311 | 95.3396 | 2.0114 | 1.5336
1.6292 | 101.84 | 95.0595 | 102.2925 | 95.3223 | 2.0129 | 1.534
1.6333 | 101.8064 | 95.043 | 102.2595 | 95.306 | 2.0144 | 1.5344
1.6375 | 101.7875 | 95.0331 | 102.2414 | 95.2962 | 2.0162 | 1.5349
1.6417 | 101.7682 | 95.0245 | 102.223 | 95.2878 | 2.0179 | 1.5355
1.6458 | 101.7419 | 95.0187 | 102.1975 | 95.2821 | 2.0197 | 1.5359
1.65 | 101.7146 | 95.0134 | 102.1709 | 95.277 | 2.0215 | 1.5363
1.6542 | 101.6752 | 94.9985 | 102.1325 | 95.2623 | 2.0235 | 1.5369
1.6583 | 101.6371 | 94.984 | 102.0952 | 95.248 | 2.0254 | 1.5375
1.6625 | 101.6452 | 94.9743 | 102.104 | 95.2385 | 2.0271 | 1.5379
1.6667 | 101.6513 | 94.9671 | 102.1109 | 95.2313 | 2.0287 | 1.5383
1.6708 | 101.6868 | 94.9747 | 102.1472 | 95.2391 | 2.0304 | 1.5388
1.675 | 101.7173 | 94.9815 | 102.1784 | 95.246 | 2.0321 | 1.5393
1.6792 | 101.6878 | 94.9655 | 102.1496 | 95.2302 | 2.0337 | 1.5397
1.6833 | 101.6608 | 94.9477 | 102.1234 | 95.2125 | 2.0353 | 1.5402
1.6875 | 101.6439 | 94.9419 | 102.1071 | 95.2069 | 2.0367 | 1.5405
1.6917 | 101.6317 | 94.9384 | 102.0955 | 95.2035 | 2.038 | 1.5409
1.6958 | 101.6365 | 94.9406 | 102.101 | 95.2059 | 2.0396 | 1.5413
1.7 | 101.6402 | 94.9419 | 102.1055 | 95.2073 | 2.0411 | 1.5418
1.7042 | 101.6174 | 94.9251 | 102.0833 | 95.1906 | 2.0426 | 1.5422
1.7083 | 101.5932 | 94.9076 | 102.0598 | 95.1734 | 2.044 | 1.5426
1.7125 | 101.5992 | 94.9039 | 102.0663 | 95.1697 | 2.0453 | 1.5429
1.7167 | 101.6032 | 94.903 | 102.0709 | 95.1689 | 2.0465 | 1.5432
1.7208 | 101.586 | 94.9138 | 102.0544 | 95.1799 | 2.0481 | 1.5436
1.725 | 101.574 | 94.9238 | 102.0431 | 95.19 | 2.0496 | 1.5439
1.7292 | 101.4825 | 94.8957 | 101.9524 | 95.1621 | 2.0514 | 1.5444
1.7333 | 101.4 | 94.8661 | 101.8707 | 95.1326 | 2.0531 | 1.5449
1.7375 | 101.4229 | 94.8637 | 101.8942 | 95.1302 | 2.0544 | 1.5451
1.7417 | 101.4373 | 94.8663 | 101.9092 | 95.1329 | 2.0556 | 1.5452
1.7458 | 101.5057 | 94.8751 | 101.9784 | 95.1419 | 2.0573 | 1.5457
1.75 | 101.5617 | 94.8822 | 102.0351 | 95.1492 | 2.059 | 1.5462
1.7542 | 101.5333 | 94.8665 | 102.0072 | 95.1335 | 2.0601 | 1.5465
1.7583 | 101.509 | 94.8463 | 101.9835 | 95.1134 | 2.0613 | 1.5466
1.7625 | 101.4595 | 94.8488 | 101.9346 | 95.116 | 2.0627 | 1.547
1.7667 | 101.4219 | 94.8526 | 101.8976 | 95.1199 | 2.064 | 1.5473
1.7708 | 101.3727 | 94.8337 | 101.8491 | 95.1011 | 2.0656 | 1.5477
1.775 | 101.3249 | 94.8149 | 101.8021 | 95.0825 | 2.0671 | 1.5481
1.7792 | 101.3462 | 94.8146 | 101.824 | 95.0823 | 2.0685 | 1.5483
1.7833 | 101.3545 | 94.8152 | 101.8329 | 95.0829 | 2.0699 | 1.5485
1.7875 | 101.3651 | 94.8147 | 101.8443 | 95.0826 | 2.0715 | 1.549
1.7917 | 101.3728 | 94.8133 | 101.8528 | 95.0814 | 2.0732 | 1.5494
1.7958 | 101.3431 | 94.7902 | 101.8237 | 95.0584 | 2.0744 | 1.5498
1.8 | 101.3237 | 94.7681 | 101.8048 | 95.0364 | 2.0757 | 1.5501
1.8042 | 101.3472 | 94.7774 | 101.8289 | 95.0457 | 2.0769 | 1.5503
1.8083 | 101.3714 | 94.7868 | 101.8536 | 95.0552 | 2.0781 | 1.5506
1.8125 | 101.3446 | 94.7737 | 101.8276 | 95.0424 | 2.0796 | 1.5511
1.8167 | 101.3167 | 94.7582 | 101.8003 | 95.027 | 2.0811 | 1.5516
1.8208 | 101.2704 | 94.7402 | 101.7546 | 95.0091 | 2.0823 | 1.5518
1.825 | 101.2259 | 94.7232 | 101.7106 | 94.9922 | 2.0835 | 1.5521
1.8292 | 101.2238 | 94.7231 | 101.7092 | 94.9922 | 2.085 | 1.5525
1.8333 | 101.2185 | 94.7236 | 101.7046 | 94.9929 | 2.0866 | 1.553
1.8375 | 101.1978 | 94.7106 | 101.6847 | 94.9801 | 2.0881 | 1.5534
1.8417 | 101.1778 | 94.6963 | 101.6654 | 94.9659 | 2.0896 | 1.5538
1.8458 | 101.1484 | 94.6844 | 101.6367 | 94.9542 | 2.0912 | 1.5542
1.85 | 101.1233 | 94.6723 | 101.6124 | 94.9422 | 2.0928 | 1.5547
1.8542 | 101.1122 | 94.6602 | 101.602 | 94.9303 | 2.0944 | 1.5551
1.8583 | 101.1014 | 94.6498 | 101.592 | 94.92 | 2.0959 | 1.5556
1.8625 | 101.1015 | 94.6527 | 101.5928 | 94.9231 | 2.0976 | 1.5559
1.8667 | 101.0989 | 94.6562 | 101.5909 | 94.9267 | 2.0992 | 1.5563
1.8708 | 101.0654 | 94.6417 | 101.5583 | 94.9124 | 2.1009 | 1.5569
1.875 | 101.0325 | 94.6267 | 101.5262 | 94.8976 | 2.1026 | 1.5574
1.8792 | 101.0382 | 94.6198 | 101.5325 | 94.8907 | 2.1039 | 1.5577
1.8833 | 101.0445 | 94.6151 | 101.5395 | 94.8861 | 2.1053 | 1.5579
1.8875 | 101.079 | 94.6222 | 101.5747 | 94.8933 | 2.1068 | 1.5584
1.8917 | 101.11 | 94.6279 | 101.6063 | 94.8993 | 2.1082 | 1.5588
1.8958 | 101.0851 | 94.6115 | 101.582 | 94.8829 | 2.1096 | 1.5592
1.9 | 101.061 | 94.5933 | 101.5585 | 94.8649 | 2.1109 | 1.5595
1.9042 | 101.0484 | 94.589 | 101.5464 | 94.8607 | 2.112 | 1.5599
1.9083 | 101.0382 | 94.587 | 101.5369 | 94.8588 | 2.1132 | 1.5602
1.9125 | 101.0289 | 94.5902 | 101.5282 | 94.8621 | 2.1146 | 1.5605
1.9167 | 101.0211 | 94.5926 | 101.5211 | 94.8646 | 2.116 | 1.5609
1.9208 | 100.9779 | 94.573 | 101.4785 | 94.8452 | 2.1174 | 1.5613
1.925 | 100.9363 | 94.5526 | 101.4377 | 94.825 | 2.1188 | 1.5617
1.9292 | 100.9543 | 94.5494 | 101.4562 | 94.8219 | 2.12 | 1.5619
1.9333 | 100.9678 | 94.5496 | 101.4702 | 94.8221 | 2.1212 | 1.5622
1.9375 | 100.981 | 94.5604 | 101.4841 | 94.833 | 2.1227 | 1.5625
1.9417 | 100.9934 | 94.5702 | 101.4973 | 94.843 | 2.1241 | 1.5629
1.9458 | 100.9192 | 94.5466 | 101.4238 | 94.8195 | 2.1256 | 1.5633
1.95 | 100.8523 | 94.5202 | 101.3576 | 94.7932 | 2.127 | 1.5636
1.9542 | 100.851 | 94.5204 | 101.3568 | 94.7934 | 2.1282 | 1.5638
1.9583 | 100.8493 | 94.5244 | 101.3556 | 94.7975 | 2.1294 | 1.564
1.9625 | 100.888 | 94.5204 | 101.3951 | 94.7937 | 2.131 | 1.5645
1.9667 | 100.9186 | 94.5155 | 101.4265 | 94.789 | 2.1325 | 1.565
1.9708 | 100.9291 | 94.5094 | 101.4374 | 94.783 | 2.1335 | 1.5651
1.975 | 100.9351 | 94.5009 | 101.4439 | 94.7745 | 2.1345 | 1.5652
1.9792 | 100.898 | 94.5036 | 101.4075 | 94.7773 | 2.1359 | 1.5656
1.9833 | 100.8688 | 94.5059 | 101.3788 | 94.7798 | 2.1372 | 1.566
1.9875 | 100.8011 | 94.4813 | 101.3119 | 94.7553 | 2.1385 | 1.5663
1.9917 | 100.7412 | 94.4575 | 101.2525 | 94.7316 | 2.1398 | 1.5666
1.9958 | 100.7679 | 94.4633 | 101.2799 | 94.7375 | 2.1411 | 1.5669
2 | 100.7865 | 94.4708 | 101.299 | 94.7451 | 2.1424 | 1.5671
2.0042 | 100.7989 | 94.4647 | 101.3122 | 94.7391 | 2.1439 | 1.5675
2.0083 | 100.8064 | 94.457 | 101.3204 | 94.7315 | 2.1454 | 1.568
2.0125 | 100.7847 | 94.4381 | 101.2992 | 94.7127 | 2.1465 | 1.5682
2.0167 | 100.7696 | 94.4202 | 101.2847 | 94.6949 | 2.1476 | 1.5685
2.0208 | 100.7827 | 94.4268 | 101.2984 | 94.7016 | 2.1488 | 1.5688
2.025 | 100.7978 | 94.4334 | 101.3139 | 94.7084 | 2.15 | 1.5691
2.0292 | 100.766 | 94.4198 | 101.2828 | 94.6949 | 2.1514 | 1.5695
2.0333 | 100.7337 | 94.4042 | 101.2512 | 94.6794 | 2.1527 | 1.57
2.0375 | 100.6932 | 94.392 | 101.2113 | 94.6674 | 2.1539 | 1.5702
2.0417 | 100.653 | 94.3804 | 101.1716 | 94.6558 | 2.1552 | 1.5705
2.0458 | 100.645 | 94.3742 | 101.1644 | 94.6498 | 2.1567 | 1.571
2.05 | 100.635 | 94.3693 | 101.1551 | 94.645 | 2.1582 | 1.5714
2.0542 | 100.6305 | 94.3644 | 101.1514 | 94.6403 | 2.1596 | 1.5717
2.0583 | 100.6262 | 94.3592 | 101.1477 | 94.6352 | 2.161 | 1.572
2.0625 | 100.6041 | 94.349 | 101.1263 | 94.6251 | 2.1626 | 1.5725
2.0667 | 100.5854 | 94.3383 | 101.1085 | 94.6146 | 2.1642 | 1.5729
2.0708 | 100.5808 | 94.3268 | 101.1045 | 94.6032 | 2.1655 | 1.5732
2.075 | 100.578 | 94.3172 | 101.1023 | 94.5937 | 2.1668 | 1.5735
2.0792 | 100.5944 | 94.3249 | 101.1193 | 94.6015 | 2.1682 | 1.5739
2.0833 | 100.6073 | 94.3326 | 101.133 | 94.6093 | 2.1697 | 1.5743
2.0875 | 100.5765 | 94.3171 | 101.1028 | 94.594 | 2.1711 | 1.5747
2.0917 | 100.5455 | 94.3007 | 101.0726 | 94.5777 | 2.1725 | 1.5751
2.0958 | 100.5506 | 94.297 | 101.0782 | 94.5741 | 2.1737 | 1.5753
2.1 | 100.5574 | 94.2955 | 101.0856 | 94.5727 | 2.1748 | 1.5755
2.1042 | 100.5841 | 94.301 | 101.1129 | 94.5784 | 2.1761 | 1.5759
2.1083 | 100.6094 | 94.3051 | 101.1388 | 94.5825 | 2.1775 | 1.5763
2.1125 | 100.5836 | 94.2887 | 101.1136 | 94.5662 | 2.1786 | 1.5766
2.1167 | 100.5593 | 94.2708 | 101.0899 | 94.5484 | 2.1798 | 1.5769
2.1208 | 100.5574 | 94.2676 | 101.0885 | 94.5454 | 2.1808 | 1.5772
2.125 | 100.5555 | 94.267 | 101.0871 | 94.5449 | 2.1819 | 1.5774
2.1292 | 100.5494 | 94.2719 | 101.0816 | 94.5498 | 2.1832 | 1.5777
2.1333 | 100.5436 | 94.276 | 101.0765 | 94.5541 | 2.1845 | 1.578
2.1375 | 100.4924 | 94.2567 | 101.026 | 94.5349 | 2.1859 | 1.5784
2.1417 | 100.4445 | 94.2359 | 100.9787 | 94.5143 | 2.1872 | 1.5787
2.1458 | 100.464 | 94.2343 | 100.9988 | 94.5127 | 2.1883 | 1.5789
2.15 | 100.4801 | 94.236 | 101.0154 | 94.5144 | 2.1894 | 1.5791
2.1542 | 100.5104 | 94.2419 | 101.0464 | 94.5204 | 2.1908 | 1.5794
2.1583 | 100.5366 | 94.2469 | 101.0733 | 94.5256 | 2.1922 | 1.5798
2.1625 | 100.4959 | 94.2308 | 101.0332 | 94.5096 | 2.1934 | 1.5801
2.1667 | 100.4583 | 94.2119 | 100.9961 | 94.4908 | 2.1945 | 1.5803
2.1708 | 100.442 | 94.2147 | 100.9804 | 94.4936 | 2.1957 | 1.5805
2.175 | 100.4297 | 94.2195 | 100.9686 | 94.4986 | 2.1969 | 1.5807
2.1792 | 100.4327 | 94.2046 | 100.9723 | 94.4838 | 2.1982 | 1.5811
2.1833 | 100.4335 | 94.1893 | 100.9738 | 94.4686 | 2.1996 | 1.5815
2.1875 | 100.4718 | 94.192 | 101.0125 | 94.4713 | 2.2004 | 1.5816
2.1917 | 100.5024 | 94.1943 | 101.0435 | 94.4737 | 2.2013 | 1.5817
2.1958 | 100.4823 | 94.1942 | 101.0241 | 94.4738 | 2.2027 | 1.5821
2.2 | 100.465 | 94.1925 | 101.0076 | 94.4722 | 2.2041 | 1.5826
2.2042 | 100.3964 | 94.1687 | 100.9395 | 94.4484 | 2.2052 | 1.5828
2.2083 | 100.3378 | 94.1459 | 100.8814 | 94.4257 | 2.2062 | 1.5829
2.2125 | 100.3587 | 94.1536 | 100.9029 | 94.4335 | 2.2075 | 1.5832
2.2167 | 100.3758 | 94.163 | 100.9206 | 94.443 | 2.2087 | 1.5835
2.2208 | 100.3861 | 94.1529 | 100.9315 | 94.433 | 2.2101 | 1.5839
2.225 | 100.3902 | 94.1411 | 100.9364 | 94.4214 | 2.2115 | 1.5842
2.2292 | 100.3819 | 94.129 | 100.9286 | 94.4093 | 2.2125 | 1.5845
2.2333 | 100.3767 | 94.1176 | 100.9238 | 94.3981 | 2.2136 | 1.5847
2.2375 | 100.3823 | 94.1194 | 100.93 | 94.3999 | 2.2147 | 1.585
2.2417 | 100.3899 | 94.121 | 100.9382 | 94.4016 | 2.2159 | 1.5854
2.2458 | 100.3623 | 94.1114 | 100.9112 | 94.3922 | 2.2171 | 1.5857
2.25 | 100.3348 | 94.1007 | 100.8843 | 94.3816 | 2.2183 | 1.586
2.2542 | 100.2994 | 94.0922 | 100.8496 | 94.3732 | 2.2196 | 1.5863
2.2583 | 100.2636 | 94.0836 | 100.8145 | 94.3647 | 2.2209 | 1.5866
2.2625 | 100.2571 | 94.0739 | 100.8086 | 94.3551 | 2.2223 | 1.5869
2.2667 | 100.2486 | 94.0657 | 100.8008 | 94.3471 | 2.2237 | 1.5873
2.2708 | 100.2646 | 94.0684 | 100.8174 | 94.3499 | 2.225 | 1.5875
2.275 | 100.2791 | 94.0713 | 100.8326 | 94.3528 | 2.2263 | 1.5878
2.2792 | 100.2626 | 94.0604 | 100.8168 | 94.3421 | 2.2278 | 1.5882
2.2833 | 100.2491 | 94.0486 | 100.8041 | 94.3304 | 2.2293 | 1.5886
2.2875 | 100.2509 | 94.0403 | 100.8064 | 94.3222 | 2.2303 | 1.5888
2.2917 | 100.2552 | 94.0339 | 100.8112 | 94.3158 | 2.2314 | 1.589
2.2958 | 100.2763 | 94.0426 | 100.8329 | 94.3247 | 2.2327 | 1.5893
2.3 | 100.294 | 94.0508 | 100.8512 | 94.333 | 2.234 | 1.5897
2.3042 | 100.2611 | 94.0346 | 100.819 | 94.3169 | 2.2352 | 1.59
2.3083 | 100.228 | 94.0173 | 100.7865 | 94.2997 | 2.2364 | 1.5903
2.3125 | 100.2326 | 94.0161 | 100.7916 | 94.2986 | 2.2374 | 1.5905
2.3167 | 100.2375 | 94.0173 | 100.797 | 94.2999 | 2.2384 | 1.5907
2.3208 | 100.2537 | 94.0212 | 100.8138 | 94.3039 | 2.2396 | 1.591
2.325 | 100.2695 | 94.0239 | 100.8303 | 94.3067 | 2.2408 | 1.5913
2.3292 | 100.2382 | 94.0083 | 100.7995 | 94.2912 | 2.2419 | 1.5915
2.3333 | 100.2097 | 93.9911 | 100.7715 | 94.2741 | 2.243 | 1.5918
2.3375 | 100.2139 | 93.9887 | 100.7763 | 94.2717 | 2.244 | 1.592
2.3417 | 100.2166 | 93.9889 | 100.7795 | 94.272 | 2.245 | 1.5922
2.3458 | 100.2173 | 93.9937 | 100.7807 | 94.2769 | 2.2462 | 1.5925
2.35 | 100.217 | 93.9981 | 100.7811 | 94.2813 | 2.2475 | 1.5927
2.3542 | 100.1687 | 93.9814 | 100.7334 | 94.2648 | 2.2487 | 1.593
2.3583 | 100.1235 | 93.963 | 100.6888 | 94.2465 | 2.2499 | 1.5933
2.3625 | 100.1344 | 93.9639 | 100.7002 | 94.2474 | 2.251 | 1.5934
2.3667 | 100.1438 | 93.9674 | 100.7101 | 94.251 | 2.252 | 1.5936
2.3708 | 100.1702 | 93.9651 | 100.7373 | 94.2488 | 2.2533 | 1.5939
2.375 | 100.1927 | 93.9622 | 100.7604 | 94.246 | 2.2546 | 1.5943
2.3792 | 100.1869 | 93.9549 | 100.7551 | 94.2388 | 2.2556 | 1.5944
2.3833 | 100.1803 | 93.9459 | 100.7489 | 94.2298 | 2.2565 | 1.5945
2.3875 | 100.1558 | 93.9492 | 100.725 | 94.2333 | 2.2577 | 1.5948
2.3917 | 100.1366 | 93.953 | 100.7064 | 94.2371 | 2.2588 | 1.5951
2.3958 | 100.1052 | 93.9316 | 100.6755 | 94.2158 | 2.26 | 1.5954
2.4 | 100.0765 | 93.9103 | 100.6475 | 94.1946 | 2.2611 | 1.5956
2.4042 | 100.1234 | 93.9188 | 100.6948 | 94.2031 | 2.262 | 1.5957
2.4083 | 100.1617 | 93.9283 | 100.7335 | 94.2127 | 2.2629 | 1.5958
2.4125 | 100.1548 | 93.924 | 100.7273 | 94.2086 | 2.2643 | 1.5963
2.4167 | 100.147 | 93.9174 | 100.7202 | 94.2021 | 2.2656 | 1.5967
2.4208 | 100.0904 | 93.8996 | 100.6641 | 94.1843 | 2.2665 | 1.5968
2.425 | 100.0435 | 93.883 | 100.6176 | 94.1677 | 2.2674 | 1.5969
2.4292 | 100.0502 | 93.8886 | 100.6249 | 94.1735 | 2.2686 | 1.5972
2.4333 | 100.0566 | 93.8955 | 100.632 | 94.1806 | 2.2699 | 1.5975
2.4375 | 100.0598 | 93.885 | 100.6358 | 94.1702 | 2.2711 | 1.5978
2.4417 | 100.0575 | 93.8734 | 100.6341 | 94.1586 | 2.2723 | 1.598
2.4458 | 100.0575 | 93.867 | 100.6346 | 94.1523 | 2.2734 | 1.5983
2.45 | 100.0569 | 93.861 | 100.6346 | 94.1464 | 2.2745 | 1.5985
2.4542 | 100.0573 | 93.8574 | 100.6356 | 94.1429 | 2.2756 | 1.5988
2.4583 | 100.0593 | 93.8539 | 100.6381 | 94.1395 | 2.2766 | 1.5991
2.4625 | 100.0406 | 93.8509 | 100.62 | 94.1366 | 2.2778 | 1.5993
2.4667 | 100.0236 | 93.8475 | 100.6036 | 94.1332 | 2.2789 | 1.5996
2.4708 | 99.9872 | 93.8397 | 100.5678 | 94.1255 | 2.2802 | 1.5999
2.475 | 99.9515 | 93.8312 | 100.5328 | 94.1172 | 2.2815 | 1.6001
2.4792 | 99.9468 | 93.821 | 100.5286 | 94.107 | 2.2827 | 1.6004
2.4833 | 99.9404 | 93.8127 | 100.5229 | 94.0988 | 2.2839 | 1.6007
2.4875 | 99.9701 | 93.8203 | 100.5532 | 94.1065 | 2.2852 | 1.6009
2.4917 | 99.9967 | 93.8279 | 100.5804 | 94.1142 | 2.2864 | 1.6011
2.4958 | 99.981 | 93.8154 | 100.5654 | 94.1018 | 2.2877 | 1.6014
2.5 | 99.9679 | 93.8017 | 100.5529 | 94.0882 | 2.2889 | 1.6018
2.5042 | 99.9728 | 93.7975 | 100.5583 | 94.0841 | 2.2898 | 1.6019
2.5083 | 99.9806 | 93.7952 | 100.5665 | 94.0818 | 2.2906 | 1.602
2.5125 | 99.9966 | 93.8025 | 100.5832 | 94.0892 | 2.2918 | 1.6023
2.5167 | 100.0104 | 93.8089 | 100.5976 | 94.0957 | 2.293 | 1.6026
2.5208 | 99.9737 | 93.7931 | 100.5613 | 94.08 | 2.294 | 1.6028
2.525 | 99.9372 | 93.7761 | 100.5254 | 94.063 | 2.295 | 1.603
2.5292 | 99.9424 | 93.7763 | 100.5311 | 94.0633 | 2.296 | 1.6032
2.5333 | 99.9464 | 93.779 | 100.5355 | 94.0661 | 2.2969 | 1.6034
2.5375 | 99.9568 | 93.7817 | 100.5465 | 94.0689 | 2.298 | 1.6036
2.5417 | 99.9673 | 93.7836 | 100.5576 | 94.0708 | 2.2991 | 1.6038
2.5458 | 99.9343 | 93.7699 | 100.5251 | 94.0573 | 2.3002 | 1.6041
2.55 | 99.9051 | 93.7547 | 100.4965 | 94.0421 | 2.3013 | 1.6043
2.5542 | 99.9112 | 93.7534 | 100.5031 | 94.0408 | 2.3022 | 1.6045
2.5583 | 99.9158 | 93.7543 | 100.5081 | 94.0419 | 2.3031 | 1.6046
2.5625 | 99.922 | 93.7565 | 100.515 | 94.0441 | 2.3043 | 1.6048
2.5667 | 99.9261 | 93.7585 | 100.5197 | 94.0462 | 2.3054 | 1.6051
2.5708 | 99.8936 | 93.7466 | 100.4876 | 94.0343 | 2.3065 | 1.6053
2.575 | 99.8623 | 93.7331 | 100.457 | 94.0209 | 2.3075 | 1.6055
2.5792 | 99.862 | 93.7364 | 100.4571 | 94.0243 | 2.3086 | 1.6056
2.5833 | 99.8625 | 93.7412 | 100.4582 | 94.0292 | 2.3096 | 1.6058
2.5875 | 99.8714 | 93.7304 | 100.4677 | 94.0185 | 2.3108 | 1.6061
2.5917 | 99.8785 | 93.7193 | 100.4753 | 94.0074 | 2.3119 | 1.6064
2.5958 | 99.9023 | 93.7203 | 100.4996 | 94.0085 | 2.3127 | 1.6065
2.6 | 99.9217 | 93.7209 | 100.5193 | 94.0091 | 2.3134 | 1.6065
2.6042 | 99.8977 | 93.7224 | 100.4959 | 94.0107 | 2.3146 | 1.6068
2.6083 | 99.878 | 93.7228 | 100.4769 | 94.0113 | 2.3158 | 1.6071
2.6125 | 99.8256 | 93.7011 | 100.425 | 93.9896 | 2.3167 | 1.6073
2.6167 | 99.78 | 93.6799 | 100.3798 | 93.9685 | 2.3176 | 1.6075
2.6208 | 99.8194 | 93.6903 | 100.4197 | 93.9788 | 2.3186 | 1.6076
2.625 | 99.852 | 93.7022 | 100.4528 | 93.9909 | 2.3196 | 1.6078
2.6292 | 99.8549 | 93.6945 | 100.4563 | 93.9832 | 2.3208 | 1.6081
2.6333 | 99.8537 | 93.6845 | 100.4558 | 93.9734 | 2.322 | 1.6084
2.6375 | 99.8191 | 93.6748 | 100.4216 | 93.9638 | 2.3228 | 1.6085
2.6417 | 99.7911 | 93.6661 | 100.394 | 93.955 | 2.3237 | 1.6086
2.6458 | 99.7843 | 93.6671 | 100.3879 | 93.9561 | 2.3249 | 1.6089
2.65 | 99.7803 | 93.6686 | 100.3845 | 93.9578 | 2.326 | 1.6092
2.6542 | 99.7773 | 93.6615 | 100.3821 | 93.9507 | 2.3271 | 1.6094
2.6583 | 99.7712 | 93.6538 | 100.3765 | 93.9431 | 2.3281 | 1.6095
2.6625 | 99.7718 | 93.6502 | 100.3776 | 93.9396 | 2.3293 | 1.6098
2.6667 | 99.7696 | 93.6462 | 100.3761 | 93.9357 | 2.3304 | 1.6101
2.6708 | 99.7703 | 93.639 | 100.3773 | 93.9286 | 2.3314 | 1.6103
2.675 | 99.7713 | 93.6324 | 100.3787 | 93.922 | 2.3323 | 1.6105
2.6792 | 99.7673 | 93.6359 | 100.3753 | 93.9256 | 2.3334 | 1.6106
2.6833 | 99.7651 | 93.6393 | 100.3736 | 93.9291 | 2.3345 | 1.6108
2.6875 | 99.7265 | 93.63 | 100.3357 | 93.9199 | 2.3357 | 1.6111
2.6917 | 99.6905 | 93.6197 | 100.3003 | 93.9096 | 2.3369 | 1.6114
2.6958 | 99.6882 | 93.6118 | 100.2986 | 93.9018 | 2.3379 | 1.6115
2.7 | 99.6853 | 93.6059 | 100.2962 | 93.896 | 2.3389 | 1.6117
2.7042 | 99.7205 | 93.615 | 100.332 | 93.9052 | 2.3401 | 1.6119
2.7083 | 99.7515 | 93.6238 | 100.3636 | 93.914 | 2.3412 | 1.6121
2.7125 | 99.7355 | 93.6101 | 100.3482 | 93.9004 | 2.3423 | 1.6123
2.7167 | 99.7214 | 93.5952 | 100.3346 | 93.8856 | 2.3433 | 1.6126
2.7208 | 99.7289 | 93.5948 | 100.3424 | 93.8852 | 2.344 | 1.6127
2.725 | 99.7385 | 93.5961 | 100.3525 | 93.8865 | 2.3447 | 1.6127
2.7292 | 99.7459 | 93.6009 | 100.3604 | 93.8915 | 2.3458 | 1.613
2.7333 | 99.7526 | 93.6047 | 100.3677 | 93.8954 | 2.3469 | 1.6133
2.7375 | 99.7127 | 93.5907 | 100.3282 | 93.8814 | 2.3478 | 1.6134
2.7417 | 99.674 | 93.5755 | 100.2899 | 93.8662 | 2.3486 | 1.6135
2.7458 | 99.6794 | 93.5762 | 100.2959 | 93.867 | 2.3495 | 1.6137
2.75 | 99.6823 | 93.5793 | 100.2992 | 93.8702 | 2.3504 | 1.6139
2.7542 | 99.6918 | 93.5807 | 100.3092 | 93.8716 | 2.3515 | 1.6141
2.7583 | 99.7007 | 93.5815 | 100.3187 | 93.8725 | 2.3525 | 1.6142
2.7625 | 99.6739 | 93.5708 | 100.2924 | 93.8619 | 2.3535 | 1.6144
2.7667 | 99.6505 | 93.5587 | 100.2696 | 93.8499 | 2.3545 | 1.6146
2.7708 | 99.6541 | 93.5591 | 100.2736 | 93.8503 | 2.3554 | 1.6147
2.775 | 99.6574 | 93.5612 | 100.2774 | 93.8523 | 2.3562 | 1.6148
2.7792 | 99.6619 | 93.5585 | 100.2824 | 93.8498 | 2.3573 | 1.6151
2.7833 | 99.6641 | 93.5557 | 100.2852 | 93.8471 | 2.3584 | 1.6154
2.7875 | 99.6545 | 93.5498 | 100.276 | 93.8412 | 2.3592 | 1.6154
2.7917 | 99.643 | 93.543 | 100.2649 | 93.8344 | 2.3601 | 1.6155
2.7958 | 99.6336 | 93.5472 | 100.2562 | 93.8388 | 2.3611 | 1.6157
2.8 | 99.6266 | 93.5519 | 100.2497 | 93.8435 | 2.3621 | 1.6159
2.8042 | 99.6128 | 93.5353 | 100.2364 | 93.827 | 2.3631 | 1.6161
2.8083 | 99.6007 | 93.5186 | 100.2248 | 93.8104 | 2.3641 | 1.6164
2.8125 | 99.6411 | 93.5259 | 100.2655 | 93.8176 | 2.3648 | 1.6164
2.8167 | 99.6755 | 93.5338 | 100.3003 | 93.8256 | 2.3655 | 1.6164
2.8208 | 99.6583 | 93.5317 | 100.2838 | 93.8236 | 2.3666 | 1.6167
2.825 | 99.6429 | 93.5278 | 100.269 | 93.8198 | 2.3677 | 1.6171
2.8292 | 99.5873 | 93.5111 | 100.2138 | 93.8032 | 2.3685 | 1.6171
2.8333 | 99.5398 | 93.4953 | 100.1666 | 93.7873 | 2.3693 | 1.6172
2.8375 | 99.5615 | 93.5034 | 100.1889 | 93.7955 | 2.3703 | 1.6174
2.8417 | 99.5798 | 93.513 | 100.2077 | 93.8052 | 2.3713 | 1.6176
2.8458 | 99.5876 | 93.5044 | 100.216 | 93.7967 | 2.3724 | 1.6178
2.85 | 99.59 | 93.4943 | 100.219 | 93.7866 | 2.3734 | 1.618
2.8542 | 99.5773 | 93.4913 | 100.2068 | 93.7837 | 2.3743 | 1.6181
2.8583 | 99.5672 | 93.4888 | 100.1971 | 93.7813 | 2.3751 | 1.6183
2.8625 | 99.5536 | 93.4846 | 100.1841 | 93.7771 | 2.3762 | 1.6185
2.8667 | 99.5437 | 93.4806 | 100.1748 | 93.7732 | 2.3772 | 1.6188
2.8708 | 99.539 | 93.4791 | 100.1705 | 93.7718 | 2.3781 | 1.6189
2.875 | 99.5337 | 93.4779 | 100.1657 | 93.7705 | 2.3791 | 1.6189
2.8792 | 99.5264 | 93.4734 | 100.159 | 93.7662 | 2.3802 | 1.6192
2.8833 | 99.5165 | 93.4682 | 100.1497 | 93.761 | 2.3813 | 1.6195
2.8875 | 99.5209 | 93.4603 | 100.1546 | 93.7532 | 2.3821 | 1.6196
2.8917 | 99.5242 | 93.4536 | 100.1584 | 93.7465 | 2.383 | 1.6197
2.8958 | 99.5358 | 93.4614 | 100.1704 | 93.7544 | 2.384 | 1.6199
2.9 | 99.5478 | 93.469 | 100.183 | 93.7621 | 2.385 | 1.6201
2.9042 | 99.5085 | 93.4577 | 100.1443 | 93.7508 | 2.3861 | 1.6203
2.9083 | 99.4731 | 93.4451 | 100.1094 | 93.7383 | 2.3871 | 1.6205
2.9125 | 99.4728 | 93.4409 | 100.1096 | 93.7342 | 2.3879 | 1.6206
2.9167 | 99.4728 | 93.4389 | 100.11 | 93.7322 | 2.3888 | 1.6207
2.9208 | 99.5046 | 93.4466 | 100.1423 | 93.7399 | 2.3898 | 1.6208
2.925 | 99.5319 | 93.4537 | 100.1702 | 93.7471 | 2.3908 | 1.621
2.9292 | 99.5152 | 93.4403 | 100.154 | 93.7339 | 2.3917 | 1.6212
2.9333 | 99.4994 | 93.4259 | 100.1387 | 93.7195 | 2.3926 | 1.6214
2.9375 | 99.5088 | 93.4278 | 100.1484 | 93.7214 | 2.3932 | 1.6215
2.9417 | 99.519 | 93.4314 | 100.159 | 93.7251 | 2.3939 | 1.6215
2.9458 | 99.519 | 93.4336 | 100.1594 | 93.7273 | 2.3948 | 1.6217
2.95 | 99.5195 | 93.435 | 100.1605 | 93.7288 | 2.3958 | 1.622
2.9542 | 99.48 | 93.4239 | 100.1214 | 93.7177 | 2.3966 | 1.6221
2.9583 | 99.4425 | 93.4116 | 100.0844 | 93.7054 | 2.3974 | 1.6222
2.9625 | 99.4463 | 93.4125 | 100.0887 | 93.7064 | 2.3983 | 1.6223
2.9667 | 99.4474 | 93.4155 | 100.0902 | 93.7094 | 2.3991 | 1.6225
2.9708 | 99.4571 | 93.4146 | 100.1004 | 93.7086 | 2.4001 | 1.6226
2.975 | 99.4655 | 93.4135 | 100.1093 | 93.7076 | 2.4011 | 1.6227
2.9792 | 99.4528 | 93.4066 | 100.097 | 93.7008 | 2.4019 | 1.6229
2.9833 | 99.4417 | 93.3987 | 100.0864 | 93.6928 | 2.4028 | 1.6231
2.9875 | 99.4403 | 93.4008 | 100.0855 | 93.695 | 2.4037 | 1.6231
2.9917 | 99.4405 | 93.4038 | 100.086 | 93.698 | 2.4045 | 1.6232
2.9958 | 99.4348 | 93.3957 | 100.0809 | 93.69 | 2.4054 | 1.6235
3 | 99.4284 | 93.3876 | 100.075 | 93.682 | 2.4064 | 1.6237
3.0042 | 99.4403 | 93.3877 | 100.0873 | 93.6821 | 2.4071 | 1.6237
3.0083 | 99.4477 | 93.3879 | 100.0951 | 93.6823 | 2.4077 | 1.6237
3.0125 | 99.4345 | 93.3911 | 100.0824 | 93.6856 | 2.4088 | 1.6239
3.0167 | 99.4234 | 93.3937 | 100.0718 | 93.6882 | 2.4098 | 1.6242
3.0208 | 99.3918 | 93.3759 | 100.0407 | 93.6705 | 2.4106 | 1.6243
3.025 | 99.3651 | 93.3582 | 100.0144 | 93.6529 | 2.4114 | 1.6244
3.0292 | 99.4067 | 93.3683 | 100.0564 | 93.663 | 2.4121 | 1.6245
3.0333 | 99.4432 | 93.3797 | 100.0933 | 93.6744 | 2.4128 | 1.6246
3.0375 | 99.4353 | 93.374 | 100.0859 | 93.6688 | 2.4139 | 1.6248
3.0417 | 99.4261 | 93.3664 | 100.0773 | 93.6613 | 2.4149 | 1.6251
3.0458 | 99.3819 | 93.3574 | 100.0335 | 93.6523 | 2.4156 | 1.6251
3.05 | 99.3442 | 93.3492 | 99.9961 | 93.6441 | 2.4163 | 1.6251
3.0542 | 99.346 | 93.3522 | 99.9985 | 93.6472 | 2.4173 | 1.6254
3.0583 | 99.3479 | 93.3562 | 100.001 | 93.6513 | 2.4182 | 1.6256
3.0625 | 99.3568 | 93.35 | 100.0103 | 93.6451 | 2.4192 | 1.6257
3.0667 | 99.3612 | 93.3433 | 100.0151 | 93.6384 | 2.42 | 1.6258
3.0708 | 99.3624 | 93.3434 | 100.0169 | 93.6386 | 2.4209 | 1.626
3.075 | 99.3629 | 93.3434 | 100.0179 | 93.6387 | 2.4218 | 1.6261
3.0792 | 99.3506 | 93.3356 | 100.006 | 93.631 | 2.4227 | 1.6263
3.0833 | 99.3414 | 93.3281 | 99.9973 | 93.6235 | 2.4236 | 1.6264
3.0875 | 99.3401 | 93.3327 | 99.9965 | 93.6281 | 2.4244 | 1.6265
3.0917 | 99.34 | 93.3376 | 99.9968 | 93.633 | 2.4252 | 1.6266
3.0958 | 99.3197 | 93.3302 | 99.9771 | 93.6257 | 2.4263 | 1.6268
3.1 | 99.2986 | 93.3215 | 99.9566 | 93.6171 | 2.4273 | 1.6271
3.1042 | 99.3071 | 93.3157 | 99.9654 | 93.6113 | 2.428 | 1.6271
3.1083 | 99.3137 | 93.3116 | 99.9724 | 93.6072 | 2.4287 | 1.6271
3.1125 | 99.3366 | 93.3205 | 99.9958 | 93.6162 | 2.4297 | 1.6273
3.1167 | 99.358 | 93.3289 | 100.0178 | 93.6247 | 2.4307 | 1.6275
3.1208 | 99.3215 | 93.3166 | 99.9818 | 93.6124 | 2.4315 | 1.6277
3.125 | 99.2892 | 93.3031 | 99.9499 | 93.599 | 2.4324 | 1.6278
3.1292 | 99.29 | 93.3026 | 99.9511 | 93.5985 | 2.4331 | 1.6279
3.1333 | 99.292 | 93.3041 | 99.9535 | 93.6 | 2.4338 | 1.6279
3.1375 | 99.3139 | 93.3089 | 99.9759 | 93.6049 | 2.4347 | 1.6281
3.1417 | 99.3325 | 93.3132 | 99.9949 | 93.6092 | 2.4356 | 1.6282
3.1458 | 99.3152 | 93.3017 | 99.9781 | 93.5978 | 2.4364 | 1.6284
3.15 | 99.2983 | 93.2892 | 99.9615 | 93.5854 | 2.4371 | 1.6285
3.1542 | 99.3082 | 93.2921 | 99.9718 | 93.5883 | 2.4377 | 1.6286
3.1583 | 99.3178 | 93.2966 | 99.9818 | 93.5928 | 2.4383 | 1.6286
3.1625 | 99.3137 | 93.2963 | 99.9781 | 93.5926 | 2.4392 | 1.6288
3.1667 | 99.3107 | 93.2956 | 99.9757 | 93.5919 | 2.4401 | 1.629
3.1708 | 99.2778 | 93.2879 | 99.943 | 93.5843 | 2.4408 | 1.6291
3.175 | 99.2467 | 93.2792 | 99.9125 | 93.5756 | 2.4416 | 1.6291
3.1792 | 99.2469 | 93.2805 | 99.913 | 93.577 | 2.4424 | 1.6292
3.1833 | 99.2451 | 93.2833 | 99.9118 | 93.5797 | 2.4433 | 1.6294
3.1875 | 99.2521 | 93.2794 | 99.9192 | 93.5759 | 2.4441 | 1.6295
3.1917 | 99.2576 | 93.2755 | 99.9251 | 93.572 | 2.445 | 1.6296
3.1958 | 99.2633 | 93.2728 | 99.9312 | 93.5693 | 2.4457 | 1.6297
3.2 | 99.2681 | 93.2695 | 99.9364 | 93.5662 | 2.4465 | 1.6298
3.2042 | 99.2622 | 93.2727 | 99.9309 | 93.5694 | 2.4473 | 1.6299
3.2083 | 99.2589 | 93.2759 | 99.9282 | 93.5726 | 2.4481 | 1.63
3.2125 | 99.2388 | 93.2637 | 99.9084 | 93.5605 | 2.4489 | 1.6302
3.2167 | 99.2204 | 93.2516 | 99.8905 | 93.5485 | 2.4497 | 1.6304
3.2208 | 99.2457 | 93.2567 | 99.9162 | 93.5535 | 2.4503 | 1.6304
3.225 | 99.2655 | 93.2625 | 99.9362 | 93.5593 | 2.4509 | 1.6303
3.2292 | 99.2535 | 93.263 | 99.9249 | 93.5599 | 2.4519 | 1.6306
3.2333 | 99.242 | 93.2622 | 99.9138 | 93.5592 | 2.4529 | 1.6309
3.2375 | 99.2038 | 93.2477 | 99.8761 | 93.5447 | 2.4535 | 1.6309
3.2417 | 99.1719 | 93.2334 | 99.8444 | 93.5304 | 2.4541 | 1.6309
3.2458 | 99.2026 | 93.2425 | 99.8756 | 93.5395 | 2.4549 | 1.631
3.25 | 99.2307 | 93.2528 | 99.9042 | 93.5499 | 2.4557 | 1.6312
3.2542 | 99.2311 | 93.2455 | 99.905 | 93.5427 | 2.4566 | 1.6313
3.2583 | 99.2284 | 93.2367 | 99.9028 | 93.534 | 2.4574 | 1.6315
3.2625 | 99.2021 | 93.2346 | 99.8769 | 93.5319 | 2.4581 | 1.6315
3.2667 | 99.1791 | 93.2331 | 99.8543 | 93.5304 | 2.4588 | 1.6316
3.2708 | 99.1663 | 93.2303 | 99.842 | 93.5276 | 2.4597 | 1.6318
3.275 | 99.1556 | 93.2278 | 99.8317 | 93.5252 | 2.4606 | 1.632
3.2792 | 99.1643 | 93.2268 | 99.8409 | 93.5242 | 2.4614 | 1.632
3.2833 | 99.1704 | 93.2258 | 99.8474 | 93.5233 | 2.4622 | 1.632
3.2875 | 99.1738 | 93.2251 | 99.8513 | 93.5226 | 2.4631 | 1.6322
3.2917 | 99.1749 | 93.2235 | 99.8529 | 93.5211 | 2.464 | 1.6324
3.2958 | 99.1702 | 93.2151 | 99.8486 | 93.5127 | 2.4647 | 1.6325
3.3 | 99.167 | 93.2074 | 99.8457 | 93.505 | 2.4653 | 1.6325
3.3042 | 99.1727 | 93.2159 | 99.8518 | 93.5136 | 2.4661 | 1.6326
3.3083 | 99.1796 | 93.2247 | 99.8591 | 93.5224 | 2.4669 | 1.6327
3.3125 | 99.1469 | 93.2141 | 99.827 | 93.5119 | 2.4678 | 1.6329
3.3167 | 99.1157 | 93.2022 | 99.7963 | 93.5 | 2.4687 | 1.6331
3.3208 | 99.1261 | 93.2 | 99.807 | 93.4978 | 2.4693 | 1.6331
3.325 | 99.1347 | 93.1998 | 99.8159 | 93.4976 | 2.4699 | 1.6331
3.3292 | 99.1619 | 93.2071 | 99.8436 | 93.505 | 2.4708 | 1.6333
3.3333 | 99.1861 | 93.2135 | 99.8683 | 93.5115 | 2.4717 | 1.6335
3.3375 | 99.1562 | 93.202 | 99.8389 | 93.5 | 2.4724 | 1.6336
3.3417 | 99.1298 | 93.1897 | 99.8128 | 93.4876 | 2.4731 | 1.6336
3.3458 | 99.1311 | 93.1917 | 99.8145 | 93.4898 | 2.4737 | 1.6337
3.35 | 99.1339 | 93.1953 | 99.8176 | 93.4933 | 2.4743 | 1.6338
3.3542 | 99.1436 | 93.197 | 99.8277 | 93.4952 | 2.4752 | 1.6339
3.3583 | 99.1517 | 93.1982 | 99.8363 | 93.4964 | 2.4759 | 1.634
3.3625 | 99.1351 | 93.1896 | 99.82 | 93.4878 | 2.4766 | 1.6341
3.3667 | 99.1184 | 93.1802 | 99.8037 | 93.4784 | 2.4773 | 1.6342
3.3708 | 99.1274 | 93.1832 | 99.813 | 93.4814 | 2.4779 | 1.6343
3.375 | 99.135 | 93.1875 | 99.821 | 93.4857 | 2.4785 | 1.6343
3.3792 | 99.1297 | 93.185 | 99.8161 | 93.4833 | 2.4793 | 1.6345
3.3833 | 99.1256 | 93.1821 | 99.8125 | 93.4805 | 2.4801 | 1.6346
3.3875 | 99.1051 | 93.1781 | 99.7924 | 93.4764 | 2.4808 | 1.6347
3.3917 | 99.0858 | 93.1733 | 99.7734 | 93.4717 | 2.4814 | 1.6347
3.3958 | 99.081 | 93.1751 | 99.769 | 93.4735 | 2.4822 | 1.6348
3.4 | 99.0759 | 93.1776 | 99.7644 | 93.4761 | 2.483 | 1.6349
3.4042 | 99.0752 | 93.1705 | 99.7641 | 93.4691 | 2.4838 | 1.635
3.4083 | 99.0738 | 93.1634 | 99.7631 | 93.462 | 2.4846 | 1.6351
3.4125 | 99.0965 | 93.1646 | 99.7861 | 93.4632 | 2.4852 | 1.6352
3.4167 | 99.1159 | 93.166 | 99.8059 | 93.4647 | 2.4858 | 1.6353
3.4208 | 99.1081 | 93.1689 | 99.7986 | 93.4675 | 2.4866 | 1.6354
3.425 | 99.1028 | 93.1709 | 99.7937 | 93.4696 | 2.4874 | 1.6355
3.4292 | 99.07 | 93.1575 | 99.7613 | 93.4563 | 2.488 | 1.6356
3.4333 | 99.0413 | 93.1443 | 99.733 | 93.4431 | 2.4887 | 1.6357
3.4375 | 99.0689 | 93.152 | 99.7609 | 93.4508 | 2.4892 | 1.6357
3.4417 | 99.0915 | 93.1608 | 99.7838 | 93.4596 | 2.4898 | 1.6357
3.4458 | 99.0843 | 93.1581 | 99.7771 | 93.4569 | 2.4907 | 1.6359
3.45 | 99.0753 | 93.1539 | 99.7686 | 93.4528 | 2.4916 | 1.6362
3.4542 | 99.0424 | 93.1453 | 99.736 | 93.4442 | 2.4922 | 1.6361
3.4583 | 99.0148 | 93.1371 | 99.7087 | 93.436 | 2.4928 | 1.6361
3.4625 | 99.0291 | 93.142 | 99.7235 | 93.441 | 2.4936 | 1.6363
3.4667 | 99.0438 | 93.1478 | 99.7385 | 93.4469 | 2.4944 | 1.6365
3.4708 | 99.0501 | 93.1418 | 99.7453 | 93.4409 | 2.4951 | 1.6365
3.475 | 99.0534 | 93.1351 | 99.749 | 93.4341 | 2.4958 | 1.6366
3.4792 | 99.0425 | 93.1368 | 99.7385 | 93.436 | 2.4965 | 1.6367
3.4833 | 99.0317 | 93.1388 | 99.7281 | 93.4379 | 2.4972 | 1.6368
3.4875 | 99.0132 | 93.1314 | 99.71 | 93.4306 | 2.498 | 1.6369
3.4917 | 98.9971 | 93.1242 | 99.6943 | 93.4235 | 2.4987 | 1.637
3.4958 | 99.0063 | 93.1289 | 99.7039 | 93.4282 | 2.4994 | 1.637
3.5 | 99.0146 | 93.1341 | 99.7126 | 93.4333 | 2.5001 | 1.637
3.5042 | 99.0098 | 93.1295 | 99.7084 | 93.4288 | 2.501 | 1.6372
3.5083 | 99.0033 | 93.1237 | 99.7023 | 93.423 | 2.5019 | 1.6375
3.5125 | 99.0084 | 93.1176 | 99.7077 | 93.417 | 2.5024 | 1.6374
3.5167 | 99.0136 | 93.1129 | 99.7132 | 93.4122 | 2.5029 | 1.6374
3.5208 | 99.0262 | 93.1223 | 99.7263 | 93.4217 | 2.5037 | 1.6375
3.525 | 99.0393 | 93.1313 | 99.7397 | 93.4309 | 2.5045 | 1.6377
3.5292 | 98.9999 | 93.1192 | 99.7008 | 93.4188 | 2.5052 | 1.6378
3.5333 | 98.9635 | 93.1059 | 99.6647 | 93.4055 | 2.5059 | 1.6379
3.5375 | 98.9727 | 93.1073 | 99.6742 | 93.4069 | 2.5065 | 1.6379
3.5417 | 98.981 | 93.1107 | 99.6828 | 93.4103 | 2.507 | 1.6379
3.5458 | 99.0049 | 93.1146 | 99.7072 | 93.4142 | 2.5078 | 1.6381
3.55 | 99.0257 | 93.1177 | 99.7284 | 93.4173 | 2.5086 | 1.6382
3.5542 | 99.0051 | 93.1086 | 99.7082 | 93.4083 | 2.5092 | 1.6383
3.5583 | 98.9864 | 93.0989 | 99.6898 | 93.3986 | 2.5098 | 1.6383
3.5625 | 98.988 | 93.1019 | 99.6917 | 93.4017 | 2.5104 | 1.6384
3.5667 | 98.9906 | 93.1061 | 99.6947 | 93.4059 | 2.5109 | 1.6385
3.5708 | 98.9894 | 93.1052 | 99.6939 | 93.405 | 2.5116 | 1.6386
3.575 | 98.9883 | 93.1039 | 99.6932 | 93.4038 | 2.5123 | 1.6387
3.5792 | 98.9746 | 93.0984 | 99.6798 | 93.3983 | 2.5129 | 1.6387
3.5833 | 98.9604 | 93.0922 | 99.6659 | 93.3921 | 2.5136 | 1.6388
3.5875 | 98.9667 | 93.095 | 99.6725 | 93.3949 | 2.5142 | 1.6389
3.5917 | 98.9713 | 93.0988 | 99.6776 | 93.3987 | 2.5148 | 1.6389
3.5958 | 98.9651 | 93.094 | 99.6718 | 93.394 | 2.5155 | 1.639
3.6 | 98.9601 | 93.0889 | 99.6672 | 93.389 | 2.5162 | 1.6392
3.6042 | 98.9559 | 93.0882 | 99.6632 | 93.3883 | 2.5168 | 1.6392
3.6083 | 98.9515 | 93.0873 | 99.6591 | 93.3873 | 2.5174 | 1.6392
3.6125 | 98.9423 | 93.0893 | 99.6505 | 93.3894 | 2.5182 | 1.6393
3.6167 | 98.9344 | 93.0913 | 99.6429 | 93.3915 | 2.5189 | 1.6394
3.6208 | 98.9227 | 93.0818 | 99.6316 | 93.382 | 2.5196 | 1.6395
3.625 | 98.9119 | 93.0724 | 99.6211 | 93.3727 | 2.5202 | 1.6396
3.6292 | 98.945 | 93.0768 | 99.6546 | 93.377 | 2.5208 | 1.6396
3.6333 | 98.9737 | 93.0819 | 99.6835 | 93.3822 | 2.5213 | 1.6397
3.6375 | 98.9676 | 93.0831 | 99.6779 | 93.3834 | 2.5221 | 1.6398
3.6417 | 98.9625 | 93.0831 | 99.6732 | 93.3834 | 2.5228 | 1.6399
3.6458 | 98.9244 | 93.0717 | 99.6354 | 93.372 | 2.5233 | 1.64
3.65 | 98.8915 | 93.0604 | 99.6028 | 93.3608 | 2.5239 | 1.64
3.6542 | 98.9111 | 93.0679 | 99.6227 | 93.3682 | 2.5245 | 1.6401
3.6583 | 98.928 | 93.0764 | 99.64 | 93.3767 | 2.525 | 1.6401
3.6625 | 98.9265 | 93.0715 | 99.639 | 93.372 | 2.5259 | 1.6403
3.6667 | 98.9219 | 93.0656 | 99.6348 | 93.3661 | 2.5267 | 1.6404
3.6708 | 98.9014 | 93.063 | 99.6146 | 93.3635 | 2.5272 | 1.6404
3.675 | 98.8839 | 93.0608 | 99.5974 | 93.3613 | 2.5277 | 1.6404
3.6792 | 98.8835 | 93.0602 | 99.5974 | 93.3608 | 2.5285 | 1.6405
3.6833 | 98.8854 | 93.0602 | 99.5998 | 93.3608 | 2.5293 | 1.6407
3.6875 | 98.8956 | 93.0582 | 99.6103 | 93.3588 | 2.5299 | 1.6407
3.6917 | 98.9039 | 93.056 | 99.6189 | 93.3566 | 2.5304 | 1.6407
3.6958 | 98.8995 | 93.0577 | 99.615 | 93.3584 | 2.5312 | 1.6408
3.7 | 98.8936 | 93.0588 | 99.6095 | 93.3596 | 2.532 | 1.641
3.7042 | 98.8782 | 93.0499 | 99.5944 | 93.3506 | 2.5325 | 1.641
3.7083 | 98.8643 | 93.0414 | 99.5808 | 93.3421 | 2.5331 | 1.6411
3.7125 | 98.8752 | 93.0503 | 99.5921 | 93.351 | 2.5338 | 1.6411
3.7167 | 98.8861 | 93.0597 | 99.6034 | 93.3604 | 2.5344 | 1.6412
3.7208 | 98.8688 | 93.0508 | 99.5865 | 93.3516 | 2.5352 | 1.6413
3.725 | 98.8513 | 93.0404 | 99.5695 | 93.3413 | 2.536 | 1.6415
3.7292 | 98.8646 | 93.0387 | 99.583 | 93.3395 | 2.5364 | 1.6414
3.7333 | 98.8772 | 93.0387 | 99.5958 | 93.3395 | 2.5368 | 1.6414
3.7375 | 98.8941 | 93.0458 | 99.6131 | 93.3468 | 2.5376 | 1.6415
3.7417 | 98.9101 | 93.0523 | 99.6296 | 93.3533 | 2.5383 | 1.6417
3.7458 | 98.872 | 93.0412 | 99.5919 | 93.3421 | 2.5389 | 1.6418
3.75 | 98.8371 | 93.0291 | 99.5572 | 93.3301 | 2.5395 | 1.6418
3.7542 | 98.8426 | 93.0328 | 99.563 | 93.3338 | 2.54 | 1.6418
3.7583 | 98.848 | 93.038 | 99.5687 | 93.339 | 2.5405 | 1.6419
3.7625 | 98.8634 | 93.0384 | 99.5845 | 93.3395 | 2.5412 | 1.642
3.7667 | 98.8764 | 93.0381 | 99.5979 | 93.3392 | 2.5419 | 1.6421
3.7708 | 98.8658 | 93.0322 | 99.5876 | 93.3333 | 2.5424 | 1.6421
3.775 | 98.8556 | 93.0259 | 99.5778 | 93.327 | 2.5429 | 1.6421
3.7792 | 98.8574 | 93.0289 | 99.5798 | 93.33 | 2.5435 | 1.6422
3.7833 | 98.8596 | 93.0325 | 99.5824 | 93.3337 | 2.544 | 1.6423
3.7875 | 98.8506 | 93.0295 | 99.5737 | 93.3308 | 2.5446 | 1.6424
3.7917 | 98.8429 | 93.0264 | 99.5664 | 93.3277 | 2.5452 | 1.6424
3.7958 | 98.8347 | 93.0238 | 99.5584 | 93.3251 | 2.5458 | 1.6425
3.8 | 98.8255 | 93.0208 | 99.5495 | 93.322 | 2.5463 | 1.6425
3.8042 | 98.8276 | 93.0233 | 99.552 | 93.3246 | 2.547 | 1.6426
3.8083 | 98.8287 | 93.0265 | 99.5534 | 93.3278 | 2.5476 | 1.6426
3.8125 | 98.8203 | 93.0196 | 99.5454 | 93.321 | 2.5482 | 1.6427
3.8167 | 98.8131 | 93.0126 | 99.5385 | 93.314 | 2.5489 | 1.6429
3.8208 | 98.8251 | 93.0148 | 99.5509 | 93.3162 | 2.5494 | 1.6429
3.825 | 98.8356 | 93.0174 | 99.5616 | 93.3188 | 2.5499 | 1.6428
3.8292 | 98.8247 | 93.0189 | 99.5512 | 93.3204 | 2.5506 | 1.643
3.8333 | 98.8154 | 93.0199 | 99.5423 | 93.3214 | 2.5513 | 1.6431
3.8375 | 98.7932 | 93.0099 | 99.5204 | 93.3114 | 2.5519 | 1.6431
3.8417 | 98.7733 | 93.0001 | 99.5008 | 93.3016 | 2.5524 | 1.6432
3.8458 | 98.8072 | 93.0061 | 99.535 | 93.3076 | 2.5529 | 1.6432
3.85 | 98.8369 | 93.0131 | 99.565 | 93.3146 | 2.5534 | 1.6432
3.8542 | 98.8352 | 93.0121 | 99.5636 | 93.3136 | 2.5541 | 1.6434
3.8583 | 98.8324 | 93.0098 | 99.5612 | 93.3114 | 2.5548 | 1.6435
3.8625 | 98.798 | 93.0025 | 99.5271 | 93.3041 | 2.5552 | 1.6435
3.8667 | 98.7683 | 92.9954 | 99.4977 | 93.297 | 2.5557 | 1.6435
3.8708 | 98.7747 | 93.0001 | 99.5044 | 93.3017 | 2.5563 | 1.6436
3.875 | 98.781 | 93.0055 | 99.5111 | 93.3071 | 2.5569 | 1.6437
3.8792 | 98.7846 | 93.0008 | 99.5151 | 93.3025 | 2.5576 | 1.6438
3.8833 | 98.785 | 92.9956 | 99.5158 | 93.2973 | 2.5583 | 1.6439
3.8875 | 98.777 | 92.997 | 99.5082 | 93.2988 | 2.5588 | 1.6439
3.8917 | 98.7694 | 92.9985 | 99.5009 | 93.3002 | 2.5594 | 1.6438
3.8958 | 98.7609 | 92.9931 | 99.4928 | 93.2949 | 2.5601 | 1.644
3.9 | 98.7552 | 92.9881 | 99.4875 | 93.2899 | 2.5607 | 1.6442
3.9042 | 98.768 | 92.9912 | 99.5005 | 93.2931 | 2.5612 | 1.6441
3.9083 | 98.7802 | 92.9947 | 99.513 | 93.2965 | 2.5617 | 1.644
3.9125 | 98.7728 | 92.9931 | 99.5061 | 93.295 | 2.5625 | 1.6442
3.9167 | 98.7637 | 92.9904 | 99.4974 | 93.2924 | 2.5632 | 1.6444
3.9208 | 98.7569 | 92.9832 | 99.4908 | 93.2852 | 2.5636 | 1.6444
3.925 | 98.7505 | 92.977 | 99.4846 | 93.2789 | 2.564 | 1.6443
3.9292 | 98.7633 | 92.9872 | 99.4978 | 93.2891 | 2.5647 | 1.6444
3.9333 | 98.7761 | 92.9975 | 99.511 | 93.2995 | 2.5654 | 1.6445
3.9375 | 98.7486 | 92.9859 | 99.4839 | 93.2879 | 2.566 | 1.6446
3.9417 | 98.7226 | 92.973 | 99.4583 | 93.275 | 2.5666 | 1.6447
3.9458 | 98.7395 | 92.9756 | 99.4753 | 93.2777 | 2.567 | 1.6447
3.95 | 98.7558 | 92.9801 | 99.4919 | 93.2822 | 2.5674 | 1.6447
3.9542 | 98.7722 | 92.9832 | 99.5087 | 93.2853 | 2.5681 | 1.6448
3.9583 | 98.787 | 92.9854 | 99.5239 | 93.2876 | 2.5687 | 1.6449
3.9625 | 98.7577 | 92.9773 | 99.4948 | 93.2794 | 2.5692 | 1.6449
3.9667 | 98.7303 | 92.9687 | 99.4677 | 93.2709 | 2.5696 | 1.6449
3.9708 | 98.731 | 92.9728 | 99.4687 | 93.275 | 2.5701 | 1.645
3.975 | 98.7321 | 92.9779 | 99.47 | 93.2801 | 2.5706 | 1.6451
3.9792 | 98.7367 | 92.9757 | 99.475 | 93.2779 | 2.5713 | 1.6451
3.9833 | 98.7405 | 92.9731 | 99.4792 | 93.2753 | 2.5719 | 1.6452
3.9875 | 98.739 | 92.9702 | 99.478 | 93.2725 | 2.5723 | 1.6452
3.9917 | 98.7368 | 92.9671 | 99.476 | 93.2693 | 2.5728 | 1.6453
3.9958 | 98.7387 | 92.9695 | 99.4782 | 93.2718 | 2.5733 | 1.6453
4 | 98.7405 | 92.9723 | 99.4803 | 93.2746 | 2.5738 | 1.6454
4.0042 | 98.7267 | 92.9677 | 99.4668 | 93.2701 | 2.5744 | 1.6454
4.0083 | 98.7149 | 92.9631 | 99.4553 | 93.2655 | 2.575 | 1.6455
4.0125 | 98.7143 | 92.963 | 99.455 | 93.2654 | 2.5754 | 1.6455
4.0167 | 98.7124 | 92.9628 | 99.4533 | 93.2652 | 2.5759 | 1.6455
4.0208 | 98.7102 | 92.9651 | 99.4516 | 93.2675 | 2.5766 | 1.6456
4.025 | 98.7077 | 92.9676 | 99.4494 | 93.27 | 2.5772 | 1.6457
4.0292 | 98.6953 | 92.9594 | 99.4373 | 93.2619 | 2.5777 | 1.6458
4.0333 | 98.6845 | 92.9512 | 99.4268 | 93.2537 | 2.5783 | 1.6458
4.0375 | 98.7085 | 92.9556 | 99.4511 | 93.2581 | 2.5787 | 1.6458
4.0417 | 98.7302 | 92.9608 | 99.473 | 93.2633 | 2.5791 | 1.6458
4.0458 | 98.7208 | 92.9613 | 99.464 | 93.2638 | 2.5798 | 1.6459
4.05 | 98.7122 | 92.9606 | 99.4558 | 93.2632 | 2.5805 | 1.6461
4.0542 | 98.6836 | 92.9522 | 99.4275 | 93.2548 | 2.5809 | 1.6461
4.0583 | 98.6583 | 92.944 | 99.4025 | 93.2466 | 2.5813 | 1.6461
4.0625 | 98.6837 | 92.9497 | 99.4281 | 93.2523 | 2.5818 | 1.6461
4.0667 | 98.7066 | 92.9562 | 99.4512 | 93.2588 | 2.5824 | 1.6462
4.0708 | 98.71 | 92.9536 | 99.4551 | 93.2562 | 2.5829 | 1.6463
4.075 | 98.7111 | 92.9499 | 99.4564 | 93.2526 | 2.5835 | 1.6463
4.0792 | 98.6871 | 92.9473 | 99.4327 | 93.25 | 2.584 | 1.6464
4.0833 | 98.6659 | 92.9447 | 99.4118 | 93.2474 | 2.5845 | 1.6464
4.0875 | 98.6598 | 92.9452 | 99.406 | 93.2479 | 2.585 | 1.6464
4.0917 | 98.6557 | 92.946 | 99.4023 | 93.2488 | 2.5856 | 1.6465
4.0958 | 98.663 | 92.9439 | 99.4099 | 93.2467 | 2.5862 | 1.6466
4.1 | 98.6681 | 92.9418 | 99.4153 | 93.2446 | 2.5867 | 1.6466
4.1042 | 98.6668 | 92.944 | 99.4144 | 93.2467 | 2.5873 | 1.6466
4.1083 | 98.664 | 92.9457 | 99.4118 | 93.2486 | 2.5879 | 1.6467
4.1125 | 98.6555 | 92.938 | 99.4037 | 93.2408 | 2.5884 | 1.6468
4.1167 | 98.6489 | 92.9307 | 99.3974 | 93.2336 | 2.589 | 1.6469
4.1208 | 98.6636 | 92.9383 | 99.4124 | 93.2412 | 2.5894 | 1.6468
4.125 | 98.6786 | 92.9463 | 99.4276 | 93.2491 | 2.5899 | 1.6468
4.1292 | 98.6622 | 92.9401 | 99.4116 | 93.243 | 2.5906 | 1.647
4.1333 | 98.6451 | 92.9326 | 99.3949 | 93.2356 | 2.5912 | 1.6472
4.1375 | 98.6479 | 92.9297 | 99.3979 | 93.2327 | 2.5915 | 1.6471
4.1417 | 98.6502 | 92.9282 | 99.4004 | 93.2311 | 2.5918 | 1.6469
4.1458 | 98.6636 | 92.9364 | 99.4141 | 93.2393 | 2.5925 | 1.6471
4.15 | 98.6763 | 92.9441 | 99.4271 | 93.2471 | 2.5931 | 1.6473
4.1542 | 98.6456 | 92.9327 | 99.3968 | 93.2357 | 2.5936 | 1.6473
4.1583 | 98.6172 | 92.9203 | 99.3686 | 93.2233 | 2.5941 | 1.6473
4.1625 | 98.6327 | 92.9258 | 99.3844 | 93.2289 | 2.5945 | 1.6473
4.1667 | 98.6481 | 92.9329 | 99.4 | 93.236 | 2.5949 | 1.6473
4.1708 | 98.6596 | 92.9318 | 99.4118 | 93.2349 | 2.5955 | 1.6474
4.175 | 98.6696 | 92.9298 | 99.4222 | 93.2328 | 2.596 | 1.6475
4.1792 | 98.653 | 92.9257 | 99.4058 | 93.2288 | 2.5964 | 1.6475
4.1833 | 98.637 | 92.9215 | 99.39 | 93.2246 | 2.5968 | 1.6475
4.1875 | 98.6335 | 92.9246 | 99.3869 | 93.2277 | 2.5973 | 1.6476
4.1917 | 98.6303 | 92.9281 | 99.3839 | 93.2313 | 2.5978 | 1.6476
4.1958 | 98.625 | 92.9245 | 99.3789 | 93.2276 | 2.5983 | 1.6477
4.2 | 98.6204 | 92.9208 | 99.3746 | 93.224 | 2.5988 | 1.6477
4.2042 | 98.6261 | 92.9202 | 99.3805 | 93.2234 | 2.5992 | 1.6477
4.2083 | 98.6304 | 92.9194 | 99.3851 | 93.2226 | 2.5997 | 1.6478
4.2125 | 98.6323 | 92.9215 | 99.3874 | 93.2247 | 2.6002 | 1.6478
4.2167 | 98.6339 | 92.9237 | 99.3892 | 93.227 | 2.6007 | 1.6479
4.2208 | 98.6179 | 92.9179 | 99.3735 | 93.2212 | 2.6012 | 1.6479
4.225 | 98.6047 | 92.9121 | 99.3606 | 93.2154 | 2.6017 | 1.648
4.2292 | 98.6139 | 92.9141 | 99.37 | 93.2174 | 2.6021 | 1.648
4.2333 | 98.6225 | 92.9163 | 99.3788 | 93.2196 | 2.6026 | 1.648
4.2375 | 98.6197 | 92.9181 | 99.3764 | 93.2214 | 2.6032 | 1.6481
4.2417 | 98.617 | 92.9196 | 99.3741 | 93.2229 | 2.6038 | 1.6481
4.2458 | 98.6028 | 92.9114 | 99.3601 | 93.2148 | 2.6043 | 1.6482
4.25 | 98.5902 | 92.9032 | 99.3478 | 93.2065 | 2.6048 | 1.6482
4.2542 | 98.6213 | 92.9086 | 99.3792 | 93.212 | 2.6052 | 1.6482
4.2583 | 98.6504 | 92.915 | 99.4085 | 93.2184 | 2.6056 | 1.6482
4.2625 | 98.6477 | 92.9139 | 99.4062 | 93.2173 | 2.6062 | 1.6483
4.2667 | 98.6443 | 92.9116 | 99.4031 | 93.2151 | 2.6068 | 1.6484
4.2708 | 98.6177 | 92.9064 | 99.3768 | 93.2098 | 2.6072 | 1.6484
4.275 | 98.5937 | 92.9014 | 99.353 | 93.2048 | 2.6076 | 1.6484
4.2792 | 98.6068 | 92.9048 | 99.3664 | 93.2082 | 2.6081 | 1.6485
4.2833 | 98.6203 | 92.9087 | 99.3802 | 93.2122 | 2.6086 | 1.6485
4.2875 | 98.6309 | 92.906 | 99.3911 | 93.2095 | 2.6091 | 1.6486
4.2917 | 98.639 | 92.9029 | 99.3994 | 93.2064 | 2.6096 | 1.6486
4.2958 | 98.6291 | 92.9036 | 99.3899 | 93.2071 | 2.6101 | 1.6486
4.3 | 98.6195 | 92.904 | 99.3806 | 93.2076 | 2.6106 | 1.6487
4.3042 | 98.6087 | 92.9005 | 99.37 | 93.204 | 2.6111 | 1.6487
4.3083 | 98.6005 | 92.8973 | 99.3621 | 93.2008 | 2.6116 | 1.6488
4.3125 | 98.6125 | 92.8991 | 99.3744 | 93.2027 | 2.6121 | 1.6488
4.3167 | 98.6241 | 92.9013 | 99.3864 | 93.2049 | 2.6126 | 1.6488
4.3208 | 98.6237 | 92.9012 | 99.3863 | 93.2048 | 2.6132 | 1.6489
4.325 | 98.6214 | 92.9003 | 99.3843 | 93.204 | 2.6138 | 1.649
4.3292 | 98.6212 | 92.8934 | 99.3843 | 93.1971 | 2.6142 | 1.649
4.3333 | 98.6215 | 92.8872 | 99.3849 | 93.1909 | 2.6146 | 1.649
4.3375 | 98.6394 | 92.8968 | 99.4031 | 93.2004 | 2.6151 | 1.649
4.3417 | 98.6576 | 92.9064 | 99.4216 | 93.2101 | 2.6155 | 1.649
4.3458 | 98.6342 | 92.8967 | 99.3985 | 93.2004 | 2.6161 | 1.6492
4.35 | 98.611 | 92.8858 | 99.3757 | 93.1896 | 2.6167 | 1.6493
4.3542 | 98.6223 | 92.8879 | 99.3871 | 93.1916 | 2.6169 | 1.6492
4.3583 | 98.6331 | 92.8914 | 99.398 | 93.1951 | 2.6172 | 1.6491
4.3625 | 98.6462 | 92.8952 | 99.4116 | 93.1989 | 2.6178 | 1.6492
4.3667 | 98.6584 | 92.8982 | 99.424 | 93.2021 | 2.6185 | 1.6494
4.3708 | 98.635 | 92.8897 | 99.4008 | 93.1935 | 2.6188 | 1.6494
4.375 | 98.6129 | 92.8807 | 99.379 | 93.1845 | 2.6192 | 1.6493
4.3792 | 98.6251 | 92.8868 | 99.3915 | 93.1906 | 2.6196 | 1.6494
4.3833 | 98.6379 | 92.8939 | 99.4045 | 93.1977 | 2.6201 | 1.6495
4.3875 | 98.6438 | 92.8897 | 99.4107 | 93.1936 | 2.6206 | 1.6495
4.3917 | 98.6493 | 92.885 | 99.4164 | 93.1888 | 2.621 | 1.6495
4.3958 | 98.6479 | 92.8845 | 99.4152 | 93.1884 | 2.6214 | 1.6495
4.4 | 98.6452 | 92.8842 | 99.4128 | 93.1881 | 2.6218 | 1.6496
4.4042 | 98.6406 | 92.8858 | 99.4085 | 93.1897 | 2.6223 | 1.6496
4.4083 | 98.6357 | 92.8875 | 99.4038 | 93.1914 | 2.6227 | 1.6496
4.4125 | 98.624 | 92.8834 | 99.3924 | 93.1873 | 2.6232 | 1.6497
4.4167 | 98.6145 | 92.8795 | 99.3831 | 93.1834 | 2.6237 | 1.6497
4.4208 | 98.6268 | 92.8803 | 99.3957 | 93.1842 | 2.6241 | 1.6497
4.425 | 98.6376 | 92.8809 | 99.4068 | 93.1848 | 2.6245 | 1.6498
4.4292 | 98.6405 | 92.883 | 99.41 | 93.1869 | 2.6251 | 1.6498
4.4333 | 98.642 | 92.8849 | 99.4118 | 93.1889 | 2.6256 | 1.6499
4.4375 | 98.6246 | 92.8783 | 99.3947 | 93.1823 | 2.626 | 1.6499
4.4417 | 98.6094 | 92.8717 | 99.3798 | 93.1757 | 2.6265 | 1.65
4.4458 | 98.6252 | 92.8752 | 99.3958 | 93.1793 | 2.6269 | 1.6499
4.45 | 98.6408 | 92.8795 | 99.4116 | 93.1835 | 2.6273 | 1.6499
4.4542 | 98.6367 | 92.8801 | 99.4079 | 93.1841 | 2.6279 | 1.65
4.4583 | 98.6322 | 92.8801 | 99.4038 | 93.1841 | 2.6285 | 1.6501
4.4625 | 98.6148 | 92.8734 | 99.3865 | 93.1775 | 2.629 | 1.6501
4.4667 | 98.599 | 92.8668 | 99.371 | 93.1708 | 2.6294 | 1.6501
4.4708 | 98.6263 | 92.8718 | 99.3986 | 93.1758 | 2.6298 | 1.6501
4.475 | 98.6536 | 92.8776 | 99.4261 | 93.1816 | 2.6302 | 1.6502
4.4792 | 98.6568 | 92.8753 | 99.4296 | 93.1794 | 2.6308 | 1.6502
4.4833 | 98.6575 | 92.8722 | 99.4306 | 93.1763 | 2.6313 | 1.6503
4.4875 | 98.6357 | 92.8705 | 99.4091 | 93.1746 | 2.6317 | 1.6503
4.4917 | 98.6143 | 92.8689 | 99.3879 | 93.173 | 2.6321 | 1.6503
4.4958 | 98.6122 | 92.8689 | 99.3862 | 93.173 | 2.6326 | 1.6503
4.5 | 98.6125 | 92.8692 | 99.3868 | 93.1734 | 2.6331 | 1.6504
4.5042 | 98.6259 | 92.8683 | 99.4004 | 93.1725 | 2.6335 | 1.6504
4.5083 | 98.6383 | 92.8675 | 99.4131 | 93.1717 | 2.634 | 1.6504
4.5125 | 98.6366 | 92.869 | 99.4116 | 93.1732 | 2.6346 | 1.6505
4.5167 | 98.6332 | 92.87 | 99.4086 | 93.1742 | 2.6351 | 1.6505
4.5208 | 98.6228 | 92.8642 | 99.3984 | 93.1684 | 2.6355 | 1.6506
4.525 | 98.6142 | 92.8589 | 99.39 | 93.1631 | 2.6359 | 1.6506
4.5292 | 98.6273 | 92.8646 | 99.4035 | 93.1688 | 2.6364 | 1.6506
4.5333 | 98.6411 | 92.8705 | 99.4175 | 93.1747 | 2.6369 | 1.6506
4.5375 | 98.6325 | 92.8666 | 99.4093 | 93.1709 | 2.6374 | 1.6507
4.5417 | 98.6227 | 92.8618 | 99.3998 | 93.1661 | 2.638 | 1.6508
4.5458 | 98.6299 | 92.8582 | 99.4071 | 93.1625 | 2.6383 | 1.6507
4.55 | 98.6374 | 92.8556 | 99.4149 | 93.1599 | 2.6386 | 1.6507
4.5542 | 98.6544 | 92.864 | 99.4322 | 93.1683 | 2.6391 | 1.6508
4.5583 | 98.671 | 92.8721 | 99.449 | 93.1764 | 2.6396 | 1.6508
4.5625 | 98.6433 | 92.8614 | 99.4217 | 93.1658 | 2.6401 | 1.6509
4.5667 | 98.6158 | 92.8499 | 99.3944 | 93.1543 | 2.6405 | 1.6509
4.5708 | 98.628 | 92.8557 | 99.4068 | 93.16 | 2.6408 | 1.6509
4.575 | 98.6409 | 92.8628 | 99.4198 | 93.1671 | 2.6411 | 1.6508
4.5792 | 98.6485 | 92.8616 | 99.4278 | 93.166 | 2.6417 | 1.651
4.5833 | 98.6554 | 92.8597 | 99.4351 | 93.1641 | 2.6423 | 1.6511
4.5875 | 98.6431 | 92.8556 | 99.423 | 93.16 | 2.6426 | 1.651
4.5917 | 98.6306 | 92.8515 | 99.4106 | 93.1559 | 2.6428 | 1.6509
4.5958 | 98.6359 | 92.8561 | 99.4161 | 93.1605 | 2.6433 | 1.651
4.6 | 98.6417 | 92.8612 | 99.4223 | 93.1656 | 2.6438 | 1.6512
4.6042 | 98.6389 | 92.8559 | 99.4197 | 93.1603 | 2.6442 | 1.6512
4.6083 | 98.6372 | 92.8503 | 99.4182 | 93.1547 | 2.6446 | 1.6511
4.6125 | 98.6459 | 92.8521 | 99.4272 | 93.1566 | 2.645 | 1.6512
4.6167 | 98.6527 | 92.8542 | 99.4342 | 93.1587 | 2.6454 | 1.6512
4.6208 | 98.6473 | 92.8548 | 99.429 | 93.1592 | 2.6459 | 1.6512
4.625 | 98.6402 | 92.8551 | 99.4222 | 93.1596 | 2.6463 | 1.6512
4.6292 | 98.6228 | 92.851 | 99.4051 | 93.1555 | 2.6468 | 1.6513
4.6333 | 98.608 | 92.8471 | 99.3905 | 93.1516 | 2.6473 | 1.6514
4.6375 | 98.623 | 92.8487 | 99.4057 | 93.1532 | 2.6476 | 1.6513
4.6417 | 98.638 | 92.8503 | 99.4211 | 93.1548 | 2.648 | 1.6513
4.6458 | 98.6413 | 92.8523 | 99.4246 | 93.1568 | 2.6486 | 1.6514
4.65 | 98.643 | 92.854 | 99.4268 | 93.1585 | 2.6492 | 1.6515
4.6542 | 98.6255 | 92.8473 | 99.4095 | 93.1518 | 2.6496 | 1.6515
4.6583 | 98.6095 | 92.8404 | 99.3936 | 93.145 | 2.65 | 1.6515
4.6625 | 98.6284 | 92.8449 | 99.4128 | 93.1495 | 2.6503 | 1.6515
4.6667 | 98.6479 | 92.8503 | 99.4325 | 93.1549 | 2.6507 | 1.6515
4.6708 | 98.6448 | 92.8495 | 99.4297 | 93.154 | 2.6513 | 1.6516
4.675 | 98.6402 | 92.8478 | 99.4255 | 93.1524 | 2.6519 | 1.6516
4.6792 | 98.622 | 92.8438 | 99.4075 | 93.1484 | 2.6522 | 1.6516
4.6833 | 98.6047 | 92.8399 | 99.3905 | 93.1445 | 2.6526 | 1.6516
4.6875 | 98.6219 | 92.8429 | 99.4079 | 93.1475 | 2.6531 | 1.6517
4.6917 | 98.6409 | 92.8464 | 99.4272 | 93.151 | 2.6535 | 1.6517
4.6958 | 98.6501 | 92.8443 | 99.4367 | 93.1489 | 2.654 | 1.6517
4.7 | 98.6568 | 92.8417 | 99.4436 | 93.1464 | 2.6544 | 1.6518
4.7042 | 98.6426 | 92.8425 | 99.4297 | 93.1472 | 2.6548 | 1.6518
4.7083 | 98.6266 | 92.8432 | 99.4139 | 93.1479 | 2.6552 | 1.6518
4.7125 | 98.614 | 92.84 | 99.4016 | 93.1447 | 2.6557 | 1.6518
4.7167 | 98.6042 | 92.8371 | 99.3921 | 93.1418 | 2.6562 | 1.6519
4.7208 | 98.6185 | 92.8392 | 99.4066 | 93.1439 | 2.6566 | 1.6519
4.725 | 98.6338 | 92.8417 | 99.4222 | 93.1464 | 2.657 | 1.6518
4.7292 | 98.6338 | 92.8416 | 99.4224 | 93.1463 | 2.6576 | 1.6519
4.7333 | 98.6319 | 92.8407 | 99.4209 | 93.1454 | 2.6581 | 1.652
4.7375 | 98.6285 | 92.8352 | 99.4177 | 93.14 | 2.6585 | 1.652
4.7417 | 98.6258 | 92.8304 | 99.4152 | 93.1352 | 2.6588 | 1.652
4.7458 | 98.6394 | 92.8381 | 99.429 | 93.1429 | 2.6592 | 1.652
4.75 | 98.6531 | 92.8458 | 99.4431 | 93.1505 | 2.6597 | 1.652
4.7542 | 98.6348 | 92.8385 | 99.425 | 93.1433 | 2.6602 | 1.6521
4.7583 | 98.6157 | 92.8303 | 99.4062 | 93.1351 | 2.6607 | 1.6522
4.7625 | 98.6279 | 92.8311 | 99.4186 | 93.136 | 2.6609 | 1.6521
4.7667 | 98.6413 | 92.8332 | 99.4321 | 93.138 | 2.6612 | 1.652
4.7708 | 98.6551 | 92.8378 | 99.4462 | 93.1426 | 2.6617 | 1.6521
4.775 | 98.6678 | 92.8419 | 99.4593 | 93.1467 | 2.6622 | 1.6523
4.7792 | 98.6439 | 92.8332 | 99.4356 | 93.1381 | 2.6626 | 1.6522
4.7833 | 98.6193 | 92.8241 | 99.4111 | 93.1289 | 2.6629 | 1.6522
4.7875 | 98.6282 | 92.8312 | 99.4202 | 93.136 | 2.6632 | 1.6522
4.7917 | 98.6381 | 92.8393 | 99.4304 | 93.1441 | 2.6636 | 1.6522
4.7958 | 98.6382 | 92.8343 | 99.4307 | 93.1391 | 2.6641 | 1.6523
4.8 | 98.6387 | 92.8286 | 99.4315 | 93.1335 | 2.6646 | 1.6524
4.8042 | 98.6395 | 92.829 | 99.4326 | 93.1339 | 2.6649 | 1.6523
4.8083 | 98.6393 | 92.8296 | 99.4325 | 93.1345 | 2.6651 | 1.6523
4.8125 | 98.6389 | 92.8318 | 99.4324 | 93.1367 | 2.6657 | 1.6524
4.8167 | 98.6381 | 92.8339 | 99.4319 | 93.1388 | 2.6662 | 1.6525
4.8208 | 98.6277 | 92.829 | 99.4217 | 93.1339 | 2.6665 | 1.6525
4.825 | 98.6195 | 92.8242 | 99.4137 | 93.1291 | 2.6669 | 1.6524
4.8292 | 98.634 | 92.8268 | 99.4285 | 93.1317 | 2.6673 | 1.6525
4.8333 | 98.6474 | 92.8296 | 99.4421 | 93.1345 | 2.6677 | 1.6525
4.8375 | 98.6434 | 92.8299 | 99.4384 | 93.1349 | 2.6681 | 1.6525
4.8417 | 98.6369 | 92.8299 | 99.4322 | 93.1349 | 2.6686 | 1.6525
4.8458 | 98.617 | 92.8258 | 99.4125 | 93.1307 | 2.669 | 1.6526
4.85 | 98.5992 | 92.8217 | 99.395 | 93.1267 | 2.6694 | 1.6526
4.8542 | 98.6151 | 92.8239 | 99.4111 | 93.1288 | 2.6698 | 1.6526
4.8583 | 98.6327 | 92.8263 | 99.4289 | 93.1312 | 2.6701 | 1.6526
4.8625 | 98.6364 | 92.8278 | 99.4329 | 93.1328 | 2.6707 | 1.6526
4.8667 | 98.6386 | 92.8289 | 99.4355 | 93.1339 | 2.6713 | 1.6527
4.8708 | 98.6221 | 92.8231 | 99.4191 | 93.1281 | 2.6716 | 1.6527
4.875 | 98.606 | 92.8171 | 99.4032 | 93.1221 | 2.6719 | 1.6527
4.8792 | 98.6234 | 92.8215 | 99.4209 | 93.1265 | 2.6723 | 1.6527
4.8833 | 98.6423 | 92.8267 | 99.44 | 93.1318 | 2.6727 | 1.6527
4.8875 | 98.642 | 92.8247 | 99.44 | 93.1298 | 2.6732 | 1.6528
4.8917 | 98.6395 | 92.822 | 99.4377 | 93.1271 | 2.6737 | 1.6528
4.8958 | 98.6235 | 92.821 | 99.422 | 93.126 | 2.674 | 1.6528
4.9 | 98.6069 | 92.8201 | 99.4056 | 93.1252 | 2.6744 | 1.6528
4.9042 | 98.6114 | 92.8201 | 99.4103 | 93.1252 | 2.6748 | 1.6529
4.9083 | 98.619 | 92.8203 | 99.4182 | 93.1254 | 2.6753 | 1.6529
4.9125 | 98.633 | 92.8199 | 99.4325 | 93.125 | 2.6757 | 1.6529
4.9167 | 98.646 | 92.8195 | 99.4457 | 93.1245 | 2.6761 | 1.6529
4.9208 | 98.6385 | 92.8208 | 99.4384 | 93.1259 | 2.6765 | 1.6529
4.925 | 98.6278 | 92.8218 | 99.428 | 93.1268 | 2.677 | 1.653
4.9292 | 98.6127 | 92.8168 | 99.4131 | 93.1219 | 2.6773 | 1.653
4.9333 | 98.5994 | 92.8122 | 99.4002 | 93.1173 | 2.6777 | 1.653
4.9375 | 98.613 | 92.8172 | 99.4139 | 93.1223 | 2.6781 | 1.653
4.9417 | 98.6287 | 92.8226 | 99.4298 | 93.1277 | 2.6785 | 1.653
4.9458 | 98.6241 | 92.8196 | 99.4257 | 93.1247 | 2.6791 | 1.6531
4.95 | 98.6185 | 92.8155 | 99.4203 | 93.1207 | 2.6796 | 1.6532
4.9542 | 98.6248 | 92.8126 | 99.4267 | 93.1177 | 2.6798 | 1.6531
4.9583 | 98.6315 | 92.8107 | 99.4336 | 93.1158 | 2.6801 | 1.6531
4.9625 | 98.6442 | 92.8177 | 99.4466 | 93.1228 | 2.6805 | 1.6531
4.9667 | 98.656 | 92.8244 | 99.4586 | 93.1295 | 2.681 | 1.6532
4.9708 | 98.6316 | 92.8157 | 99.4345 | 93.1209 | 2.6814 | 1.6532
4.975 | 98.6061 | 92.8063 | 99.4092 | 93.1115 | 2.6818 | 1.6532
4.9792 | 98.6188 | 92.811 | 99.422 | 93.1162 | 2.682 | 1.6532
4.9833 | 98.6333 | 92.8167 | 99.4367 | 93.1219 | 2.6823 | 1.6531
4.9875 | 98.6412 | 92.8165 | 99.4449 | 93.1217 | 2.6828 | 1.6532
4.9917 | 98.6486 | 92.8157 | 99.4526 | 93.121 | 2.6833 | 1.6533
4.9958 | 98.6354 | 92.811 | 99.4396 | 93.1163 | 2.6835 | 1.6533
5 | 98.6208 | 92.8063 | 99.4251 | 93.1115 | 2.6838 | 1.6532
5.0042 | 98.6242 | 92.8124 | 99.4289 | 93.1176 | 2.6842 | 1.6533
5.0083 | 98.6282 | 92.819 | 99.4331 | 93.1242 | 2.6846 | 1.6533
5.0125 | 98.6204 | 92.8122 | 99.4254 | 93.1175 | 2.685 | 1.6534
5.0167 | 98.6142 | 92.8052 | 99.4196 | 93.1105 | 2.6854 | 1.6534
5.0208 | 98.6261 | 92.8086 | 99.4316 | 93.1139 | 2.6857 | 1.6534
5.025 | 98.637 | 92.8123 | 99.4427 | 93.1176 | 2.686 | 1.6533
5.0292 | 98.6338 | 92.8123 | 99.4397 | 93.1176 | 2.6865 | 1.6534
5.0333 | 98.6287 | 92.8118 | 99.435 | 93.1171 | 2.687 | 1.6535
5.0375 | 98.6135 | 92.8082 | 99.4199 | 93.1135 | 2.6873 | 1.6535
5.0417 | 98.6006 | 92.8048 | 99.4072 | 93.1101 | 2.6876 | 1.6534
5.0458 | 98.6165 | 92.8071 | 99.4234 | 93.1124 | 2.688 | 1.6535
5.05 | 98.6329 | 92.8094 | 99.44 | 93.1148 | 2.6884 | 1.6535
5.0542 | 98.6318 | 92.8102 | 99.4391 | 93.1155 | 2.6888 | 1.6535
5.0583 | 98.6277 | 92.8106 | 99.4353 | 93.1159 | 2.6893 | 1.6535
5.0625 | 98.6078 | 92.8064 | 99.4157 | 93.1117 | 2.6897 | 1.6536
5.0667 | 98.5891 | 92.8021 | 99.3972 | 93.1074 | 2.6901 | 1.6536
5.0708 | 98.6041 | 92.8047 | 99.4124 | 93.11 | 2.6904 | 1.6536
5.075 | 98.6221 | 92.8077 | 99.4306 | 93.1131 | 2.6907 | 1.6535
5.0792 | 98.6265 | 92.8083 | 99.4352 | 93.1136 | 2.6912 | 1.6536
5.0833 | 98.6293 | 92.8083 | 99.4384 | 93.1137 | 2.6918 | 1.6537
5.0875 | 98.6149 | 92.8043 | 99.4242 | 93.1097 | 2.6921 | 1.6537
5.0917 | 98.5997 | 92.8003 | 99.4091 | 93.1056 | 2.6924 | 1.6536
5.0958 | 98.6113 | 92.8033 | 99.421 | 93.1087 | 2.6928 | 1.6537
5.1 | 98.6251 | 92.8071 | 99.435 | 93.1125 | 2.6931 | 1.6537
5.1042 | 98.6287 | 92.805 | 99.4389 | 93.1103 | 2.6935 | 1.6537
5.1083 | 98.6303 | 92.8023 | 99.4407 | 93.1077 | 2.6939 | 1.6537
5.1125 | 98.6181 | 92.8035 | 99.4287 | 93.1089 | 2.6943 | 1.6537
5.1167 | 98.6039 | 92.8048 | 99.4148 | 93.1102 | 2.6947 | 1.6538
5.1208 | 98.5979 | 92.8019 | 99.409 | 93.1073 | 2.6951 | 1.6538
5.125 | 98.5952 | 92.7989 | 99.4066 | 93.1044 | 2.6955 | 1.6538
5.1292 | 98.6122 | 92.8012 | 99.4237 | 93.1067 | 2.6958 | 1.6538
5.1333 | 98.6299 | 92.8038 | 99.4417 | 93.1093 | 2.6962 | 1.6538
5.1375 | 98.6253 | 92.8037 | 99.4374 | 93.1091 | 2.6966 | 1.6538
5.1417 | 98.6175 | 92.8028 | 99.4298 | 93.1083 | 2.6971 | 1.6539
5.1458 | 98.6073 | 92.7983 | 99.4198 | 93.1037 | 2.6974 | 1.6539
5.15 | 98.5979 | 92.7943 | 99.4106 | 93.0998 | 2.6977 | 1.6539
5.1542 | 98.6094 | 92.8008 | 99.4223 | 93.1063 | 2.6981 | 1.6539
5.1583 | 98.6227 | 92.8075 | 99.4359 | 93.1129 | 2.6985 | 1.6539
5.1625 | 98.6107 | 92.8016 | 99.4242 | 93.1071 | 2.699 | 1.654
5.1667 | 98.5984 | 92.7948 | 99.4121 | 93.1003 | 2.6994 | 1.654
5.1708 | 98.6123 | 92.7956 | 99.4261 | 93.1011 | 2.6996 | 1.654
5.175 | 98.6273 | 92.7975 | 99.4413 | 93.1029 | 2.6998 | 1.6539
5.1792 | 98.6376 | 92.8015 | 99.4518 | 93.107 | 2.7002 | 1.654
5.1833 | 98.646 | 92.805 | 99.4605 | 93.1105 | 2.7007 | 1.6541
5.1875 | 98.6228 | 92.7974 | 99.4375 | 93.1029 | 2.701 | 1.6541
5.1917 | 98.5976 | 92.7896 | 99.4124 | 93.0951 | 2.7012 | 1.654
5.1958 | 98.6059 | 92.7961 | 99.4209 | 93.1016 | 2.7015 | 1.654
5.2 | 98.6165 | 92.8033 | 99.4316 | 93.1088 | 2.7019 | 1.654
5.2042 | 98.6165 | 92.7991 | 99.4319 | 93.1046 | 2.7023 | 1.6541
5.2083 | 98.6173 | 92.7943 | 99.4331 | 93.0999 | 2.7027 | 1.6542
5.2125 | 98.6182 | 92.7941 | 99.434 | 93.0996 | 2.703 | 1.6541
5.2167 | 98.6176 | 92.7941 | 99.4336 | 93.0996 | 2.7032 | 1.654
5.2208 | 98.6165 | 92.7976 | 99.4328 | 93.1032 | 2.7036 | 1.6541
5.225 | 98.6143 | 92.8011 | 99.4308 | 93.1067 | 2.7041 | 1.6542
5.2292 | 98.6001 | 92.7949 | 99.4169 | 93.1004 | 2.7044 | 1.6542
5.2333 | 98.5884 | 92.7886 | 99.4053 | 93.0941 | 2.7047 | 1.6542
5.2375 | 98.6059 | 92.793 | 99.4231 | 93.0986 | 2.705 | 1.6542
5.2417 | 98.6239 | 92.7978 | 99.4413 | 93.1034 | 2.7054 | 1.6542
5.2458 | 98.6208 | 92.7966 | 99.4384 | 93.1021 | 2.7058 | 1.6542
5.25 | 98.6148 | 92.7949 | 99.4327 | 93.1004 | 2.7063 | 1.6543
5.2542 | 98.5977 | 92.7925 | 99.4157 | 93.0981 | 2.7066 | 1.6543
5.2583 | 98.5821 | 92.7904 | 99.4003 | 93.0959 | 2.7069 | 1.6542
5.2625 | 98.5965 | 92.7918 | 99.415 | 93.0973 | 2.7072 | 1.6543
5.2667 | 98.6129 | 92.7934 | 99.4316 | 93.099 | 2.7076 | 1.6543
5.2708 | 98.6147 | 92.7946 | 99.4337 | 93.1002 | 2.708 | 1.6543
5.275 | 98.6139 | 92.7955 | 99.4331 | 93.1012 | 2.7084 | 1.6543
5.2792 | 98.5959 | 92.7915 | 99.4153 | 93.0971 | 2.7088 | 1.6543
5.2833 | 98.5776 | 92.7872 | 99.3972 | 93.0928 | 2.7092 | 1.6544
5.2875 | 98.59 | 92.7899 | 99.4098 | 93.0956 | 2.7094 | 1.6543
5.2917 | 98.6059 | 92.7933 | 99.4259 | 93.0989 | 2.7097 | 1.6543
5.2958 | 98.6112 | 92.7928 | 99.4315 | 93.0984 | 2.7102 | 1.6544
5.3 | 98.6151 | 92.7917 | 99.4357 | 93.0973 | 2.7107 | 1.6545
5.3042 | 98.6038 | 92.7901 | 99.4245 | 93.0957 | 2.7109 | 1.6544
5.3083 | 98.5905 | 92.7885 | 99.4113 | 93.0941 | 2.7112 | 1.6543
5.3125 | 98.5939 | 92.7893 | 99.4149 | 93.0949 | 2.7116 | 1.6544
5.3167 | 98.5999 | 92.7905 | 99.4212 | 93.0961 | 2.712 | 1.6545
5.3208 | 98.6077 | 92.7895 | 99.4292 | 93.0951 | 2.7123 | 1.6545
5.325 | 98.6145 | 92.7883 | 99.4362 | 93.0939 | 2.7126 | 1.6544
5.3292 | 98.6058 | 92.7902 | 99.4277 | 93.0959 | 2.713 | 1.6545
5.3333 | 98.5941 | 92.7919 | 99.4163 | 93.0977 | 2.7134 | 1.6545
5.3375 | 98.5833 | 92.7872 | 99.4056 | 93.0929 | 2.7137 | 1.6545
5.3417 | 98.5751 | 92.7825 | 99.3977 | 93.0883 | 2.7141 | 1.6545
5.3458 | 98.5925 | 92.7875 | 99.4153 | 93.0932 | 2.7144 | 1.6545
5.35 | 98.6121 | 92.7928 | 99.435 | 93.0985 | 2.7148 | 1.6545
5.3542 | 98.6061 | 92.7899 | 99.4293 | 93.0956 | 2.7152 | 1.6546
5.3583 | 98.5974 | 92.7861 | 99.421 | 93.0918 | 2.7156 | 1.6546
5.3625 | 98.5966 | 92.784 | 99.4203 | 93.0897 | 2.7158 | 1.6546
5.3667 | 98.5959 | 92.7827 | 99.4197 | 93.0884 | 2.716 | 1.6546
5.3708 | 98.6042 | 92.7885 | 99.4282 | 93.0942 | 2.7164 | 1.6546
5.375 | 98.613 | 92.794 | 99.4373 | 93.0997 | 2.7169 | 1.6546
5.3792 | 98.5954 | 92.7869 | 99.4199 | 93.0926 | 2.7172 | 1.6547
5.3833 | 98.5773 | 92.7791 | 99.402 | 93.0849 | 2.7176 | 1.6547
5.3875 | 98.5938 | 92.7832 | 99.4186 | 93.089 | 2.7178 | 1.6546
5.3917 | 98.6123 | 92.7882 | 99.4372 | 93.094 | 2.7179 | 1.6546
5.3958 | 98.6182 | 92.7882 | 99.4434 | 93.094 | 2.7184 | 1.6547
5.4 | 98.6224 | 92.7875 | 99.4478 | 93.0933 | 2.7188 | 1.6548
5.4042 | 98.6077 | 92.7831 | 99.4332 | 93.0889 | 2.719 | 1.6547
5.4083 | 98.5903 | 92.7788 | 99.416 | 93.0846 | 2.7192 | 1.6547
5.4125 | 98.592 | 92.785 | 99.4179 | 93.0907 | 2.7195 | 1.6547
5.4167 | 98.5949 | 92.7913 | 99.421 | 93.0971 | 2.7199 | 1.6547
5.4208 | 98.5866 | 92.7848 | 99.413 | 93.0906 | 2.7203 | 1.6548
5.425 | 98.5808 | 92.7782 | 99.4074 | 93.084 | 2.7206 | 1.6548
5.4292 | 98.594 | 92.7814 | 99.4207 | 93.0871 | 2.7209 | 1.6547
5.4333 | 98.6071 | 92.7849 | 99.4339 | 93.0907 | 2.7211 | 1.6547
5.4375 | 98.6042 | 92.7856 | 99.4313 | 93.0914 | 2.7216 | 1.6548
5.4417 | 98.5982 | 92.786 | 99.4256 | 93.0918 | 2.722 | 1.6549
5.4458 | 98.5806 | 92.7816 | 99.4081 | 93.0874 | 2.7223 | 1.6548
5.45 | 98.565 | 92.7773 | 99.3927 | 93.0831 | 2.7225 | 1.6548
5.4542 | 98.5828 | 92.7811 | 99.4107 | 93.0869 | 2.7228 | 1.6548
5.4583 | 98.6024 | 92.7852 | 99.4305 | 93.091 | 2.7232 | 1.6548
5.4625 | 98.6013 | 92.784 | 99.4297 | 93.0898 | 2.7236 | 1.6548
5.4667 | 98.5972 | 92.7823 | 99.4258 | 93.0882 | 2.724 | 1.6549
5.4708 | 98.5806 | 92.7806 | 99.4093 | 93.0865 | 2.7243 | 1.6549
5.475 | 98.5642 | 92.7791 | 99.3932 | 93.0849 | 2.7246 | 1.6549
5.4792 | 98.5756 | 92.7798 | 99.4047 | 93.0857 | 2.7249 | 1.6549
5.4833 | 98.59 | 92.7809 | 99.4193 | 93.0867 | 2.7252 | 1.6549
5.4875 | 98.5944 | 92.7823 | 99.4239 | 93.0881 | 2.7256 | 1.6549
5.4917 | 98.5966 | 92.7835 | 99.4265 | 93.0893 | 2.726 | 1.6549
5.4958 | 98.5816 | 92.7799 | 99.4116 | 93.0858 | 2.7263 | 1.6549
5.5 | 98.5649 | 92.7762 | 99.3951 | 93.0821 | 2.7266 | 1.655
5.5042 | 98.5728 | 92.7786 | 99.4032 | 93.0845 | 2.7269 | 1.6549
5.5083 | 98.5843 | 92.7817 | 99.4149 | 93.0875 | 2.7272 | 1.6549
5.5125 | 98.591 | 92.7804 | 99.4218 | 93.0863 | 2.7276 | 1.655
5.5167 | 98.5969 | 92.7786 | 99.4279 | 93.0845 | 2.728 | 1.655
5.5208 | 98.5885 | 92.7792 | 99.4198 | 93.0851 | 2.7283 | 1.655
5.525 | 98.5776 | 92.7798 | 99.4089 | 93.0857 | 2.7285 | 1.6549
5.5292 | 98.5735 | 92.778 | 99.4051 | 93.0839 | 2.7289 | 1.655
5.5333 | 98.5719 | 92.7764 | 99.4037 | 93.0823 | 2.7292 | 1.6551
5.5375 | 98.5832 | 92.7776 | 99.4151 | 93.0836 | 2.7295 | 1.655
5.5417 | 98.5949 | 92.7791 | 99.427 | 93.085 | 2.7297 | 1.655
5.5458 | 98.5875 | 92.7798 | 99.4199 | 93.0857 | 2.7302 | 1.655
5.55 | 98.577 | 92.78 | 99.4097 | 93.0859 | 2.7306 | 1.6551
5.5542 | 98.5678 | 92.7755 | 99.4006 | 93.0814 | 2.7308 | 1.6551
5.5583 | 98.5605 | 92.7712 | 99.3934 | 93.0771 | 2.731 | 1.655
5.5625 | 98.5759 | 92.7775 | 99.409 | 93.0834 | 2.7314 | 1.6551
5.5667 | 98.5936 | 92.7841 | 99.4269 | 93.09 | 2.7318 | 1.6551
5.5708 | 98.5837 | 92.7785 | 99.4173 | 93.0845 | 2.7322 | 1.6551
5.575 | 98.572 | 92.7721 | 99.4059 | 93.078 | 2.7325 | 1.6552
5.5792 | 98.5804 | 92.7734 | 99.4143 | 93.0793 | 2.7327 | 1.6551
5.5833 | 98.5891 | 92.7757 | 99.423 | 93.0816 | 2.7328 | 1.6551
5.5875 | 98.5932 | 92.7787 | 99.4274 | 93.0846 | 2.7332 | 1.6551
5.5917 | 98.5963 | 92.7812 | 99.4308 | 93.0871 | 2.7336 | 1.6552
5.5958 | 98.5782 | 92.775 | 99.4128 | 93.0809 | 2.7339 | 1.6552
5.6 | 98.5592 | 92.7686 | 99.394 | 93.0746 | 2.7341 | 1.6552
5.6042 | 98.5725 | 92.7715 | 99.4074 | 93.0774 | 2.7344 | 1.6552
5.6083 | 98.5883 | 92.7779 | 99.4233 | 93.0838 | 2.7346 | 1.6552
5.6125 | 98.5884 | 92.774 | 99.4237 | 93.08 | 2.735 | 1.6552
5.6167 | 98.5879 | 92.7699 | 99.4234 | 93.0759 | 2.7354 | 1.6553
5.6208 | 98.5861 | 92.769 | 99.4217 | 93.0749 | 2.7355 | 1.6553
5.625 | 98.5818 | 92.7688 | 99.4175 | 93.0747 | 2.7357 | 1.6552
5.6292 | 98.5777 | 92.7734 | 99.4137 | 93.0794 | 2.7361 | 1.6553
5.6333 | 98.5727 | 92.7773 | 99.4089 | 93.0832 | 2.7365 | 1.6553
5.6375 | 98.5575 | 92.7734 | 99.3939 | 93.0793 | 2.7368 | 1.6553
5.6417 | 98.5458 | 92.7669 | 99.3824 | 93.0729 | 2.737 | 1.6553
5.6458 | 98.5661 | 92.7717 | 99.4028 | 93.0776 | 2.7373 | 1.6553
5.65 | 98.5881 | 92.7768 | 99.425 | 93.0827 | 2.7376 | 1.6553
5.6542 | 98.5863 | 92.7753 | 99.4235 | 93.0813 | 2.738 | 1.6553
5.6583 | 98.5804 | 92.7736 | 99.4178 | 93.0796 | 2.7384 | 1.6554
5.6625 | 98.5625 | 92.7705 | 99.4 | 93.0765 | 2.7386 | 1.6554
5.6667 | 98.5453 | 92.7684 | 99.383 | 93.0744 | 2.7388 | 1.6553
5.6708 | 98.5592 | 92.7707 | 99.397 | 93.0766 | 2.7391 | 1.6554
5.675 | 98.576 | 92.773 | 99.414 | 93.079 | 2.7394 | 1.6554
5.6792 | 98.5776 | 92.7727 | 99.4158 | 93.0787 | 2.7398 | 1.6554
5.6833 | 98.5766 | 92.7721 | 99.4151 | 93.0781 | 2.7402 | 1.6554
5.6875 | 98.562 | 92.7707 | 99.4007 | 93.0768 | 2.7405 | 1.6554
5.6917 | 98.5465 | 92.7691 | 99.3853 | 93.0751 | 2.7407 | 1.6554
5.6958 | 98.5542 | 92.7696 | 99.3931 | 93.0757 | 2.741 | 1.6554
5.7 | 98.5655 | 92.7706 | 99.4047 | 93.0766 | 2.7413 | 1.6554
5.7042 | 98.572 | 92.7716 | 99.4114 | 93.0777 | 2.7416 | 1.6554
5.7083 | 98.577 | 92.7725 | 99.4165 | 93.0785 | 2.742 | 1.6555
5.7125 | 98.5651 | 92.7701 | 99.4049 | 93.0762 | 2.7423 | 1.6555
5.7167 | 98.5507 | 92.7676 | 99.3907 | 93.0736 | 2.7426 | 1.6554
5.7208 | 98.5532 | 92.769 | 99.3933 | 93.075 | 2.7429 | 1.6555
5.725 | 98.5589 | 92.7708 | 99.3992 | 93.0768 | 2.7431 | 1.6555
5.7292 | 98.5673 | 92.7697 | 99.4078 | 93.0758 | 2.7434 | 1.6555
5.7333 | 98.5757 | 92.7684 | 99.4163 | 93.0744 | 2.7438 | 1.6555
5.7375 | 98.5696 | 92.7701 | 99.4105 | 93.0762 | 2.744 | 1.6555
5.7417 | 98.5605 | 92.7718 | 99.4015 | 93.0778 | 2.7443 | 1.6555
5.7458 | 98.5523 | 92.7681 | 99.3935 | 93.0741 | 2.7446 | 1.6555
5.75 | 98.5461 | 92.7644 | 99.3874 | 93.0705 | 2.7449 | 1.6556
5.7542 | 98.5592 | 92.7682 | 99.4007 | 93.0742 | 2.7452 | 1.6555
5.7583 | 98.5738 | 92.7724 | 99.4155 | 93.0784 | 2.7454 | 1.6554
5.7625 | 98.5652 | 92.7705 | 99.4072 | 93.0766 | 2.7458 | 1.6555
5.7667 | 98.554 | 92.7679 | 99.3962 | 93.074 | 2.7462 | 1.6556
5.7708 | 98.5512 | 92.7655 | 99.3934 | 93.0715 | 2.7464 | 1.6556
5.775 | 98.5498 | 92.7636 | 99.3922 | 93.0697 | 2.7465 | 1.6555
5.7792 | 98.561 | 92.7693 | 99.4036 | 93.0753 | 2.7469 | 1.6555
5.7833 | 98.5736 | 92.7748 | 99.4165 | 93.0809 | 2.7473 | 1.6556
5.7875 | 98.5606 | 92.7682 | 99.4036 | 93.0742 | 2.7476 | 1.6556
5.7917 | 98.5463 | 92.7607 | 99.3894 | 93.0668 | 2.7478 | 1.6556
5.7958 | 98.5599 | 92.7642 | 99.4032 | 93.0703 | 2.748 | 1.6556
5.8 | 98.5745 | 92.7696 | 99.4178 | 93.0757 | 2.7482 | 1.6556
5.8042 | 98.5737 | 92.769 | 99.4172 | 93.075 | 2.7485 | 1.6556
5.8083 | 98.5712 | 92.7675 | 99.415 | 93.0736 | 2.7489 | 1.6557
5.8125 | 98.5588 | 92.7642 | 99.4028 | 93.0703 | 2.749 | 1.6556
5.8167 | 98.5451 | 92.7611 | 99.3892 | 93.0672 | 2.7492 | 1.6556
5.8208 | 98.5515 | 92.7646 | 99.3957 | 93.0707 | 2.7495 | 1.6556
5.825 | 98.5597 | 92.7701 | 99.404 | 93.0762 | 2.7498 | 1.6556
5.8292 | 98.5535 | 92.7653 | 99.398 | 93.0714 | 2.7501 | 1.6557
5.8333 | 98.5485 | 92.7594 | 99.3933 | 93.0656 | 2.7504 | 1.6557
5.8375 | 98.5594 | 92.7616 | 99.4042 | 93.0678 | 2.7506 | 1.6557
5.8417 | 98.569 | 92.7647 | 99.414 | 93.0708 | 2.7507 | 1.6556
5.8458 | 98.5624 | 92.767 | 99.4076 | 93.0731 | 2.7511 | 1.6557
5.85 | 98.5522 | 92.7679 | 99.3977 | 93.0741 | 2.7516 | 1.6558
5.8542 | 98.533 | 92.7646 | 99.3786 | 93.0708 | 2.7518 | 1.6558
5.8583 | 98.5169 | 92.76 | 99.3626 | 93.0661 | 2.752 | 1.6557
5.8625 | 98.5377 | 92.7645 | 99.3836 | 93.0706 | 2.7523 | 1.6557
5.8667 | 98.5621 | 92.7691 | 99.4081 | 93.0752 | 2.7525 | 1.6557
5.8708 | 98.5634 | 92.7668 | 99.4096 | 93.073 | 2.7529 | 1.6558
5.875 | 98.5606 | 92.7645 | 99.4071 | 93.0707 | 2.7532 | 1.6558
5.8792 | 98.545 | 92.7627 | 99.3917 | 93.0689 | 2.7535 | 1.6557
5.8833 | 98.5285 | 92.7622 | 99.3753 | 93.0683 | 2.7537 | 1.6557
5.8875 | 98.5366 | 92.7628 | 99.3835 | 93.0689 | 2.754 | 1.6558
5.8917 | 98.5481 | 92.7635 | 99.3952 | 93.0697 | 2.7542 | 1.6558
5.8958 | 98.552 | 92.7643 | 99.3993 | 93.0705 | 2.7545 | 1.6558
5.9 | 98.5543 | 92.7648 | 99.4018 | 93.071 | 2.7549 | 1.6558
5.9042 | 98.5422 | 92.7636 | 99.3898 | 93.0698 | 2.7551 | 1.6558
5.9083 | 98.528 | 92.7617 | 99.3758 | 93.0679 | 2.7554 | 1.6558
5.9125 | 98.5322 | 92.7622 | 99.3803 | 93.0684 | 2.7557 | 1.6558
5.9167 | 98.5403 | 92.7632 | 99.3884 | 93.0694 | 2.7559 | 1.6558
5.9208 | 98.5484 | 92.7637 | 99.3967 | 93.0699 | 2.7562 | 1.6558
5.925 | 98.5557 | 92.7641 | 99.4042 | 93.0703 | 2.7565 | 1.6558
5.9292 | 98.5468 | 92.763 | 99.3955 | 93.0692 | 2.7568 | 1.6558
5.9333 | 98.5348 | 92.7619 | 99.3837 | 93.0681 | 2.757 | 1.6558
5.9375 | 98.5274 | 92.7617 | 99.3764 | 93.0679 | 2.7573 | 1.6558
5.9417 | 98.5274 | 92.7618 | 99.3766 | 93.068 | 2.7576 | 1.6559
5.9458 | 98.5374 | 92.762 | 99.3867 | 93.0682 | 2.7578 | 1.6558
5.95 | 98.5482 | 92.7621 | 99.3978 | 93.0683 | 2.7581 | 1.6558
5.9542 | 98.5428 | 92.7635 | 99.3925 | 93.0697 | 2.7585 | 1.6558
5.9583 | 98.5343 | 92.7646 | 99.3842 | 93.0708 | 2.7588 | 1.6559
5.9625 | 98.5282 | 92.7604 | 99.3782 | 93.0666 | 2.759 | 1.6559
5.9667 | 98.5219 | 92.7563 | 99.372 | 93.0625 | 2.7592 | 1.6559
5.9708 | 98.5391 | 92.7618 | 99.3895 | 93.068 | 2.7595 | 1.6559
5.975 | 98.5537 | 92.7676 | 99.4042 | 93.0738 | 2.7597 | 1.6558
5.9792 | 98.5424 | 92.7631 | 99.3931 | 93.0693 | 2.7601 | 1.6559
5.9833 | 98.5293 | 92.7577 | 99.3802 | 93.0639 | 2.7604 | 1.656
5.9875 | 98.5339 | 92.7582 | 99.3849 | 93.0644 | 2.7605 | 1.6559
5.9917 | 98.5402 | 92.76 | 99.3913 | 93.0662 | 2.7606 | 1.6558
5.9958 | 98.5441 | 92.763 | 99.3954 | 93.0692 | 2.761 | 1.6559
6 | 98.5496 | 92.7656 | 99.4011 | 93.0719 | 2.7614 | 1.656
6.0042 | 98.537 | 92.7598 | 99.3886 | 93.0661 | 2.7616 | 1.656
6.0083 | 98.5233 | 92.7538 | 99.375 | 93.06 | 2.7617 | 1.6559
6.0125 | 98.5368 | 92.7585 | 99.3887 | 93.0647 | 2.7619 | 1.6559
6.0167 | 98.5514 | 92.7651 | 99.4034 | 93.0713 | 2.7622 | 1.6559
6.0208 | 98.546 | 92.7615 | 99.3981 | 93.0678 | 2.7625 | 1.656
6.025 | 98.5389 | 92.7569 | 99.3912 | 93.0631 | 2.7627 | 1.656
6.0292 | 98.5365 | 92.757 | 99.3889 | 93.0632 | 2.7629 | 1.656
6.0333 | 98.5331 | 92.7576 | 99.3855 | 93.0639 | 2.763 | 1.6559
6.0375 | 98.532 | 92.7601 | 99.3847 | 93.0664 | 2.7634 | 1.656
6.0417 | 98.5309 | 92.7633 | 99.3839 | 93.0695 | 2.7637 | 1.656
6.0458 | 98.5192 | 92.7588 | 99.3723 | 93.065 | 2.7639 | 1.656
6.05 | 98.5103 | 92.7532 | 99.3635 | 93.0595 | 2.7642 | 1.656
6.0542 | 98.5295 | 92.7569 | 99.3829 | 93.0631 | 2.7643 | 1.656
6.0583 | 98.5496 | 92.7614 | 99.4031 | 93.0676 | 2.7645 | 1.656
6.0625 | 98.5441 | 92.7616 | 99.3978 | 93.0678 | 2.7649 | 1.656
6.0667 | 98.5336 | 92.7603 | 99.3875 | 93.0666 | 2.7653 | 1.6561
6.0708 | 98.5136 | 92.7582 | 99.3676 | 93.0645 | 2.7655 | 1.656
6.075 | 98.4953 | 92.7559 | 99.3494 | 93.0621 | 2.7656 | 1.656
6.0792 | 98.5111 | 92.7589 | 99.3654 | 93.0652 | 2.7659 | 1.656
6.0833 | 98.5318 | 92.7619 | 99.3862 | 93.0682 | 2.7662 | 1.6561
6.0875 | 98.5365 | 92.76 | 99.3912 | 93.0663 | 2.7665 | 1.6561
6.0917 | 98.5384 | 92.7583 | 99.3932 | 93.0646 | 2.7668 | 1.656
6.0958 | 98.5265 | 92.7575 | 99.3814 | 93.0637 | 2.767 | 1.656
6.1 | 98.512 | 92.7574 | 99.3671 | 93.0637 | 2.7672 | 1.6561
6.1042 | 98.5148 | 92.757 | 99.37 | 93.0632 | 2.7674 | 1.6561
6.1083 | 98.5209 | 92.7567 | 99.3762 | 93.063 | 2.7677 | 1.6561
6.1125 | 98.5263 | 92.7583 | 99.3818 | 93.0645 | 2.7679 | 1.6561
6.1167 | 98.531 | 92.7596 | 99.3867 | 93.0658 | 2.7682 | 1.6561
6.1208 | 98.521 | 92.7585 | 99.3769 | 93.0648 | 2.7685 | 1.6561
6.125 | 98.5085 | 92.7565 | 99.3646 | 93.0628 | 2.7688 | 1.6561
6.1292 | 98.5082 | 92.7569 | 99.3644 | 93.0632 | 2.769 | 1.6561
6.1333 | 98.5129 | 92.7578 | 99.3692 | 93.064 | 2.7692 | 1.6561
6.1375 | 98.5225 | 92.7579 | 99.379 | 93.0642 | 2.7695 | 1.6561
6.1417 | 98.532 | 92.758 | 99.3886 | 93.0643 | 2.7697 | 1.6561
6.1458 | 98.5254 | 92.7579 | 99.3822 | 93.0642 | 2.77 | 1.6561
6.15 | 98.5153 | 92.7579 | 99.3723 | 93.0642 | 2.7702 | 1.6561
6.1542 | 98.5061 | 92.7562 | 99.3633 | 93.0625 | 2.7705 | 1.6561
6.1583 | 98.5022 | 92.7547 | 99.3595 | 93.061 | 2.7707 | 1.6562
6.1625 | 98.5145 | 92.7566 | 99.3718 | 93.0629 | 2.7709 | 1.6561
6.1667 | 98.5267 | 92.7587 | 99.3842 | 93.065 | 2.7711 | 1.6561
6.1708 | 98.5198 | 92.7586 | 99.3775 | 93.0649 | 2.7715 | 1.6561
6.175 | 98.5104 | 92.7577 | 99.3684 | 93.064 | 2.7718 | 1.6562
6.1792 | 98.5095 | 92.7546 | 99.3675 | 93.0609 | 2.7719 | 1.6561
6.1833 | 98.5075 | 92.752 | 99.3655 | 93.0583 | 2.7721 | 1.6561
6.1875 | 98.5203 | 92.7575 | 99.3786 | 93.0638 | 2.7724 | 1.6561
6.1917 | 98.5316 | 92.7632 | 99.3901 | 93.0695 | 2.7727 | 1.6561
6.1958 | 98.5186 | 92.757 | 99.3772 | 93.0633 | 2.7729 | 1.6562
6.2 | 98.5044 | 92.75 | 99.3631 | 93.0564 | 2.7731 | 1.6562
6.2042 | 98.5141 | 92.7535 | 99.373 | 93.0598 | 2.7733 | 1.6561
6.2083 | 98.5263 | 92.7586 | 99.3851 | 93.0649 | 2.7733 | 1.6561
6.2125 | 98.5229 | 92.7581 | 99.382 | 93.0644 | 2.7737 | 1.6562
6.2167 | 98.5208 | 92.7567 | 99.3802 | 93.0631 | 2.7741 | 1.6563
6.2208 | 98.5134 | 92.7537 | 99.3728 | 93.0601 | 2.7742 | 1.6562
6.225 | 98.5048 | 92.7509 | 99.3642 | 93.0571 | 2.7742 | 1.6561
6.2292 | 98.5137 | 92.7552 | 99.3733 | 93.0615 | 2.7745 | 1.6562
6.2333 | 98.5229 | 92.7608 | 99.3827 | 93.0672 | 2.7748 | 1.6562
6.2375 | 98.5136 | 92.7559 | 99.3736 | 93.0622 | 2.775 | 1.6562
6.2417 | 98.5033 | 92.7498 | 99.3634 | 93.0561 | 2.7752 | 1.6562
6.2458 | 98.5117 | 92.7526 | 99.3718 | 93.0589 | 2.7754 | 1.6562
6.25 | 98.5198 | 92.7561 | 99.3801 | 93.0624 | 2.7755 | 1.6562
6.2542 | 98.5139 | 92.7568 | 99.3743 | 93.0631 | 2.7759 | 1.6562
6.2583 | 98.5058 | 92.7571 | 99.3664 | 93.0635 | 2.7762 | 1.6562
6.2625 | 98.4903 | 92.754 | 99.3511 | 93.0603 | 2.7764 | 1.6562
6.2667 | 98.4783 | 92.7502 | 99.3392 | 93.0565 | 2.7766 | 1.6562
6.2708 | 98.4995 | 92.7537 | 99.3605 | 93.06 | 2.7768 | 1.6562
6.275 | 98.5235 | 92.7578 | 99.3847 | 93.0641 | 2.777 | 1.6562
6.2792 | 98.5222 | 92.7568 | 99.3835 | 93.0631 | 2.7773 | 1.6562
6.2833 | 98.5155 | 92.7548 | 99.377 | 93.0612 | 2.7776 | 1.6563
6.2875 | 98.4978 | 92.7538 | 99.3595 | 93.0602 | 2.7778 | 1.6563
6.2917 | 98.4795 | 92.7532 | 99.3412 | 93.0595 | 2.7779 | 1.6562
6.2958 | 98.4876 | 92.7546 | 99.3495 | 93.0609 | 2.7782 | 1.6562
6.3 | 98.501 | 92.7557 | 99.363 | 93.0621 | 2.7784 | 1.6563
6.3042 | 98.5082 | 92.7549 | 99.3704 | 93.0612 | 2.7787 | 1.6563
6.3083 | 98.5142 | 92.7544 | 99.3766 | 93.0608 | 2.7789 | 1.6562
6.3125 | 98.5059 | 92.754 | 99.3684 | 93.0603 | 2.7791 | 1.6563
6.3167 | 98.4942 | 92.7537 | 99.3568 | 93.0601 | 2.7794 | 1.6563
6.3208 | 98.4929 | 92.7528 | 99.3556 | 93.0591 | 2.7796 | 1.6563
6.325 | 98.4949 | 92.7522 | 99.3578 | 93.0585 | 2.7797 | 1.6563
6.3292 | 98.5015 | 92.754 | 99.3645 | 93.0603 | 2.78 | 1.6563
6.3333 | 98.5078 | 92.7555 | 99.371 | 93.0619 | 2.7802 | 1.6563
6.3375 | 98.4992 | 92.7547 | 99.3626 | 93.061 | 2.7805 | 1.6563
6.3417 | 98.4881 | 92.753 | 99.3516 | 93.0594 | 2.7807 | 1.6563
6.3458 | 98.4846 | 92.753 | 99.3483 | 93.0593 | 2.7809 | 1.6563
6.35 | 98.4865 | 92.7534 | 99.3502 | 93.0597 | 2.7811 | 1.6563
6.3542 | 98.4978 | 92.7537 | 99.3616 | 93.0601 | 2.7814 | 1.6563
6.3583 | 98.5089 | 92.7541 | 99.373 | 93.0604 | 2.7816 | 1.6563
6.3625 | 98.5033 | 92.7542 | 99.3675 | 93.0605 | 2.7819 | 1.6563
6.3667 | 98.4941 | 92.7545 | 99.3585 | 93.0609 | 2.7821 | 1.6563
6.3708 | 98.4867 | 92.752 | 99.3511 | 93.0583 | 2.7823 | 1.6563
6.375 | 98.4818 | 92.7496 | 99.3464 | 93.056 | 2.7824 | 1.6563
6.3792 | 98.4938 | 92.7531 | 99.3584 | 93.0595 | 2.7827 | 1.6563
6.3833 | 98.5054 | 92.7569 | 99.3702 | 93.0632 | 2.7829 | 1.6563
6.3875 | 98.496 | 92.7545 | 99.3611 | 93.0609 | 2.7832 | 1.6563
6.3917 | 98.4852 | 92.7513 | 99.3504 | 93.0576 | 2.7835 | 1.6564
6.3958 | 98.4906 | 92.7506 | 99.3558 | 93.0569 | 2.7835 | 1.6563
6.4 | 98.4949 | 92.7508 | 99.3602 | 93.0571 | 2.7836 | 1.6563
6.4042 | 98.5011 | 92.7545 | 99.3665 | 93.0609 | 2.7839 | 1.6563
6.4083 | 98.5065 | 92.7579 | 99.3722 | 93.0643 | 2.7842 | 1.6564
6.4125 | 98.4949 | 92.752 | 99.3607 | 93.0584 | 2.7843 | 1.6564
6.4167 | 98.4824 | 92.7457 | 99.3482 | 93.052 | 2.7845 | 1.6564
6.4208 | 98.4932 | 92.751 | 99.3591 | 93.0573 | 2.7847 | 1.6563
6.425 | 98.5064 | 92.7578 | 99.3725 | 93.0641 | 2.7848 | 1.6563
6.4292 | 98.497 | 92.754 | 99.3631 | 93.0604 | 2.7851 | 1.6564
6.4333 | 98.4886 | 92.7492 | 99.3549 | 93.0556 | 2.7854 | 1.6564
6.4375 | 98.4895 | 92.7496 | 99.356 | 93.056 | 2.7855 | 1.6564
6.4417 | 98.4898 | 92.7507 | 99.3563 | 93.057 | 2.7855 | 1.6563
6.4458 | 98.4923 | 92.7532 | 99.3589 | 93.0596 | 2.7858 | 1.6564
6.45 | 98.4934 | 92.7562 | 99.3603 | 93.0625 | 2.7862 | 1.6564
6.4542 | 98.4814 | 92.7516 | 99.3483 | 93.058 | 2.7863 | 1.6564
6.4583 | 98.4694 | 92.7462 | 99.3365 | 93.0526 | 2.7864 | 1.6563
6.4625 | 98.4853 | 92.75 | 99.3523 | 93.0564 | 2.7866 | 1.6564
6.4667 | 98.5025 | 92.7547 | 99.3698 | 93.0611 | 2.7868 | 1.6564
6.4708 | 98.4957 | 92.7539 | 99.3632 | 93.0603 | 2.7871 | 1.6564
6.475 | 98.4851 | 92.7522 | 99.3527 | 93.0586 | 2.7874 | 1.6564
6.4792 | 98.4684 | 92.7506 | 99.3361 | 93.057 | 2.7876 | 1.6564
6.4833 | 98.4544 | 92.749 | 99.3222 | 93.0554 | 2.7877 | 1.6564
6.4875 | 98.4716 | 92.7513 | 99.3395 | 93.0577 | 2.7879 | 1.6564
6.4917 | 98.493 | 92.7538 | 99.3611 | 93.0602 | 2.7881 | 1.6564
6.4958 | 98.4969 | 92.7528 | 99.3651 | 93.0592 | 2.7884 | 1.6564
6.5 | 98.4964 | 92.7513 | 99.3649 | 93.0577 | 2.7886 | 1.6564
6.5042 | 98.483 | 92.751 | 99.3515 | 93.0573 | 2.7888 | 1.6564
6.5083 | 98.4664 | 92.7511 | 99.335 | 93.0575 | 2.789 | 1.6564
6.5125 | 98.467 | 92.7512 | 99.3357 | 93.0576 | 2.7892 | 1.6564
6.5167 | 98.4724 | 92.751 | 99.3413 | 93.0574 | 2.7894 | 1.6564
6.5208 | 98.4806 | 92.7512 | 99.3496 | 93.0576 | 2.7896 | 1.6564
6.525 | 98.4893 | 92.7519 | 99.3585 | 93.0583 | 2.7898 | 1.6564
6.5292 | 98.4835 | 92.7515 | 99.3528 | 93.0579 | 2.79 | 1.6564
6.5333 | 98.4743 | 92.7508 | 99.3437 | 93.0572 | 2.7903 | 1.6565
6.5375 | 98.4709 | 92.7497 | 99.3404 | 93.0561 | 2.7904 | 1.6564
6.5417 | 98.4708 | 92.7492 | 99.3404 | 93.0556 | 2.7905 | 1.6564
6.5458 | 98.4785 | 92.7511 | 99.3482 | 93.0574 | 2.7908 | 1.6564
6.55 | 98.4859 | 92.7525 | 99.3557 | 93.0589 | 2.791 | 1.6565
6.5542 | 98.478 | 92.7518 | 99.3481 | 93.0582 | 2.7912 | 1.6564
6.5583 | 98.4676 | 92.7505 | 99.3377 | 93.0569 | 2.7914 | 1.6564
6.5625 | 98.4629 | 92.75 | 99.3332 | 93.0564 | 2.7916 | 1.6564
6.5667 | 98.4628 | 92.7498 | 99.3331 | 93.0562 | 2.7918 | 1.6565
6.5708 | 98.475 | 92.7508 | 99.3455 | 93.0572 | 2.792 | 1.6564
6.575 | 98.487 | 92.7519 | 99.3576 | 93.0583 | 2.7922 | 1.6564
6.5792 | 98.4809 | 92.7514 | 99.3516 | 93.0578 | 2.7925 | 1.6564
6.5833 | 98.4719 | 92.751 | 99.3428 | 93.0574 | 2.7927 | 1.6565
6.5875 | 98.4686 | 92.7487 | 99.3396 | 93.0551 | 2.7928 | 1.6565
6.5917 | 98.4661 | 92.7468 | 99.3371 | 93.0532 | 2.7929 | 1.6565
6.5958 | 98.4749 | 92.7509 | 99.346 | 93.0573 | 2.7931 | 1.6564
6.6 | 98.4833 | 92.7551 | 99.3547 | 93.0615 | 2.7934 | 1.6564
6.6042 | 98.4725 | 92.751 | 99.3439 | 93.0574 | 2.7936 | 1.6565
6.6083 | 98.4609 | 92.746 | 99.3326 | 93.0524 | 2.7938 | 1.6565
6.6125 | 98.4712 | 92.7481 | 99.3429 | 93.0545 | 2.7939 | 1.6565
6.6167 | 98.481 | 92.7515 | 99.3527 | 93.0579 | 2.7939 | 1.6564
6.6208 | 98.4797 | 92.7521 | 99.3516 | 93.0586 | 2.7942 | 1.6565
6.625 | 98.4781 | 92.7521 | 99.3502 | 93.0585 | 2.7945 | 1.6565
6.6292 | 98.4718 | 92.7482 | 99.344 | 93.0546 | 2.7946 | 1.6565
6.6333 | 98.4647 | 92.7444 | 99.3368 | 93.0508 | 2.7946 | 1.6564
6.6375 | 98.4723 | 92.7498 | 99.3446 | 93.0562 | 2.7949 | 1.6565
6.6417 | 98.4819 | 92.7561 | 99.3543 | 93.0625 | 2.7951 | 1.6565
6.6458 | 98.4683 | 92.7506 | 99.3408 | 93.057 | 2.7953 | 1.6565
6.65 | 98.4557 | 92.7439 | 99.3283 | 93.0503 | 2.7955 | 1.6565
6.6542 | 98.4655 | 92.7473 | 99.3382 | 93.0537 | 2.7956 | 1.6565
6.6583 | 98.4757 | 92.7515 | 99.3485 | 93.0579 | 2.7957 | 1.6564
6.6625 | 98.4728 | 92.7516 | 99.3458 | 93.058 | 2.796 | 1.6565
6.6667 | 98.4666 | 92.7513 | 99.3398 | 93.0578 | 2.7963 | 1.6566
6.6708 | 98.4534 | 92.7485 | 99.3267 | 93.0549 | 2.7964 | 1.6565
6.675 | 98.441 | 92.7453 | 99.3142 | 93.0517 | 2.7965 | 1.6565
6.6792 | 98.4588 | 92.7485 | 99.3322 | 93.055 | 2.7967 | 1.6565
6.6833 | 98.4799 | 92.7524 | 99.3534 | 93.0588 | 2.7969 | 1.6565
6.6875 | 98.476 | 92.751 | 99.3497 | 93.0575 | 2.7971 | 1.6565
6.6917 | 98.4679 | 92.7489 | 99.3418 | 93.0553 | 2.7974 | 1.6565
6.6958 | 98.4522 | 92.7485 | 99.3262 | 93.0549 | 2.7975 | 1.6565
6.7 | 98.4376 | 92.7485 | 99.3116 | 93.0549 | 2.7977 | 1.6565
6.7042 | 98.4471 | 92.7493 | 99.3213 | 93.0557 | 2.7979 | 1.6565
6.7083 | 98.4617 | 92.75 | 99.3359 | 93.0564 | 2.798 | 1.6565
6.7125 | 98.4698 | 92.7497 | 99.3442 | 93.0561 | 2.7983 | 1.6565
6.7167 | 98.4756 | 92.7493 | 99.3502 | 93.0557 | 2.7985 | 1.6565
6.7208 | 98.4666 | 92.7492 | 99.3413 | 93.0556 | 2.7987 | 1.6565
6.725 | 98.4529 | 92.7493 | 99.3277 | 93.0557 | 2.7988 | 1.6565
6.7292 | 98.4482 | 92.7485 | 99.3231 | 93.0549 | 2.799 | 1.6565
6.7333 | 98.4477 | 92.7477 | 99.3227 | 93.0542 | 2.7992 | 1.6566
6.7375 | 98.4558 | 92.7488 | 99.3309 | 93.0552 | 2.7993 | 1.6565
6.7417 | 98.4653 | 92.7502 | 99.3404 | 93.0566 | 2.7995 | 1.6565
6.7458 | 98.4604 | 92.7497 | 99.3358 | 93.0561 | 2.7997 | 1.6565
6.75 | 98.4528 | 92.7486 | 99.3283 | 93.055 | 2.8 | 1.6566
6.7542 | 98.4492 | 92.7476 | 99.3247 | 93.054 | 2.8001 | 1.6565
6.7583 | 98.4488 | 92.7473 | 99.3244 | 93.0537 | 2.8002 | 1.6565
6.7625 | 98.4576 | 92.749 | 99.3333 | 93.0554 | 2.8004 | 1.6565
6.7667 | 98.4657 | 92.7503 | 99.3415 | 93.0568 | 2.8006 | 1.6566
6.7708 | 98.4579 | 92.7496 | 99.3338 | 93.056 | 2.8008 | 1.6566
6.775 | 98.4474 | 92.7486 | 99.3236 | 93.055 | 2.801 | 1.6565
6.7792 | 98.4435 | 92.7477 | 99.3198 | 93.0542 | 2.8012 | 1.6565
6.7833 | 98.4429 | 92.7471 | 99.3192 | 93.0536 | 2.8013 | 1.6566
6.7875 | 98.4542 | 92.7489 | 99.3306 | 93.0553 | 2.8015 | 1.6566
6.7917 | 98.4653 | 92.7507 | 99.3418 | 93.0572 | 2.8017 | 1.6565
6.7958 | 98.4583 | 92.7492 | 99.3349 | 93.0556 | 2.8019 | 1.6566
6.8 | 98.4492 | 92.7475 | 99.326 | 93.0539 | 2.8021 | 1.6566
6.8042 | 98.4515 | 92.7465 | 99.3283 | 93.0529 | 2.8022 | 1.6566
6.8083 | 98.4532 | 92.7462 | 99.3301 | 93.0526 | 2.8022 | 1.6565
6.8125 | 98.4564 | 92.7495 | 99.3335 | 93.056 | 2.8025 | 1.6565
6.8167 | 98.4595 | 92.7526 | 99.3367 | 93.0591 | 2.8027 | 1.6566
6.8208 | 98.4498 | 92.748 | 99.3271 | 93.0545 | 2.8028 | 1.6566
6.825 | 98.4398 | 92.7427 | 99.3172 | 93.0491 | 2.803 | 1.6566
6.8292 | 98.4517 | 92.747 | 99.3291 | 93.0534 | 2.8031 | 1.6565
6.8333 | 98.4637 | 92.7526 | 99.3412 | 93.059 | 2.8032 | 1.6565
6.8375 | 98.4557 | 92.75 | 99.3333 | 93.0564 | 2.8035 | 1.6566
6.8417 | 98.4477 | 92.7463 | 99.3256 | 93.0528 | 2.8037 | 1.6567
6.8458 | 98.4495 | 92.7456 | 99.3274 | 93.0521 | 2.8037 | 1.6566
6.85 | 98.4508 | 92.7456 | 99.3286 | 93.052 | 2.8037 | 1.6565
6.8542 | 98.4529 | 92.7492 | 99.3309 | 93.0556 | 2.804 | 1.6566
6.8583 | 98.4555 | 92.7531 | 99.3336 | 93.0596 | 2.8043 | 1.6566
6.8625 | 98.44 | 92.7477 | 99.3182 | 93.0541 | 2.8044 | 1.6566
6.8667 | 98.4257 | 92.7414 | 99.304 | 93.0479 | 2.8045 | 1.6566
6.8708 | 98.4414 | 92.7462 | 99.3198 | 93.0527 | 2.8047 | 1.6566
6.875 | 98.4592 | 92.7518 | 99.3376 | 93.0582 | 2.8048 | 1.6566
6.8792 | 98.4543 | 92.7499 | 99.333 | 93.0563 | 2.805 | 1.6566
6.8833 | 98.4445 | 92.7472 | 99.3234 | 93.0537 | 2.8053 | 1.6566
6.8875 | 98.4319 | 92.7465 | 99.3108 | 93.053 | 2.8054 | 1.6566
6.8917 | 98.4197 | 92.7459 | 99.2986 | 93.0524 | 2.8055 | 1.6566
6.8958 | 98.4342 | 92.7475 | 99.3132 | 93.054 | 2.8057 | 1.6566
6.9 | 98.453 | 92.7494 | 99.3322 | 93.0558 | 2.8059 | 1.6566
6.9042 | 98.4542 | 92.7485 | 99.3335 | 93.055 | 2.8061 | 1.6566
6.9083 | 98.4522 | 92.7471 | 99.3316 | 93.0536 | 2.8063 | 1.6566
6.9125 | 98.4391 | 92.7472 | 99.3186 | 93.0537 | 2.8064 | 1.6566
6.9167 | 98.4249 | 92.7477 | 99.3046 | 93.0542 | 2.8066 | 1.6566
6.9208 | 98.4265 | 92.7475 | 99.3063 | 93.0539 | 2.8068 | 1.6566
6.925 | 98.4328 | 92.747 | 99.3126 | 93.0534 | 2.8069 | 1.6566
6.9292 | 98.4432 | 92.7475 | 99.3232 | 93.0539 | 2.8071 | 1.6566
6.9333 | 98.4533 | 92.7482 | 99.3333 | 93.0547 | 2.8073 | 1.6566
6.9375 | 98.4479 | 92.748 | 99.328 | 93.0544 | 2.8074 | 1.6566
6.9417 | 98.4373 | 92.7476 | 99.3175 | 93.054 | 2.8076 | 1.6566
6.9458 | 98.4305 | 92.7466 | 99.3109 | 93.053 | 2.8077 | 1.6566
6.95 | 98.4272 | 92.7458 | 99.3076 | 93.0522 | 2.8079 | 1.6566
6.9542 | 98.4348 | 92.7472 | 99.3153 | 93.0537 | 2.808 | 1.6566
6.9583 | 98.4435 | 92.7488 | 99.3241 | 93.0553 | 2.8082 | 1.6566
6.9625 | 98.4381 | 92.7482 | 99.3189 | 93.0546 | 2.8084 | 1.6566
6.9667 | 98.4309 | 92.747 | 99.3118 | 93.0534 | 2.8086 | 1.6567
6.9708 | 98.4284 | 92.7461 | 99.3093 | 93.0525 | 2.8087 | 1.6566
6.975 | 98.4289 | 92.7458 | 99.3099 | 93.0523 | 2.8088 | 1.6566
6.9792 | 98.4384 | 92.7476 | 99.3196 | 93.054 | 2.809 | 1.6566
6.9833 | 98.4469 | 92.7489 | 99.3281 | 93.0554 | 2.8092 | 1.6566
6.9875 | 98.4388 | 92.7478 | 99.3201 | 93.0543 | 2.8094 | 1.6566
6.9917 | 98.4282 | 92.7467 | 99.3096 | 93.0531 | 2.8095 | 1.6566
6.9958 | 98.4267 | 92.746 | 99.3082 | 93.0524 | 2.8096 | 1.6566
7 | 98.427 | 92.7456 | 99.3086 | 93.052 | 2.8097 | 1.6566
7.0042 | 98.435 | 92.7476 | 99.3167 | 93.0541 | 2.8099 | 1.6566
7.0083 | 98.4432 | 92.7499 | 99.3251 | 93.0563 | 2.8101 | 1.6566
7.0125 | 98.4359 | 92.7473 | 99.3179 | 93.0538 | 2.8103 | 1.6566
7.0167 | 98.4276 | 92.7443 | 99.3096 | 93.0508 | 2.8104 | 1.6567
7.0208 | 98.4346 | 92.7452 | 99.3167 | 93.0517 | 2.8105 | 1.6566
7.025 | 98.4406 | 92.7471 | 99.3227 | 93.0536 | 2.8105 | 1.6566
7.0292 | 98.4373 | 92.7485 | 99.3195 | 93.0549 | 2.8108 | 1.6566
7.0333 | 98.4339 | 92.7492 | 99.3163 | 93.0557 | 2.811 | 1.6567
7.0375 | 98.4285 | 92.7456 | 99.3109 | 93.0521 | 2.8111 | 1.6567
7.0417 | 98.4232 | 92.7417 | 99.3056 | 93.0482 | 2.8111 | 1.6566
7.0458 | 98.4328 | 92.7468 | 99.3153 | 93.0532 | 2.8113 | 1.6566
7.05 | 98.4428 | 92.7528 | 99.3256 | 93.0592 | 2.8115 | 1.6566
7.0542 | 98.4301 | 92.7478 | 99.3129 | 93.0543 | 2.8117 | 1.6567
7.0583 | 98.4179 | 92.7419 | 99.3008 | 93.0483 | 2.8118 | 1.6567
7.0625 | 98.4279 | 92.7443 | 99.3109 | 93.0507 | 2.8119 | 1.6566
7.0667 | 98.4383 | 92.7477 | 99.3213 | 93.0542 | 2.8119 | 1.6566
7.0708 | 98.4353 | 92.7486 | 99.3184 | 93.0551 | 2.8122 | 1.6566
7.075 | 98.4305 | 92.7492 | 99.3139 | 93.0557 | 2.8125 | 1.6567
7.0792 | 98.4156 | 92.7455 | 99.2989 | 93.052 | 2.8125 | 1.6567
7.0833 | 98.4015 | 92.7416 | 99.2849 | 93.048 | 2.8126 | 1.6566
7.0875 | 98.4183 | 92.7458 | 99.3018 | 93.0523 | 2.8128 | 1.6566
7.0917 | 98.4388 | 92.7506 | 99.3224 | 93.0571 | 2.8129 | 1.6567
7.0958 | 98.4357 | 92.748 | 99.3194 | 93.0545 | 2.8131 | 1.6567
7.1 | 98.4273 | 92.7446 | 99.3112 | 93.0511 | 2.8134 | 1.6567
7.1042 | 98.4162 | 92.7455 | 99.3001 | 93.052 | 2.8135 | 1.6567
7.1083 | 98.4047 | 92.7469 | 99.2887 | 93.0534 | 2.8136 | 1.6566
7.1125 | 98.4124 | 92.7466 | 99.2965 | 93.053 | 2.8137 | 1.6567
7.1167 | 98.4249 | 92.7462 | 99.309 | 93.0527 | 2.8139 | 1.6567
7.1208 | 98.431 | 92.7465 | 99.3153 | 93.053 | 2.814 | 1.6567
7.125 | 98.436 | 92.7467 | 99.3204 | 93.0532 | 2.8142 | 1.6566
7.1292 | 98.4261 | 92.7466 | 99.3106 | 93.053 | 2.8143 | 1.6567
7.1333 | 98.4133 | 92.7466 | 99.2979 | 93.0531 | 2.8145 | 1.6567
7.1375 | 98.409 | 92.746 | 99.2937 | 93.0524 | 2.8146 | 1.6567
7.1417 | 98.4089 | 92.7451 | 99.2935 | 93.0516 | 2.8147 | 1.6566
7.1458 | 98.4195 | 92.7461 | 99.3043 | 93.0526 | 2.8149 | 1.6567
7.15 | 98.4307 | 92.7474 | 99.3157 | 93.0539 | 2.8151 | 1.6567
7.1542 | 98.4274 | 92.747 | 99.3124 | 93.0535 | 2.8152 | 1.6567
7.1583 | 98.4192 | 92.7462 | 99.3044 | 93.0527 | 2.8154 | 1.6567
7.1625 | 98.4133 | 92.7452 | 99.2985 | 93.0517 | 2.8155 | 1.6567
7.1667 | 98.4101 | 92.7446 | 99.2954 | 93.0511 | 2.8156 | 1.6567
7.1708 | 98.4171 | 92.7463 | 99.3025 | 93.0528 | 2.8157 | 1.6567
7.175 | 98.4246 | 92.7478 | 99.31 | 93.0543 | 2.8159 | 1.6566
7.1792 | 98.4179 | 92.7469 | 99.3035 | 93.0534 | 2.8161 | 1.6567
7.1833 | 98.4102 | 92.7456 | 99.2958 | 93.0521 | 2.8163 | 1.6567
7.1875 | 98.4096 | 92.745 | 99.2953 | 93.0514 | 2.8164 | 1.6567
7.1917 | 98.4114 | 92.7448 | 99.2971 | 93.0513 | 2.8164 | 1.6566
7.1958 | 98.4205 | 92.7466 | 99.3064 | 93.0531 | 2.8166 | 1.6567
7.2 | 98.4284 | 92.7481 | 99.3144 | 93.0546 | 2.8168 | 1.6567
7.2042 | 98.4203 | 92.7464 | 99.3065 | 93.0529 | 2.8169 | 1.6567
7.2083 | 98.4102 | 92.7447 | 99.2964 | 93.0512 | 2.817 | 1.6567
7.2125 | 98.4118 | 92.7448 | 99.2981 | 93.0513 | 2.8171 | 1.6567
7.2167 | 98.4141 | 92.7452 | 99.3004 | 93.0517 | 2.8172 | 1.6567
7.2208 | 98.4168 | 92.7469 | 99.3032 | 93.0534 | 2.8174 | 1.6567
7.225 | 98.42 | 92.7485 | 99.3065 | 93.055 | 2.8176 | 1.6567
7.2292 | 98.4143 | 92.7456 | 99.3008 | 93.0521 | 2.8177 | 1.6567
7.2333 | 98.4084 | 92.7421 | 99.295 | 93.0486 | 2.8178 | 1.6567
7.2375 | 98.4179 | 92.7448 | 99.3046 | 93.0513 | 2.8179 | 1.6567
7.2417 | 98.4264 | 92.7485 | 99.3132 | 93.055 | 2.8179 | 1.6566
7.2458 | 98.4171 | 92.7474 | 99.304 | 93.0539 | 2.8182 | 1.6567
7.25 | 98.4078 | 92.7453 | 99.2949 | 93.0518 | 2.8184 | 1.6568
7.2542 | 98.409 | 92.7439 | 99.296 | 93.0504 | 2.8184 | 1.6567
7.2583 | 98.4106 | 92.7428 | 99.2976 | 93.0493 | 2.8184 | 1.6566
7.2625 | 98.4154 | 92.7469 | 99.3025 | 93.0534 | 2.8186 | 1.6567
7.2667 | 98.4201 | 92.7514 | 99.3074 | 93.0579 | 2.8189 | 1.6567
7.2708 | 98.4054 | 92.7458 | 99.2927 | 93.0524 | 2.819 | 1.6567
7.275 | 98.3913 | 92.7395 | 99.2787 | 93.046 | 2.8191 | 1.6567
7.2792 | 98.407 | 92.7439 | 99.2945 | 93.0504 | 2.8191 | 1.6567
7.2833 | 98.4243 | 92.7493 | 99.3119 | 93.0558 | 2.8192 | 1.6567
7.2875 | 98.4188 | 92.7477 | 99.3065 | 93.0542 | 2.8195 | 1.6567
7.2917 | 98.4096 | 92.7453 | 99.2975 | 93.0518 | 2.8197 | 1.6568
7.2958 | 98.3967 | 92.7442 | 99.2846 | 93.0507 | 2.8198 | 1.6567
7.3 | 98.3841 | 92.7434 | 99.272 | 93.0498 | 2.8198 | 1.6566
7.3042 | 98.397 | 92.7457 | 99.285 | 93.0522 | 2.82 | 1.6567
7.3083 | 98.4148 | 92.7482 | 99.3029 | 93.0546 | 2.8202 | 1.6567
7.3125 | 98.4161 | 92.7462 | 99.3043 | 93.0527 | 2.8203 | 1.6567
7.3167 | 98.4132 | 92.7438 | 99.3016 | 93.0502 | 2.8204 | 1.6567
7.3208 | 98.4043 | 92.7452 | 99.2927 | 93.0517 | 2.8206 | 1.6567
7.325 | 98.3936 | 92.7471 | 99.2821 | 93.0536 | 2.8207 | 1.6567
7.3292 | 98.3941 | 92.7455 | 99.2826 | 93.052 | 2.8208 | 1.6567
7.3333 | 98.3988 | 92.7438 | 99.2874 | 93.0503 | 2.8209 | 1.6567
7.3375 | 98.4083 | 92.7452 | 99.297 | 93.0517 | 2.8211 | 1.6567
7.3417 | 98.4184 | 92.7469 | 99.3072 | 93.0533 | 2.8212 | 1.6567
7.3458 | 98.4113 | 92.7461 | 99.3002 | 93.0526 | 2.8214 | 1.6567
7.35 | 98.4002 | 92.7452 | 99.2892 | 93.0517 | 2.8215 | 1.6567
7.3542 | 98.3936 | 92.7447 | 99.2826 | 93.0512 | 2.8216 | 1.6567
7.3583 | 98.3902 | 92.7443 | 99.2794 | 93.0508 | 2.8217 | 1.6567
7.3625 | 98.3997 | 92.7454 | 99.2888 | 93.0518 | 2.8218 | 1.6567
7.3667 | 98.4097 | 92.7466 | 99.299 | 93.0531 | 2.822 | 1.6567
7.3708 | 98.4067 | 92.7462 | 99.2961 | 93.0527 | 2.8222 | 1.6567
7.375 | 98.4001 | 92.7452 | 99.2896 | 93.0517 | 2.8223 | 1.6567
7.3792 | 98.3966 | 92.7442 | 99.2861 | 93.0507 | 2.8224 | 1.6567
7.3833 | 98.3954 | 92.7439 | 99.285 | 93.0504 | 2.8225 | 1.6567
7.3875 | 98.4019 | 92.7457 | 99.2915 | 93.0522 | 2.8226 | 1.6567
7.3917 | 98.4081 | 92.7471 | 99.2979 | 93.0536 | 2.8227 | 1.6567
7.3958 | 98.4001 | 92.7458 | 99.2899 | 93.0523 | 2.8229 | 1.6567
7.4 | 98.3915 | 92.7443 | 99.2814 | 93.0509 | 2.8231 | 1.6568
7.4042 | 98.3931 | 92.7442 | 99.2832 | 93.0507 | 2.8231 | 1.6567
7.4083 | 98.3964 | 92.7444 | 99.2864 | 93.0509 | 2.8232 | 1.6567
7.4125 | 98.4031 | 92.746 | 99.2933 | 93.0525 | 2.8233 | 1.6567
7.4167 | 98.409 | 92.7473 | 99.2993 | 93.0538 | 2.8235 | 1.6567
7.4208 | 98.4022 | 92.7452 | 99.2925 | 93.0517 | 2.8236 | 1.6567
7.425 | 98.3937 | 92.743 | 99.2841 | 93.0494 | 2.8237 | 1.6567
7.4292 | 98.3984 | 92.7442 | 99.2888 | 93.0507 | 2.8238 | 1.6567
7.4333 | 98.4028 | 92.7459 | 99.2933 | 93.0524 | 2.8239 | 1.6567
7.4375 | 98.399 | 92.7463 | 99.2896 | 93.0528 | 2.824 | 1.6567
7.4417 | 98.396 | 92.7465 | 99.2867 | 93.053 | 2.8242 | 1.6567
7.4458 | 98.394 | 92.7441 | 99.2847 | 93.0506 | 2.8243 | 1.6567
7.45 | 98.3926 | 92.7414 | 99.2834 | 93.048 | 2.8243 | 1.6568
7.4542 | 98.4016 | 92.745 | 99.2925 | 93.0515 | 2.8244 | 1.6567
7.4583 | 98.4097 | 92.7494 | 99.3007 | 93.0559 | 2.8246 | 1.6567
7.4625 | 98.3962 | 92.7461 | 99.2873 | 93.0527 | 2.8247 | 1.6567
7.4667 | 98.3829 | 92.7419 | 99.274 | 93.0484 | 2.8249 | 1.6568
7.4708 | 98.391 | 92.743 | 99.2821 | 93.0495 | 2.8249 | 1.6567
7.475 | 98.4001 | 92.7449 | 99.2912 | 93.0514 | 2.8249 | 1.6566
7.4792 | 98.3996 | 92.7469 | 99.2909 | 93.0534 | 2.8251 | 1.6567
7.4833 | 98.3979 | 92.7486 | 99.2894 | 93.0552 | 2.8254 | 1.6568
7.4875 | 98.3838 | 92.7443 | 99.2753 | 93.0508 | 2.8255 | 1.6568
7.4917 | 98.3702 | 92.7395 | 99.2617 | 93.046 | 2.8255 | 1.6567
7.4958 | 98.387 | 92.7441 | 99.2786 | 93.0506 | 2.8256 | 1.6567
7.5 | 98.407 | 92.7495 | 99.2987 | 93.056 | 2.8257 | 1.6567
7.5042 | 98.4024 | 92.7464 | 99.2942 | 93.0529 | 2.8259 | 1.6568
7.5083 | 98.3934 | 92.7425 | 99.2853 | 93.049 | 2.8261 | 1.6568
7.5125 | 98.3833 | 92.7438 | 99.2752 | 93.0503 | 2.8262 | 1.6567
7.5167 | 98.3725 | 92.7455 | 99.2645 | 93.052 | 2.8262 | 1.6567
7.5208 | 98.3785 | 92.7454 | 99.2706 | 93.0519 | 2.8264 | 1.6567
7.525 | 98.3895 | 92.745 | 99.2817 | 93.0516 | 2.8265 | 1.6568
7.5292 | 98.396 | 92.7448 | 99.2882 | 93.0513 | 2.8266 | 1.6567
7.5333 | 98.4003 | 92.7444 | 99.2925 | 93.0509 | 2.8267 | 1.6567
7.5375 | 98.3933 | 92.7452 | 99.2856 | 93.0518 | 2.8269 | 1.6567
7.5417 | 98.3833 | 92.7463 | 99.2758 | 93.0528 | 2.827 | 1.6568
7.5458 | 98.3786 | 92.7445 | 99.2712 | 93.051 | 2.8271 | 1.6567
7.55 | 98.3773 | 92.7426 | 99.2699 | 93.0491 | 2.8272 | 1.6567
7.5542 | 98.3878 | 92.7446 | 99.2804 | 93.0511 | 2.8273 | 1.6567
7.5583 | 98.3998 | 92.7468 | 99.2925 | 93.0534 | 2.8274 | 1.6567
7.5625 | 98.3946 | 92.7456 | 99.2875 | 93.0521 | 2.8276 | 1.6567
7.5667 | 98.3854 | 92.7439 | 99.2783 | 93.0505 | 2.8277 | 1.6568
7.5708 | 98.3794 | 92.7438 | 99.2724 | 93.0504 | 2.8278 | 1.6568
7.575 | 98.3762 | 92.744 | 99.2692 | 93.0506 | 2.8278 | 1.6567
7.5792 | 98.3839 | 92.745 | 99.2769 | 93.0514 | 2.828 | 1.6567
7.5833 | 98.3915 | 92.7458 | 99.2846 | 93.0523 | 2.8281 | 1.6568
7.5875 | 98.3874 | 92.7454 | 99.2807 | 93.0519 | 2.8283 | 1.6568
7.5917 | 98.3813 | 92.7445 | 99.2746 | 93.051 | 2.8284 | 1.6567
7.5958 | 98.3809 | 92.7437 | 99.2743 | 93.0502 | 2.8284 | 1.6567
7.6 | 98.3822 | 92.7434 | 99.2757 | 93.0499 | 2.8285 | 1.6568
7.6042 | 98.3878 | 92.7452 | 99.2813 | 93.0518 | 2.8287 | 1.6567
7.6083 | 98.3928 | 92.7467 | 99.2864 | 93.0532 | 2.8288 | 1.6567
7.6125 | 98.3842 | 92.7449 | 99.2779 | 93.0514 | 2.8289 | 1.6568
7.6167 | 98.3754 | 92.743 | 99.2691 | 93.0495 | 2.829 | 1.6568
7.6208 | 98.3792 | 92.7437 | 99.273 | 93.0502 | 2.8291 | 1.6568
7.625 | 98.3837 | 92.7447 | 99.2775 | 93.0513 | 2.8291 | 1.6567
7.6292 | 98.3862 | 92.7456 | 99.28 | 93.0521 | 2.8293 | 1.6567
7.6333 | 98.3883 | 92.7462 | 99.2823 | 93.0528 | 2.8295 | 1.6568
7.6375 | 98.3843 | 92.7442 | 99.2784 | 93.0507 | 2.8295 | 1.6568
7.6417 | 98.3792 | 92.7418 | 99.2733 | 93.0483 | 2.8296 | 1.6567
7.6458 | 98.3858 | 92.7441 | 99.2799 | 93.0506 | 2.8297 | 1.6567
7.65 | 98.3913 | 92.7469 | 99.2855 | 93.0534 | 2.8298 | 1.6568
7.6542 | 98.3815 | 92.7457 | 99.2758 | 93.0522 | 2.8299 | 1.6568
7.6583 | 98.3726 | 92.744 | 99.267 | 93.0505 | 2.8301 | 1.6568
7.6625 | 98.3756 | 92.7431 | 99.27 | 93.0496 | 2.8301 | 1.6568
7.6667 | 98.3802 | 92.7422 | 99.2746 | 93.0487 | 2.8301 | 1.6568
7.6708 | 98.3863 | 92.7454 | 99.2808 | 93.0519 | 2.8303 | 1.6567
7.675 | 98.3911 | 92.749 | 99.2858 | 93.0555 | 2.8304 | 1.6567
7.6792 | 98.3763 | 92.7449 | 99.2709 | 93.0514 | 2.8305 | 1.6568
7.6833 | 98.3614 | 92.7398 | 99.2561 | 93.0463 | 2.8307 | 1.6568
7.6875 | 98.3744 | 92.7428 | 99.2692 | 93.0493 | 2.8307 | 1.6568
7.6917 | 98.3893 | 92.7469 | 99.284 | 93.0534 | 2.8307 | 1.6567
7.6958 | 98.3851 | 92.7465 | 99.2801 | 93.053 | 2.8309 | 1.6568
7.7 | 98.3787 | 92.7453 | 99.2738 | 93.0519 | 2.8312 | 1.6568
7.7042 | 98.367 | 92.7432 | 99.2621 | 93.0497 | 2.8312 | 1.6568
7.7083 | 98.3554 | 92.7413 | 99.2505 | 93.0478 | 2.8312 | 1.6567
7.7125 | 98.3687 | 92.7445 | 99.2639 | 93.051 | 2.8313 | 1.6567
7.7167 | 98.3862 | 92.748 | 99.2814 | 93.0545 | 2.8315 | 1.6568
7.7208 | 98.3857 | 92.745 | 99.281 | 93.0515 | 2.8316 | 1.6568
7.725 | 98.3811 | 92.7414 | 99.2765 | 93.0479 | 2.8317 | 1.6567
7.7292 | 98.3736 | 92.7439 | 99.2691 | 93.0504 | 2.8318 | 1.6567
7.7333 | 98.3643 | 92.7469 | 99.2599 | 93.0534 | 2.8319 | 1.6568
7.7375 | 98.363 | 92.7448 | 99.2586 | 93.0513 | 2.832 | 1.6568
7.7417 | 98.3662 | 92.7423 | 99.2619 | 93.0489 | 2.8321 | 1.6568
7.7458 | 98.3764 | 92.7439 | 99.2722 | 93.0504 | 2.8322 | 1.6568
7.75 | 98.3867 | 92.7457 | 99.2825 | 93.0522 | 2.8323 | 1.6567
7.7542 | 98.3812 | 92.7453 | 99.2771 | 93.0518 | 2.8325 | 1.6568
7.7583 | 98.372 | 92.7447 | 99.268 | 93.0512 | 2.8326 | 1.6568
7.7625 | 98.3655 | 92.7435 | 99.2616 | 93.05 | 2.8327 | 1.6568
7.7667 | 98.3616 | 92.7426 | 99.2576 | 93.0491 | 2.8327 | 1.6567
7.7708 | 98.3708 | 92.7443 | 99.2669 | 93.0509 | 2.8328 | 1.6568
7.775 | 98.3815 | 92.7463 | 99.2777 | 93.0528 | 2.8329 | 1.6568
7.7792 | 98.3771 | 92.7451 | 99.2734 | 93.0516 | 2.8331 | 1.6568
7.7833 | 98.3693 | 92.7433 | 99.2657 | 93.0498 | 2.8332 | 1.6568
7.7875 | 98.3661 | 92.7434 | 99.2625 | 93.0499 | 2.8332 | 1.6568
7.7917 | 98.3651 | 92.7439 | 99.2615 | 93.0505 | 2.8333 | 1.6568
7.7958 | 98.3708 | 92.7447 | 99.2674 | 93.0512 | 2.8334 | 1.6568
7.8 | 98.3759 | 92.7453 | 99.2725 | 93.0518 | 2.8335 | 1.6568
7.8042 | 98.3705 | 92.7447 | 99.2672 | 93.0512 | 2.8337 | 1.6568
7.8083 | 98.3643 | 92.7439 | 99.261 | 93.0504 | 2.8338 | 1.6568
7.8125 | 98.3668 | 92.7433 | 99.2636 | 93.0499 | 2.8338 | 1.6568
7.8167 | 98.3703 | 92.7433 | 99.2671 | 93.0499 | 2.8339 | 1.6568
7.8208 | 98.3739 | 92.745 | 99.2708 | 93.0515 | 2.834 | 1.6568
7.825 | 98.3772 | 92.7463 | 99.2741 | 93.0529 | 2.8341 | 1.6568
7.8292 | 98.3696 | 92.7441 | 99.2666 | 93.0506 | 2.8342 | 1.6568
7.8333 | 98.362 | 92.7418 | 99.2591 | 93.0484 | 2.8343 | 1.6568
7.8375 | 98.3675 | 92.7435 | 99.2646 | 93.05 | 2.8344 | 1.6568
7.8417 | 98.3727 | 92.7456 | 99.2698 | 93.0521 | 2.8344 | 1.6567
7.8458 | 98.3696 | 92.7453 | 99.2668 | 93.0518 | 2.8346 | 1.6568
7.85 | 98.3666 | 92.7447 | 99.2639 | 93.0512 | 2.8347 | 1.6568
7.8542 | 98.367 | 92.7432 | 99.2644 | 93.0498 | 2.8347 | 1.6568
7.8583 | 98.3671 | 92.7417 | 99.2644 | 93.0482 | 2.8347 | 1.6568
7.8625 | 98.3735 | 92.7443 | 99.2709 | 93.0508 | 2.8349 | 1.6568
7.8667 | 98.3786 | 92.7475 | 99.2761 | 93.054 | 2.835 | 1.6568
7.8708 | 98.3646 | 92.745 | 99.2622 | 93.0515 | 2.8351 | 1.6568
7.875 | 98.3514 | 92.7417 | 99.249 | 93.0483 | 2.8352 | 1.6568
7.8792 | 98.3595 | 92.7425 | 99.2571 | 93.049 | 2.8352 | 1.6568
7.8833 | 98.3699 | 92.7438 | 99.2676 | 93.0503 | 2.8352 | 1.6568
7.8875 | 98.3718 | 92.7456 | 99.2696 | 93.0521 | 2.8354 | 1.6568
7.8917 | 98.3722 | 92.7474 | 99.2701 | 93.0539 | 2.8357 | 1.6568
7.8958 | 98.3587 | 92.7437 | 99.2566 | 93.0502 | 2.8357 | 1.6568
7.9 | 98.3447 | 92.7395 | 99.2427 | 93.046 | 2.8357 | 1.6568
7.9042 | 98.3591 | 92.7432 | 99.2571 | 93.0497 | 2.8358 | 1.6568
7.9083 | 98.376 | 92.7478 | 99.274 | 93.0543 | 2.8359 | 1.6567
7.9125 | 98.3713 | 92.7456 | 99.2695 | 93.0521 | 2.836 | 1.6568
7.9167 | 98.3637 | 92.7426 | 99.262 | 93.0491 | 2.8362 | 1.6569
7.9208 | 98.355 | 92.7428 | 99.2534 | 93.0494 | 2.8363 | 1.6568
7.925 | 98.3459 | 92.7437 | 99.2442 | 93.0502 | 2.8363 | 1.6567
7.9292 | 98.3524 | 92.7447 | 99.2508 | 93.0512 | 2.8364 | 1.6568
7.9333 | 98.3636 | 92.7454 | 99.2621 | 93.0519 | 2.8366 | 1.6569
7.9375 | 98.3685 | 92.7438 | 99.2671 | 93.0503 | 2.8366 | 1.6568
7.9417 | 98.3708 | 92.7421 | 99.2693 | 93.0486 | 2.8367 | 1.6567
7.9458 | 98.3652 | 92.7444 | 99.2639 | 93.0509 | 2.8368 | 1.6568
7.95 | 98.3568 | 92.7468 | 99.2556 | 93.0533 | 2.837 | 1.6568
7.9542 | 98.3504 | 92.7439 | 99.2492 | 93.0505 | 2.837 | 1.6568
7.9583 | 98.3475 | 92.7409 | 99.2462 | 93.0474 | 2.837 | 1.6568
7.9625 | 98.359 | 92.7436 | 99.2578 | 93.0501 | 2.8371 | 1.6568
7.9667 | 98.3721 | 92.7467 | 99.271 | 93.0533 | 2.8372 | 1.6568
7.9708 | 98.3673 | 92.7451 | 99.2663 | 93.0516 | 2.8374 | 1.6568
7.975 | 98.3588 | 92.743 | 99.2579 | 93.0495 | 2.8375 | 1.6568
7.9792 | 98.3538 | 92.7429 | 99.2529 | 93.0494 | 2.8375 | 1.6568
7.9833 | 98.3506 | 92.7433 | 99.2497 | 93.0499 | 2.8376 | 1.6568
7.9875 | 98.3573 | 92.7443 | 99.2565 | 93.0509 | 2.8377 | 1.6568
7.9917 | 98.3647 | 92.7454 | 99.264 | 93.0519 | 2.8378 | 1.6568
7.9958 | 98.3603 | 92.7444 | 99.2596 | 93.051 | 2.8379 | 1.6568
8 | 98.3536 | 92.7431 | 99.253 | 93.0496 | 2.838 | 1.6568
8.0042 | 98.3536 | 92.7432 | 99.253 | 93.0497 | 2.8381 | 1.6568
8.0083 | 98.3553 | 92.7437 | 99.2548 | 93.0502 | 2.8381 | 1.6568
8.0125 | 98.3594 | 92.7445 | 99.2589 | 93.0511 | 2.8382 | 1.6568
8.0167 | 98.3623 | 92.7451 | 99.2619 | 93.0516 | 2.8383 | 1.6568
8.0208 | 98.3562 | 92.7441 | 99.2558 | 93.0506 | 2.8384 | 1.6568
8.025 | 98.3501 | 92.7431 | 99.2498 | 93.0496 | 2.8385 | 1.6568
8.0292 | 98.3547 | 92.7432 | 99.2545 | 93.0497 | 2.8385 | 1.6568
8.0333 | 98.3595 | 92.7438 | 99.2593 | 93.0503 | 2.8386 | 1.6568
8.0375 | 98.3598 | 92.7448 | 99.2597 | 93.0514 | 2.8387 | 1.6568
8.0417 | 98.3602 | 92.7456 | 99.2601 | 93.0522 | 2.8389 | 1.6568
8.0458 | 98.3556 | 92.7434 | 99.2556 | 93.0499 | 2.8389 | 1.6568
8.05 | 98.351 | 92.7411 | 99.2511 | 93.0476 | 2.8389 | 1.6568
8.0542 | 98.3571 | 92.7437 | 99.2572 | 93.0502 | 2.839 | 1.6568
8.0583 | 98.3624 | 92.7466 | 99.2625 | 93.053 | 2.8391 | 1.6568
8.0625 | 98.3537 | 92.7448 | 99.2539 | 93.0514 | 2.8392 | 1.6568
8.0667 | 98.3455 | 92.7428 | 99.2457 | 93.0493 | 2.8394 | 1.6568
8.0708 | 98.3509 | 92.7426 | 99.2511 | 93.0491 | 2.8393 | 1.6568
8.075 | 98.3569 | 92.7425 | 99.2572 | 93.049 | 2.8393 | 1.6568
8.0792 | 98.3615 | 92.7447 | 99.2618 | 93.0512 | 2.8395 | 1.6568
8.0833 | 98.3644 | 92.7472 | 99.2649 | 93.0537 | 2.8397 | 1.6568
8.0875 | 98.3491 | 92.7441 | 99.2496 | 93.0506 | 2.8397 | 1.6568
8.0917 | 98.3342 | 92.7403 | 99.2347 | 93.0469 | 2.8398 | 1.6568
8.0958 | 98.3455 | 92.7425 | 99.2461 | 93.049 | 2.8398 | 1.6568
8.1 | 98.3599 | 92.7454 | 99.2604 | 93.0519 | 2.8398 | 1.6568
8.1042 | 98.3585 | 92.7455 | 99.2592 | 93.052 | 2.84 | 1.6568
8.1083 | 98.355 | 92.7451 | 99.2558 | 93.0516 | 2.8402 | 1.6568
8.1125 | 98.3445 | 92.7429 | 99.2454 | 93.0495 | 2.8402 | 1.6568
8.1167 | 98.3333 | 92.7407 | 99.2341 | 93.0472 | 2.8402 | 1.6568
8.1208 | 98.3449 | 92.7438 | 99.2458 | 93.0503 | 2.8403 | 1.6568
8.125 | 98.3598 | 92.7472 | 99.2607 | 93.0538 | 2.8404 | 1.6568
8.1292 | 98.3577 | 92.7445 | 99.2587 | 93.051 | 2.8405 | 1.6568
8.1333 | 98.3528 | 92.7411 | 99.2539 | 93.0477 | 2.8407 | 1.6568
8.1375 | 98.3468 | 92.7431 | 99.248 | 93.0496 | 2.8407 | 1.6568
8.1417 | 98.3395 | 92.7457 | 99.2406 | 93.0522 | 2.8408 | 1.6567
8.1458 | 98.3387 | 92.7444 | 99.2399 | 93.051 | 2.8409 | 1.6568
8.15 | 98.3423 | 92.7427 | 99.2436 | 93.0492 | 2.841 | 1.6569
8.1542 | 98.3519 | 92.7431 | 99.2532 | 93.0496 | 2.841 | 1.6568
8.1583 | 98.3607 | 92.7438 | 99.262 | 93.0503 | 2.8411 | 1.6567
8.1625 | 98.3561 | 92.7448 | 99.2576 | 93.0513 | 2.8412 | 1.6568
8.1667 | 98.348 | 92.7455 | 99.2496 | 93.052 | 2.8414 | 1.6569
8.1708 | 98.3401 | 92.7431 | 99.2417 | 93.0496 | 2.8414 | 1.6568
8.175 | 98.3345 | 92.7408 | 99.2361 | 93.0473 | 2.8414 | 1.6568
8.1792 | 98.3446 | 92.7437 | 99.2463 | 93.0502 | 2.8415 | 1.6568
8.1833 | 98.3568 | 92.747 | 99.2586 | 93.0535 | 2.8416 | 1.6568
8.1875 | 98.3522 | 92.7446 | 99.254 | 93.0511 | 2.8417 | 1.6568
8.1917 | 98.3446 | 92.7417 | 99.2465 | 93.0482 | 2.8418 | 1.6568
8.1958 | 98.3428 | 92.7427 | 99.2447 | 93.0492 | 2.8418 | 1.6568
8.2 | 98.3426 | 92.7442 | 99.2445 | 93.0507 | 2.8419 | 1.6568
8.2042 | 98.3467 | 92.7444 | 99.2486 | 93.0509 | 2.842 | 1.6568
8.2083 | 98.3502 | 92.7443 | 99.2523 | 93.0508 | 2.8421 | 1.6568
8.2125 | 98.3454 | 92.7439 | 99.2475 | 93.0504 | 2.8422 | 1.6568
8.2167 | 98.3397 | 92.7432 | 99.2418 | 93.0497 | 2.8423 | 1.6568
8.2208 | 98.3424 | 92.7431 | 99.2445 | 93.0496 | 2.8423 | 1.6568
8.225 | 98.3461 | 92.7434 | 99.2483 | 93.05 | 2.8423 | 1.6568
8.2292 | 98.3482 | 92.7444 | 99.2504 | 93.0509 | 2.8425 | 1.6568
8.2333 | 98.3492 | 92.745 | 99.2516 | 93.0515 | 2.8426 | 1.6568
8.2375 | 98.3437 | 92.7436 | 99.2461 | 93.0501 | 2.8426 | 1.6568
8.2417 | 98.3387 | 92.7421 | 99.2411 | 93.0487 | 2.8427 | 1.6568
8.2458 | 98.3445 | 92.7432 | 99.247 | 93.0497 | 2.8427 | 1.6568
8.25 | 98.3497 | 92.7446 | 99.2522 | 93.0511 | 2.8428 | 1.6568
8.2542 | 98.3456 | 92.7446 | 99.2481 | 93.0512 | 2.8429 | 1.6568
8.2583 | 98.3421 | 92.7444 | 99.2447 | 93.0509 | 2.843 | 1.6568
8.2625 | 98.3421 | 92.7428 | 99.2447 | 93.0493 | 2.843 | 1.6568
8.2667 | 98.3422 | 92.7412 | 99.2448 | 93.0477 | 2.843 | 1.6568
8.2708 | 98.3476 | 92.744 | 99.2503 | 93.0505 | 2.8431 | 1.6568
8.275 | 98.3518 | 92.7471 | 99.2546 | 93.0536 | 2.8432 | 1.6568
8.2792 | 98.3392 | 92.7443 | 99.242 | 93.0508 | 2.8433 | 1.6568
8.2833 | 98.3268 | 92.7411 | 99.2297 | 93.0476 | 2.8434 | 1.6568
8.2875 | 98.3365 | 92.7424 | 99.2394 | 93.0489 | 2.8434 | 1.6568
8.2917 | 98.348 | 92.744 | 99.2508 | 93.0505 | 2.8434 | 1.6568
8.2958 | 98.3498 | 92.7449 | 99.2527 | 93.0514 | 2.8436 | 1.6568
8.3 | 98.3497 | 92.7459 | 99.2527 | 93.0525 | 2.8438 | 1.6568
8.3042 | 98.3358 | 92.7433 | 99.2389 | 93.0499 | 2.8438 | 1.6568
8.3083 | 98.3218 | 92.7402 | 99.2249 | 93.0468 | 2.8438 | 1.6568
8.3125 | 98.3334 | 92.7429 | 99.2365 | 93.0494 | 2.8438 | 1.6568
8.3167 | 98.3484 | 92.7463 | 99.2516 | 93.0528 | 2.8439 | 1.6568
8.3208 | 98.3459 | 92.745 | 99.2492 | 93.0515 | 2.8441 | 1.6568
8.325 | 98.3409 | 92.7429 | 99.2443 | 93.0495 | 2.8442 | 1.6568
8.3292 | 98.3341 | 92.7427 | 99.2375 | 93.0492 | 2.8442 | 1.6568
8.3333 | 98.3259 | 92.7427 | 99.2293 | 93.0492 | 2.8442 | 1.6568
8.3375 | 98.332 | 92.7441 | 99.2355 | 93.0506 | 2.8444 | 1.6568
8.3417 | 98.3416 | 92.7455 | 99.2451 | 93.052 | 2.8445 | 1.6568
8.3458 | 98.3441 | 92.7435 | 99.2477 | 93.05 | 2.8445 | 1.6568
8.35 | 98.3446 | 92.7413 | 99.2482 | 93.0478 | 2.8446 | 1.6568
8.3542 | 98.3403 | 92.7437 | 99.2439 | 93.0502 | 2.8447 | 1.6568
8.3583 | 98.3338 | 92.7465 | 99.2375 | 93.053 | 2.8447 | 1.6568
8.3625 | 98.3275 | 92.7438 | 99.2313 | 93.0503 | 2.8448 | 1.6568
8.3667 | 98.325 | 92.7407 | 99.2288 | 93.0472 | 2.8449 | 1.6569
8.3708 | 98.337 | 92.7429 | 99.2408 | 93.0494 | 2.8449 | 1.6568
8.375 | 98.3497 | 92.7456 | 99.2535 | 93.0521 | 2.845 | 1.6567
8.3792 | 98.3453 | 92.7448 | 99.2492 | 93.0514 | 2.8451 | 1.6568
8.3833 | 98.3373 | 92.7435 | 99.2414 | 93.05 | 2.8453 | 1.6569
8.3875 | 98.3314 | 92.7424 | 99.2354 | 93.049 | 2.8452 | 1.6568
8.3917 | 98.3267 | 92.7419 | 99.2307 | 93.0484 | 2.8452 | 1.6567
8.3958 | 98.3336 | 92.744 | 99.2377 | 93.0506 | 2.8453 | 1.6568
8.4 | 98.342 | 92.7462 | 99.2462 | 93.0528 | 2.8455 | 1.6569
8.4042 | 98.3374 | 92.7439 | 99.2416 | 93.0505 | 2.8455 | 1.6568
8.4083 | 98.3308 | 92.7413 | 99.2351 | 93.0479 | 2.8456 | 1.6568
8.4125 | 98.3326 | 92.7428 | 99.2369 | 93.0492 | 2.8456 | 1.6568
8.4167 | 98.3357 | 92.7447 | 99.24 | 93.0512 | 2.8457 | 1.6568
8.4208 | 98.3374 | 92.7443 | 99.2418 | 93.0508 | 2.8458 | 1.6568
8.425 | 98.3378 | 92.7435 | 99.2422 | 93.05 | 2.8459 | 1.6568
8.4292 | 98.333 | 92.7435 | 99.2374 | 93.05 | 2.8459 | 1.6568
8.4333 | 98.3283 | 92.7433 | 99.2328 | 93.0499 | 2.846 | 1.6568
8.4375 | 98.3327 | 92.7432 | 99.2372 | 93.0497 | 2.846 | 1.6568
8.4417 | 98.3373 | 92.7433 | 99.2418 | 93.0498 | 2.8461 | 1.6568
8.4458 | 98.3366 | 92.7443 | 99.2411 | 93.0508 | 2.8462 | 1.6568
8.45 | 98.3356 | 92.7449 | 99.2403 | 93.0514 | 2.8463 | 1.6568
8.4542 | 98.3324 | 92.7431 | 99.2371 | 93.0496 | 2.8463 | 1.6568
8.4583 | 98.3298 | 92.7413 | 99.2345 | 93.0479 | 2.8463 | 1.6568
8.4625 | 98.3359 | 92.7434 | 99.2407 | 93.0499 | 2.8464 | 1.6568
8.4667 | 98.3407 | 92.7457 | 99.2455 | 93.0522 | 2.8465 | 1.6568
8.4708 | 98.332 | 92.7444 | 99.2369 | 93.0509 | 2.8466 | 1.6568
8.475 | 98.3241 | 92.7427 | 99.2291 | 93.0493 | 2.8467 | 1.6568
8.4792 | 98.3291 | 92.7424 | 99.2341 | 93.0489 | 2.8466 | 1.6568
8.4833 | 98.3348 | 92.7421 | 99.2397 | 93.0486 | 2.8466 | 1.6568
8.4875 | 98.3385 | 92.7443 | 99.2434 | 93.0509 | 2.8468 | 1.6568
8.4917 | 98.3406 | 92.7467 | 99.2457 | 93.0533 | 2.8469 | 1.6568
8.4958 | 98.3266 | 92.7436 | 99.2317 | 93.0502 | 2.847 | 1.6568
8.5 | 98.3123 | 92.7401 | 99.2175 | 93.0467 | 2.847 | 1.6568
8.5042 | 98.3242 | 92.7425 | 99.2293 | 93.049 | 2.847 | 1.6568
8.5083 | 98.3388 | 92.7454 | 99.244 | 93.0518 | 2.847 | 1.6568
8.5125 | 98.3383 | 92.7448 | 99.2435 | 93.0514 | 2.8472 | 1.6568
8.5167 | 98.3356 | 92.7441 | 99.2409 | 93.0506 | 2.8474 | 1.6568
8.5208 | 98.3251 | 92.7428 | 99.2305 | 93.0493 | 2.8474 | 1.6568
8.525 | 98.314 | 92.7413 | 99.2194 | 93.0479 | 2.8473 | 1.6568
8.5292 | 98.3228 | 92.7434 | 99.2282 | 93.0499 | 2.8474 | 1.6568
8.5333 | 98.3352 | 92.7459 | 99.2406 | 93.0525 | 2.8475 | 1.6568
8.5375 | 98.334 | 92.7442 | 99.2395 | 93.0507 | 2.8476 | 1.6568
8.5417 | 98.3307 | 92.7417 | 99.2362 | 93.0482 | 2.8477 | 1.6568
8.5458 | 98.3267 | 92.7428 | 99.2324 | 93.0494 | 2.8477 | 1.6568
8.55 | 98.3208 | 92.7446 | 99.2265 | 93.0511 | 2.8478 | 1.6568
8.5542 | 98.3207 | 92.7441 | 99.2264 | 93.0506 | 2.8479 | 1.6568
8.5583 | 98.3239 | 92.7433 | 99.2297 | 93.0498 | 2.848 | 1.6568
8.5625 | 98.3311 | 92.7428 | 99.2368 | 93.0493 | 2.848 | 1.6568
8.5667 | 98.3374 | 92.7425 | 99.2432 | 93.0491 | 2.848 | 1.6568
8.5708 | 98.3335 | 92.7443 | 99.2394 | 93.0508 | 2.8481 | 1.6568
8.575 | 98.3269 | 92.7458 | 99.2328 | 93.0524 | 2.8483 | 1.6568
8.5792 | 98.3187 | 92.7431 | 99.2247 | 93.0496 | 2.8483 | 1.6568
8.5833 | 98.3132 | 92.7401 | 99.2192 | 93.0467 | 2.8483 | 1.6568
8.5875 | 98.3246 | 92.7432 | 99.2306 | 93.0497 | 2.8484 | 1.6568
8.5917 | 98.3375 | 92.7467 | 99.2435 | 93.0532 | 2.8484 | 1.6568
8.5958 | 98.3329 | 92.7445 | 99.239 | 93.0511 | 2.8485 | 1.6568
8.6 | 98.3253 | 92.7417 | 99.2315 | 93.0482 | 2.8486 | 1.6569
8.6042 | 98.3235 | 92.7422 | 99.2296 | 93.0487 | 2.8486 | 1.6568
8.6083 | 98.3223 | 92.7434 | 99.2284 | 93.05 | 2.8486 | 1.6568
8.6125 | 98.3254 | 92.7443 | 99.2315 | 93.0508 | 2.8487 | 1.6568
8.6167 | 98.3288 | 92.7448 | 99.2351 | 93.0514 | 2.8489 | 1.6569
8.6208 | 98.3241 | 92.7433 | 99.2305 | 93.0499 | 2.8489 | 1.6568
8.625 | 98.3189 | 92.7418 | 99.2253 | 93.0483 | 2.8489 | 1.6568
8.6292 | 98.3232 | 92.743 | 99.2297 | 93.0495 | 2.849 | 1.6568
8.6333 | 98.3286 | 92.7446 | 99.235 | 93.0511 | 2.849 | 1.6569
8.6375 | 98.3283 | 92.7441 | 99.2348 | 93.0506 | 2.8491 | 1.6568
8.6417 | 98.3265 | 92.7432 | 99.233 | 93.0497 | 2.8492 | 1.6568
8.6458 | 98.3227 | 92.7432 | 99.2292 | 93.0497 | 2.8492 | 1.6568
8.65 | 98.3196 | 92.7431 | 99.2261 | 93.0496 | 2.8493 | 1.6568
8.6542 | 98.3246 | 92.7432 | 99.2312 | 93.0497 | 2.8493 | 1.6568
8.6583 | 98.3289 | 92.7436 | 99.2355 | 93.0501 | 2.8493 | 1.6568
8.6625 | 98.3247 | 92.7441 | 99.2314 | 93.0507 | 2.8495 | 1.6568
8.6667 | 98.3211 | 92.7444 | 99.2279 | 93.051 | 2.8496 | 1.6568
8.6708 | 98.3216 | 92.7427 | 99.2283 | 93.0492 | 2.8495 | 1.6568
8.675 | 98.3229 | 92.741 | 99.2296 | 93.0475 | 2.8495 | 1.6568
8.6792 | 98.3282 | 92.7437 | 99.235 | 93.0501 | 2.8496 | 1.6568
8.6833 | 98.3319 | 92.7465 | 99.2388 | 93.053 | 2.8497 | 1.6568
8.6875 | 98.3198 | 92.744 | 99.2267 | 93.0505 | 2.8498 | 1.6568
8.6917 | 98.3082 | 92.7411 | 99.2151 | 93.0476 | 2.8499 | 1.6568
8.6958 | 98.3174 | 92.7422 | 99.2243 | 93.0488 | 2.8499 | 1.6568
8.7 | 98.328 | 92.7437 | 99.235 | 93.0502 | 2.8498 | 1.6568
8.7042 | 98.3293 | 92.7446 | 99.2363 | 93.0511 | 2.85 | 1.6568
8.7083 | 98.329 | 92.7455 | 99.2361 | 93.052 | 2.8502 | 1.6568
8.7125 | 98.3163 | 92.743 | 99.2234 | 93.0496 | 2.8502 | 1.6568
8.7167 | 98.3028 | 92.7403 | 99.2099 | 93.0468 | 2.8502 | 1.6568
8.7208 | 98.314 | 92.7429 | 99.2212 | 93.0494 | 2.8502 | 1.6568
8.725 | 98.3286 | 92.746 | 99.2358 | 93.0525 | 2.8502 | 1.6568
8.7292 | 98.3272 | 92.7444 | 99.2346 | 93.0509 | 2.8504 | 1.6568
8.7333 | 98.3236 | 92.7424 | 99.2309 | 93.0489 | 2.8505 | 1.6568
8.7375 | 98.3171 | 92.7427 | 99.2245 | 93.0492 | 2.8505 | 1.6568
8.7417 | 98.3095 | 92.743 | 99.2168 | 93.0495 | 2.8505 | 1.6568
8.7458 | 98.3133 | 92.7438 | 99.2207 | 93.0503 | 2.8506 | 1.6568
8.75 | 98.3205 | 92.7446 | 99.228 | 93.0512 | 2.8507 | 1.6568
8.7542 | 98.3227 | 92.7434 | 99.2302 | 93.0499 | 2.8507 | 1.6568
8.7583 | 98.3234 | 92.7417 | 99.2309 | 93.0482 | 2.8508 | 1.6568
8.7625 | 98.3209 | 92.7434 | 99.2285 | 93.0499 | 2.8508 | 1.6568
8.7667 | 98.3161 | 92.7455 | 99.2237 | 93.052 | 2.8509 | 1.6568
8.7708 | 98.3111 | 92.7437 | 99.2188 | 93.0502 | 2.851 | 1.6568
8.775 | 98.3091 | 92.7415 | 99.2168 | 93.048 | 2.851 | 1.6568
8.7792 | 98.3192 | 92.7426 | 99.2269 | 93.0491 | 2.851 | 1.6568
8.7833 | 98.3298 | 92.7443 | 99.2375 | 93.0508 | 2.8511 | 1.6568
8.7875 | 98.3255 | 92.7445 | 99.2332 | 93.051 | 2.8512 | 1.6568
8.7917 | 98.3184 | 92.7443 | 99.2262 | 93.0508 | 2.8513 | 1.6568
8.7958 | 98.3118 | 92.7424 | 99.2196 | 93.049 | 2.8513 | 1.6568
8.8 | 98.3069 | 92.7409 | 99.2147 | 93.0474 | 2.8513 | 1.6568
8.8042 | 98.3151 | 92.7437 | 99.223 | 93.0502 | 2.8514 | 1.6568
8.8083 | 98.3248 | 92.7466 | 99.2327 | 93.0531 | 2.8515 | 1.6568
8.8125 | 98.3201 | 92.7439 | 99.2281 | 93.0505 | 2.8515 | 1.6568
8.8167 | 98.3135 | 92.7407 | 99.2216 | 93.0472 | 2.8516 | 1.6568
8.8208 | 98.316 | 92.7424 | 99.2241 | 93.0489 | 2.8516 | 1.6568
8.825 | 98.3189 | 92.7448 | 99.227 | 93.0513 | 2.8516 | 1.6568
8.8292 | 98.3184 | 92.7443 | 99.2266 | 93.0508 | 2.8517 | 1.6568
8.8333 | 98.3172 | 92.7434 | 99.2254 | 93.0499 | 2.8518 | 1.6569
8.8375 | 98.3132 | 92.7429 | 99.2214 | 93.0494 | 2.8518 | 1.6568
8.8417 | 98.3097 | 92.7425 | 99.2179 | 93.0491 | 2.8518 | 1.6568
8.8458 | 98.315 | 92.7432 | 99.2233 | 93.0498 | 2.8519 | 1.6568
8.85 | 98.3209 | 92.7442 | 99.2292 | 93.0507 | 2.852 | 1.6569
8.8542 | 98.3187 | 92.7438 | 99.227 | 93.0504 | 2.852 | 1.6568
8.8583 | 98.3154 | 92.7433 | 99.2238 | 93.0498 | 2.8521 | 1.6568
8.8625 | 98.3138 | 92.743 | 99.2222 | 93.0495 | 2.8521 | 1.6568
8.8667 | 98.3131 | 92.7426 | 99.2215 | 93.0492 | 2.8522 | 1.6569
8.8708 | 98.3179 | 92.7433 | 99.2263 | 93.0498 | 2.8522 | 1.6568
8.875 | 98.3212 | 92.7442 | 99.2297 | 93.0508 | 2.8522 | 1.6568
8.8792 | 98.3133 | 92.744 | 99.2218 | 93.0505 | 2.8523 | 1.6568
8.8833 | 98.3065 | 92.7435 | 99.2151 | 93.05 | 2.8524 | 1.6569
8.8875 | 98.3113 | 92.7424 | 99.2198 | 93.0489 | 2.8524 | 1.6568
8.8917 | 98.317 | 92.7415 | 99.2255 | 93.048 | 2.8524 | 1.6568
8.8958 | 98.3208 | 92.744 | 99.2294 | 93.0505 | 2.8525 | 1.6568
8.9 | 98.323 | 92.7466 | 99.2317 | 93.0531 | 2.8526 | 1.6568
8.9042 | 98.3095 | 92.7435 | 99.2183 | 93.05 | 2.8527 | 1.6568
8.9083 | 98.2959 | 92.74 | 99.2046 | 93.0465 | 2.8527 | 1.6568
8.9125 | 98.3072 | 92.7424 | 99.216 | 93.0489 | 2.8527 | 1.6568
8.9167 | 98.3208 | 92.7452 | 99.2295 | 93.0517 | 2.8527 | 1.6568
8.9208 | 98.3201 | 92.7445 | 99.2289 | 93.051 | 2.8528 | 1.6568
8.925 | 98.3177 | 92.7437 | 99.2267 | 93.0502 | 2.853 | 1.6569
8.9292 | 98.3083 | 92.7426 | 99.2173 | 93.0491 | 2.853 | 1.6568
8.9333 | 98.2977 | 92.7415 | 99.2066 | 93.048 | 2.8529 | 1.6568
8.9375 | 98.3055 | 92.7433 | 99.2145 | 93.0499 | 2.853 | 1.6568
8.9417 | 98.3169 | 92.7456 | 99.2259 | 93.0521 | 2.8531 | 1.6568
8.9458 | 98.3167 | 92.7438 | 99.2257 | 93.0503 | 2.8532 | 1.6568
8.95 | 98.3144 | 92.7415 | 99.2235 | 93.0481 | 2.8532 | 1.6568
8.9542 | 98.3111 | 92.7429 | 99.2202 | 93.0494 | 2.8533 | 1.6568
8.9583 | 98.3062 | 92.7445 | 99.2154 | 93.051 | 2.8533 | 1.6568
8.9625 | 98.3049 | 92.7438 | 99.2141 | 93.0504 | 2.8534 | 1.6568
8.9667 | 98.3064 | 92.7429 | 99.2156 | 93.0494 | 2.8534 | 1.6568
8.9708 | 98.3123 | 92.7428 | 99.2215 | 93.0494 | 2.8535 | 1.6568
8.975 | 98.3178 | 92.7427 | 99.227 | 93.0492 | 2.8535 | 1.6568
8.9792 | 98.3153 | 92.7439 | 99.2246 | 93.0504 | 2.8536 | 1.6568
8.9833 | 98.3102 | 92.7452 | 99.2196 | 93.0517 | 2.8537 | 1.6568
8.9875 | 98.3034 | 92.7431 | 99.2128 | 93.0496 | 2.8537 | 1.6568
8.9917 | 98.2989 | 92.7407 | 99.2083 | 93.0473 | 2.8537 | 1.6568
8.9958 | 98.3093 | 92.7429 | 99.2187 | 93.0494 | 2.8537 | 1.6568
9 | 98.3209 | 92.7456 | 99.2303 | 93.0521 | 2.8538 | 1.6568
9.0042 | 98.3159 | 92.7444 | 99.2254 | 93.0509 | 2.8539 | 1.6568
9.0083 | 98.3087 | 92.7425 | 99.2182 | 93.049 | 2.854 | 1.6569
9.0125 | 98.306 | 92.7421 | 99.2156 | 93.0486 | 2.8539 | 1.6568
9.0167 | 98.3043 | 92.7424 | 99.2138 | 93.0489 | 2.8539 | 1.6568
9.0208 | 98.3081 | 92.7441 | 99.2177 | 93.0506 | 2.854 | 1.6568
9.025 | 98.3126 | 92.7456 | 99.2222 | 93.0522 | 2.8541 | 1.6568
9.0292 | 98.3083 | 92.7433 | 99.218 | 93.0498 | 2.8542 | 1.6568
9.0333 | 98.3033 | 92.7406 | 99.213 | 93.0472 | 2.8542 | 1.6568
9.0375 | 98.309 | 92.7428 | 99.2187 | 93.0493 | 2.8542 | 1.6568
9.0417 | 98.3147 | 92.7454 | 99.2245 | 93.0519 | 2.8542 | 1.6568
9.0458 | 98.3116 | 92.7441 | 99.2214 | 93.0507 | 2.8543 | 1.6568
9.05 | 98.3072 | 92.7424 | 99.217 | 93.0489 | 2.8544 | 1.6568
9.0542 | 98.3046 | 92.7427 | 99.2145 | 93.0492 | 2.8544 | 1.6568
9.0583 | 98.3032 | 92.7432 | 99.213 | 93.0497 | 2.8544 | 1.6568
9.0625 | 98.3081 | 92.7434 | 99.218 | 93.05 | 2.8545 | 1.6568
9.0667 | 98.313 | 92.7437 | 99.223 | 93.0502 | 2.8546 | 1.6569
9.0708 | 98.3086 | 92.7437 | 99.2186 | 93.0502 | 2.8546 | 1.6568
9.075 | 98.3041 | 92.7435 | 99.2141 | 93.05 | 2.8546 | 1.6568
9.0792 | 98.3056 | 92.7428 | 99.2156 | 93.0493 | 2.8547 | 1.6568
9.0833 | 98.308 | 92.7421 | 99.218 | 93.0487 | 2.8547 | 1.6569
9.0875 | 98.3122 | 92.7435 | 99.2222 | 93.05 | 2.8547 | 1.6568
9.0917 | 98.3143 | 92.745 | 99.2244 | 93.0516 | 2.8548 | 1.6568
9.0958 | 98.3033 | 92.7438 | 99.2134 | 93.0503 | 2.8549 | 1.6568
9.1 | 98.2934 | 92.7422 | 99.2035 | 93.0488 | 2.855 | 1.6569
9.1042 | 98.3017 | 92.7422 | 99.2119 | 93.0488 | 2.8549 | 1.6568
9.1083 | 98.3114 | 92.7426 | 99.2215 | 93.0491 | 2.8549 | 1.6568
9.1125 | 98.3133 | 92.7442 | 99.2234 | 93.0508 | 2.855 | 1.6568
9.1167 | 98.3137 | 92.7458 | 99.224 | 93.0523 | 2.8552 | 1.6569
9.1208 | 98.3015 | 92.743 | 99.2118 | 93.0495 | 2.8552 | 1.6568
9.125 | 98.2883 | 92.7399 | 99.1986 | 93.0464 | 2.8551 | 1.6568
9.1292 | 98.2989 | 92.7428 | 99.2092 | 93.0493 | 2.8552 | 1.6568
9.1333 | 98.3124 | 92.7461 | 99.2227 | 93.0527 | 2.8552 | 1.6568
9.1375 | 98.311 | 92.7442 | 99.2214 | 93.0507 | 2.8553 | 1.6568
9.1417 | 98.3078 | 92.7419 | 99.2183 | 93.0485 | 2.8554 | 1.6568
9.1458 | 98.3024 | 92.7425 | 99.2129 | 93.0491 | 2.8554 | 1.6568
9.15 | 98.2955 | 92.7433 | 99.2059 | 93.0498 | 2.8554 | 1.6568
9.1542 | 98.2982 | 92.7437 | 99.2088 | 93.0502 | 2.8555 | 1.6568
9.1583 | 98.3044 | 92.7442 | 99.215 | 93.0507 | 2.8556 | 1.6568
9.1625 | 98.3069 | 92.7431 | 99.2175 | 93.0497 | 2.8556 | 1.6568
9.1667 | 98.3081 | 92.7418 | 99.2187 | 93.0483 | 2.8556 | 1.6568
9.1708 | 98.3063 | 92.7433 | 99.217 | 93.0499 | 2.8557 | 1.6568
9.175 | 98.3026 | 92.7452 | 99.2133 | 93.0517 | 2.8557 | 1.6568
9.1792 | 98.2975 | 92.7435 | 99.2082 | 93.05 | 2.8558 | 1.6568
9.1833 | 98.2945 | 92.7416 | 99.2053 | 93.0481 | 2.8558 | 1.6568
9.1875 | 98.3031 | 92.7427 | 99.2139 | 93.0492 | 2.8558 | 1.6568
9.1917 | 98.3122 | 92.7441 | 99.223 | 93.0506 | 2.8558 | 1.6568
9.1958 | 98.3088 | 92.7442 | 99.2197 | 93.0507 | 2.856 | 1.6568
9.2 | 98.3029 | 92.744 | 99.2138 | 93.0505 | 2.8561 | 1.6568
9.2042 | 98.2974 | 92.7426 | 99.2083 | 93.0491 | 2.8561 | 1.6568
9.2083 | 98.2934 | 92.7411 | 99.2043 | 93.0477 | 2.856 | 1.6568
9.2125 | 98.3016 | 92.7434 | 99.2125 | 93.0499 | 2.8561 | 1.6568
9.2167 | 98.3108 | 92.7459 | 99.2217 | 93.0525 | 2.8562 | 1.6568
9.2208 | 98.3056 | 92.7439 | 99.2166 | 93.0505 | 2.8562 | 1.6568
9.225 | 98.2991 | 92.7412 | 99.2101 | 93.0477 | 2.8563 | 1.6568
9.2292 | 98.3009 | 92.7422 | 99.2119 | 93.0487 | 2.8563 | 1.6568
9.2333 | 98.3031 | 92.7439 | 99.2141 | 93.0504 | 2.8563 | 1.6568
9.2375 | 98.3024 | 92.7443 | 99.2135 | 93.0508 | 2.8564 | 1.6568
9.2417 | 98.3015 | 92.7442 | 99.2126 | 93.0507 | 2.8565 | 1.6569
9.2458 | 98.2984 | 92.7427 | 99.2096 | 93.0493 | 2.8565 | 1.6568
9.25 | 98.2956 | 92.7414 | 99.2067 | 93.0479 | 2.8565 | 1.6568
9.2542 | 98.3024 | 92.7432 | 99.2136 | 93.0497 | 2.8565 | 1.6568
9.2583 | 98.3091 | 92.7453 | 99.2203 | 93.0518 | 2.8566 | 1.6568
9.2625 | 98.3042 | 92.7438 | 99.2155 | 93.0503 | 2.8566 | 1.6568
9.2667 | 98.2982 | 92.742 | 99.2095 | 93.0485 | 2.8567 | 1.6568
9.2708 | 98.2978 | 92.7427 | 99.2091 | 93.0492 | 2.8567 | 1.6568
9.275 | 98.2988 | 92.7435 | 99.2101 | 93.05 | 2.8567 | 1.6568
9.2792 | 98.3027 | 92.7435 | 99.214 | 93.05 | 2.8567 | 1.6568
9.2833 | 98.3057 | 92.7435 | 99.2171 | 93.05 | 2.8568 | 1.6568
9.2875 | 98.2989 | 92.7435 | 99.2103 | 93.05 | 2.8569 | 1.6568
9.2917 | 98.2928 | 92.7435 | 99.2043 | 93.05 | 2.8569 | 1.6568
9.2958 | 98.2977 | 92.7427 | 99.2091 | 93.0492 | 2.8569 | 1.6568
9.3 | 98.3035 | 92.7419 | 99.2149 | 93.0484 | 2.8569 | 1.6568
9.3042 | 98.3066 | 92.7437 | 99.2181 | 93.0502 | 2.857 | 1.6568
9.3083 | 98.3076 | 92.7456 | 99.2191 | 93.0521 | 2.8571 | 1.6568
9.3125 | 98.2952 | 92.7435 | 99.2067 | 93.05 | 2.8571 | 1.6568
9.3167 | 98.2831 | 92.741 | 99.1947 | 93.0476 | 2.8572 | 1.6569
9.3208 | 98.2932 | 92.7423 | 99.2048 | 93.0489 | 2.8571 | 1.6568
9.325 | 98.3054 | 92.744 | 99.2169 | 93.0506 | 2.8571 | 1.6568
9.3292 | 98.3055 | 92.7443 | 99.2171 | 93.0508 | 2.8572 | 1.6568
9.3333 | 98.3045 | 92.7443 | 99.2162 | 93.0508 | 2.8574 | 1.6569
9.3375 | 98.2955 | 92.7426 | 99.2072 | 93.0491 | 2.8574 | 1.6568
9.3417 | 98.2849 | 92.7409 | 99.1965 | 93.0474 | 2.8573 | 1.6568
9.3458 | 98.2921 | 92.7433 | 99.2038 | 93.0498 | 2.8574 | 1.6568
9.35 | 98.3026 | 92.746 | 99.2144 | 93.0525 | 2.8575 | 1.6569
9.3542 | 98.3022 | 92.7436 | 99.2141 | 93.0502 | 2.8575 | 1.6568
9.3583 | 98.3001 | 92.741 | 99.212 | 93.0475 | 2.8576 | 1.6568
9.3625 | 98.2979 | 92.7428 | 99.2098 | 93.0493 | 2.8576 | 1.6568
9.3667 | 98.2941 | 92.7449 | 99.206 | 93.0514 | 2.8576 | 1.6568
9.3708 | 98.2919 | 92.7437 | 99.2038 | 93.0502 | 2.8577 | 1.6568
9.375 | 98.2925 | 92.7424 | 99.2044 | 93.0489 | 2.8577 | 1.6568
9.3792 | 98.2982 | 92.7427 | 99.2101 | 93.0492 | 2.8577 | 1.6568
9.3833 | 98.3036 | 92.7429 | 99.2155 | 93.0495 | 2.8577 | 1.6568
9.3875 | 98.3016 | 92.7438 | 99.2136 | 93.0503 | 2.8578 | 1.6568
9.3917 | 98.2976 | 92.7447 | 99.2096 | 93.0513 | 2.8579 | 1.6568
9.3958 | 98.2914 | 92.743 | 99.2034 | 93.0496 | 2.8579 | 1.6568
9.4 | 98.2866 | 92.7411 | 99.1987 | 93.0476 | 2.8579 | 1.6568
9.4042 | 98.2957 | 92.7429 | 99.2078 | 93.0494 | 2.8579 | 1.6568
9.4083 | 98.3058 | 92.7451 | 99.2178 | 93.0517 | 2.858 | 1.6568
9.4125 | 98.3013 | 92.7441 | 99.2134 | 93.0507 | 2.8581 | 1.6568
9.4167 | 98.2947 | 92.7426 | 99.207 | 93.0491 | 2.8582 | 1.6569
9.4208 | 98.2927 | 92.7422 | 99.205 | 93.0488 | 2.8581 | 1.6568
9.425 | 98.2917 | 92.7423 | 99.2039 | 93.0488 | 2.8581 | 1.6568
9.4292 | 98.2957 | 92.7438 | 99.208 | 93.0504 | 2.8582 | 1.6568
9.4333 | 98.3002 | 92.7454 | 99.2125 | 93.0519 | 2.8583 | 1.6568
9.4375 | 98.2957 | 92.7433 | 99.208 | 93.0499 | 2.8583 | 1.6568
9.4417 | 98.2908 | 92.7408 | 99.2031 | 93.0473 | 2.8583 | 1.6568
9.4458 | 98.2961 | 92.7426 | 99.2084 | 93.0491 | 2.8583 | 1.6568
9.45 | 98.3013 | 92.745 | 99.2136 | 93.0515 | 2.8583 | 1.6568
9.4542 | 98.2971 | 92.7442 | 99.2095 | 93.0507 | 2.8584 | 1.6568
9.4583 | 98.292 | 92.7428 | 99.2045 | 93.0493 | 2.8585 | 1.6569
9.4625 | 98.2908 | 92.7424 | 99.2032 | 93.049 | 2.8585 | 1.6568
9.4667 | 98.2905 | 92.7424 | 99.2029 | 93.0489 | 2.8585 | 1.6568
9.4708 | 98.2966 | 92.7435 | 99.2091 | 93.0501 | 2.8585 | 1.6568
9.475 | 98.3023 | 92.7447 | 99.2148 | 93.0512 | 2.8586 | 1.6568
9.4792 | 98.2962 | 92.7435 | 99.2088 | 93.05 | 2.8586 | 1.6568
9.4833 | 98.2896 | 92.7421 | 99.2022 | 93.0486 | 2.8587 | 1.6568
9.4875 | 98.2919 | 92.7427 | 99.2044 | 93.0492 | 2.8587 | 1.6568
9.4917 | 98.2956 | 92.7434 | 99.2081 | 93.05 | 2.8587 | 1.6568
9.4958 | 98.2982 | 92.7435 | 99.2107 | 93.05 | 2.8587 | 1.6568
9.5 | 98.2992 | 92.7437 | 99.2119 | 93.0502 | 2.8588 | 1.6568
9.5042 | 98.2904 | 92.7434 | 99.203 | 93.05 | 2.8589 | 1.6568
9.5083 | 98.2824 | 92.7431 | 99.1951 | 93.0496 | 2.8589 | 1.6568
9.5125 | 98.2901 | 92.7426 | 99.2028 | 93.0491 | 2.8589 | 1.6568
9.5167 | 98.2988 | 92.7422 | 99.2115 | 93.0487 | 2.8589 | 1.6568
9.5208 | 98.3008 | 92.7439 | 99.2136 | 93.0504 | 2.859 | 1.6568
9.525 | 98.301 | 92.7455 | 99.2137 | 93.0521 | 2.859 | 1.6568
9.5292 | 98.2892 | 92.7431 | 99.202 | 93.0497 | 2.8591 | 1.6568
9.5333 | 98.2768 | 92.7404 | 99.1897 | 93.047 | 2.8591 | 1.6569
9.5375 | 98.2863 | 92.7426 | 99.1991 | 93.0492 | 2.8591 | 1.6568
9.5417 | 98.2984 | 92.7453 | 99.2112 | 93.0518 | 2.8591 | 1.6568
9.5458 | 98.2977 | 92.7441 | 99.2105 | 93.0506 | 2.8592 | 1.6568
9.55 | 98.296 | 92.7425 | 99.209 | 93.0491 | 2.8593 | 1.6569
9.5542 | 98.2911 | 92.7425 | 99.204 | 93.049 | 2.8593 | 1.6568
9.5583 | 98.2842 | 92.7426 | 99.1971 | 93.0491 | 2.8592 | 1.6568
9.5625 | 98.2866 | 92.7437 | 99.1996 | 93.0502 | 2.8593 | 1.6568
9.5667 | 98.2921 | 92.7448 | 99.2051 | 93.0513 | 2.8594 | 1.6569
9.5708 | 98.2942 | 92.743 | 99.2072 | 93.0496 | 2.8594 | 1.6568
9.575 | 98.2948 | 92.7411 | 99.2079 | 93.0476 | 2.8594 | 1.6568
9.5792 | 98.2941 | 92.7433 | 99.2072 | 93.0498 | 2.8595 | 1.6568
9.5833 | 98.2918 | 92.7456 | 99.205 | 93.0522 | 2.8595 | 1.6568
9.5875 | 98.2862 | 92.7434 | 99.1994 | 93.05 | 2.8596 | 1.6568
9.5917 | 98.2827 | 92.741 | 99.1959 | 93.0475 | 2.8596 | 1.6568
9.5958 | 98.2908 | 92.7426 | 99.204 | 93.0492 | 2.8596 | 1.6568
9.6 | 98.2994 | 92.7444 | 99.2126 | 93.0509 | 2.8596 | 1.6568
9.6042 | 98.2962 | 92.744 | 99.2094 | 93.0506 | 2.8597 | 1.6568
9.6083 | 98.2909 | 92.7435 | 99.2042 | 93.05 | 2.8598 | 1.6568
9.6125 | 98.2864 | 92.7426 | 99.1997 | 93.0491 | 2.8598 | 1.6568
9.6167 | 98.2828 | 92.7416 | 99.1961 | 93.0482 | 2.8597 | 1.6568
9.6208 | 98.2899 | 92.7433 | 99.2031 | 93.0499 | 2.8598 | 1.6568
9.625 | 98.2978 | 92.7454 | 99.2112 | 93.0519 | 2.8598 | 1.6568
9.6292 | 98.293 | 92.7438 | 99.2064 | 93.0503 | 2.8599 | 1.6568
9.6333 | 98.2869 | 92.7415 | 99.2003 | 93.0481 | 2.86 | 1.6568
9.6375 | 98.2889 | 92.7422 | 99.2023 | 93.0488 | 2.8599 | 1.6568
9.6417 | 98.2914 | 92.7436 | 99.2048 | 93.0501 | 2.8599 | 1.6568
9.6458 | 98.2909 | 92.7441 | 99.2043 | 93.0506 | 2.86 | 1.6568
9.65 | 98.2901 | 92.7443 | 99.2036 | 93.0508 | 2.8601 | 1.6569
9.6542 | 98.2872 | 92.7428 | 99.2006 | 93.0493 | 2.8601 | 1.6568
9.6583 | 98.2847 | 92.7412 | 99.1982 | 93.0477 | 2.8601 | 1.6568
9.6625 | 98.2915 | 92.7431 | 99.205 | 93.0496 | 2.8601 | 1.6568
9.6667 | 98.2978 | 92.7453 | 99.2113 | 93.0518 | 2.8602 | 1.6568
9.6708 | 98.2913 | 92.7439 | 99.2049 | 93.0504 | 2.8602 | 1.6568
9.675 | 98.284 | 92.7419 | 99.1976 | 93.0485 | 2.8603 | 1.6568
9.6792 | 98.2851 | 92.7424 | 99.1986 | 93.0489 | 2.8602 | 1.6568
9.6833 | 98.2875 | 92.7432 | 99.201 | 93.0498 | 2.8602 | 1.6568
9.6875 | 98.2918 | 92.7437 | 99.2054 | 93.0502 | 2.8603 | 1.6568
9.6917 | 98.2953 | 92.744 | 99.2089 | 93.0505 | 2.8604 | 1.6568
9.6958 | 98.2883 | 92.7432 | 99.2019 | 93.0498 | 2.8604 | 1.6568
9.7 | 98.2814 | 92.7424 | 99.195 | 93.049 | 2.8604 | 1.6568
9.7042 | 98.2862 | 92.7428 | 99.1999 | 93.0493 | 2.8604 | 1.6568
9.7083 | 98.2925 | 92.7431 | 99.2061 | 93.0497 | 2.8604 | 1.6568
9.7125 | 98.294 | 92.7435 | 99.2077 | 93.05 | 2.8605 | 1.6568
9.7167 | 98.2937 | 92.744 | 99.2075 | 93.0506 | 2.8606 | 1.6568
9.7208 | 98.2837 | 92.7434 | 99.1974 | 93.0499 | 2.8606 | 1.6568
9.725 | 98.2741 | 92.7424 | 99.1879 | 93.049 | 2.8606 | 1.6568
9.7292 | 98.2831 | 92.7426 | 99.1968 | 93.0491 | 2.8606 | 1.6568
9.7333 | 98.2935 | 92.743 | 99.2073 | 93.0495 | 2.8606 | 1.6568
9.7375 | 98.2946 | 92.744 | 99.2084 | 93.0505 | 2.8607 | 1.6568
9.7417 | 98.2942 | 92.7448 | 99.2081 | 93.0513 | 2.8608 | 1.6568
9.7458 | 98.2851 | 92.7428 | 99.199 | 93.0494 | 2.8608 | 1.6568
9.75 | 98.2745 | 92.7407 | 99.1884 | 93.0472 | 2.8608 | 1.6568
9.7542 | 98.2809 | 92.7431 | 99.1949 | 93.0496 | 2.8608 | 1.6568
9.7583 | 98.2904 | 92.7458 | 99.2044 | 93.0523 | 2.8608 | 1.6568
9.7625 | 98.2901 | 92.7437 | 99.2041 | 93.0502 | 2.8609 | 1.6568
9.7667 | 98.289 | 92.7412 | 99.2031 | 93.0477 | 2.861 | 1.6569
9.7708 | 98.2877 | 92.7427 | 99.2017 | 93.0492 | 2.861 | 1.6568
9.775 | 98.2843 | 92.7444 | 99.1984 | 93.0509 | 2.8609 | 1.6568
9.7792 | 98.2819 | 92.7438 | 99.196 | 93.0503 | 2.861 | 1.6568
9.7833 | 98.2821 | 92.743 | 99.1962 | 93.0495 | 2.8611 | 1.6569
9.7875 | 98.2871 | 92.7426 | 99.2012 | 93.0491 | 2.8611 | 1.6568
9.7917 | 98.2914 | 92.7423 | 99.2055 | 93.0488 | 2.861 | 1.6568
9.7958 | 98.2902 | 92.7438 | 99.2044 | 93.0503 | 2.8611 | 1.6568
9.8 | 98.2877 | 92.7452 | 99.2019 | 93.0518 | 2.8612 | 1.6569
9.8042 | 98.2815 | 92.7429 | 99.1957 | 93.0495 | 2.8612 | 1.6568
9.8083 | 98.2765 | 92.7405 | 99.1906 | 93.0471 | 2.8612 | 1.6568
9.8125 | 98.2849 | 92.7429 | 99.1991 | 93.0494 | 2.8612 | 1.6568
9.8167 | 98.2944 | 92.7455 | 99.2087 | 93.052 | 2.8613 | 1.6568
9.8208 | 98.29 | 92.744 | 99.2042 | 93.0505 | 2.8613 | 1.6568
9.825 | 98.2837 | 92.742 | 99.198 | 93.0486 | 2.8614 | 1.6568
9.8292 | 98.2827 | 92.7423 | 99.197 | 93.0488 | 2.8614 | 1.6568
9.8333 | 98.2821 | 92.7428 | 99.1964 | 93.0494 | 2.8613 | 1.6568
9.8375 | 98.2853 | 92.7438 | 99.1997 | 93.0503 | 2.8614 | 1.6568
9.8417 | 98.289 | 92.7448 | 99.2034 | 93.0513 | 2.8615 | 1.6568
9.8458 | 98.2849 | 92.7432 | 99.1993 | 93.0498 | 2.8615 | 1.6568
9.85 | 98.2804 | 92.7413 | 99.1948 | 93.0478 | 2.8615 | 1.6568
9.8542 | 98.2856 | 92.7426 | 99.1999 | 93.0491 | 2.8615 | 1.6568
9.8583 | 98.2908 | 92.7445 | 99.2051 | 93.051 | 2.8615 | 1.6568
9.8625 | 98.2864 | 92.7441 | 99.2008 | 93.0506 | 2.8616 | 1.6568
9.8667 | 98.2813 | 92.7431 | 99.1957 | 93.0496 | 2.8617 | 1.6569
9.8708 | 98.2805 | 92.7424 | 99.195 | 93.049 | 2.8617 | 1.6568
9.875 | 98.2809 | 92.742 | 99.1954 | 93.0485 | 2.8616 | 1.6568
9.8792 | 98.2873 | 92.7435 | 99.2017 | 93.05 | 2.8617 | 1.6568
9.8833 | 98.2927 | 92.745 | 99.2072 | 93.0516 | 2.8618 | 1.6568
9.8875 | 98.2852 | 92.7435 | 99.1997 | 93.05 | 2.8618 | 1.6568
9.8917 | 98.2772 | 92.7417 | 99.1917 | 93.0482 | 2.8618 | 1.6568
9.8958 | 98.2806 | 92.7425 | 99.1952 | 93.0491 | 2.8618 | 1.6568
9.9 | 98.2854 | 92.7437 | 99.2 | 93.0502 | 2.8618 | 1.6568
9.9042 | 98.2878 | 92.7437 | 99.2024 | 93.0502 | 2.8619 | 1.6568
9.9083 | 98.2889 | 92.7436 | 99.2035 | 93.0501 | 2.8619 | 1.6568
9.9125 | 98.2811 | 92.7431 | 99.1958 | 93.0496 | 2.862 | 1.6568
9.9167 | 98.2738 | 92.7427 | 99.1885 | 93.0492 | 2.862 | 1.6568
9.9208 | 98.2806 | 92.7429 | 99.1953 | 93.0494 | 2.862 | 1.6568
9.925 | 98.2888 | 92.743 | 99.2035 | 93.0495 | 2.862 | 1.6568
9.9292 | 98.2897 | 92.7435 | 99.2045 | 93.0501 | 2.862 | 1.6568
9.9333 | 98.2888 | 92.7443 | 99.2036 | 93.0508 | 2.8621 | 1.6568
9.9375 | 98.279 | 92.7432 | 99.1938 | 93.0497 | 2.8621 | 1.6568
9.9417 | 98.2689 | 92.7419 | 99.1837 | 93.0484 | 2.8621 | 1.6568
9.9458 | 98.2772 | 92.7427 | 99.192 | 93.0492 | 2.8621 | 1.6568
9.95 | 98.2874 | 92.7439 | 99.2022 | 93.0504 | 2.8621 | 1.6568
9.9542 | 98.288 | 92.7439 | 99.2029 | 93.0504 | 2.8622 | 1.6568
9.9583 | 98.2877 | 92.7436 | 99.2026 | 93.0501 | 2.8623 | 1.6569
9.9625 | 98.2822 | 92.7426 | 99.1971 | 93.0492 | 2.8623 | 1.6568
9.9667 | 98.2748 | 92.7418 | 99.1896 | 93.0483 | 2.8623 | 1.6568
9.9708 | 98.2768 | 92.7434 | 99.1917 | 93.05 | 2.8623 | 1.6568
9.975 | 98.2819 | 92.7452 | 99.1968 | 93.0518 | 2.8624 | 1.6568
9.9792 | 98.2833 | 92.7431 | 99.1983 | 93.0497 | 2.8624 | 1.6568
9.9833 | 98.2841 | 92.7408 | 99.1991 | 93.0473 | 2.8624 | 1.6568
9.9875 | 98.2845 | 92.7431 | 99.1995 | 93.0496 | 2.8624 | 1.6568
9.9917 | 98.2834 | 92.7456 | 99.1984 | 93.0521 | 2.8625 | 1.6568
9.9958 | 98.2778 | 92.7435 | 99.1928 | 93.0501 | 2.8625 | 1.6568
10 | 98.2739 | 92.7412 | 99.189 | 93.0478 | 2.8626 | 1.6569
10.0042 | 98.2814 | 92.7425 | 99.1964 | 93.0491 | 2.8625 | 1.6568
10.0083 | 98.2237 | 92.6823 | 99.1384 | 92.9886 | 2.862 | 1.6563
10.0125 | 98.0914 | 92.5585 | 99.0054 | 92.8645 | 2.861 | 1.6553
10.0167 | 97.9226 | 92.4059 | 98.8356 | 92.7112 | 2.8593 | 1.6537
10.0208 | 97.7194 | 92.2232 | 98.6307 | 92.5278 | 2.8567 | 1.6513
10.025 | 97.5475 | 92.0741 | 98.4569 | 92.3776 | 2.8539 | 1.6487
10.0292 | 97.4162 | 91.9617 | 98.3238 | 92.2643 | 2.851 | 1.6461
10.0333 | 97.2592 | 91.825 | 98.1649 | 92.1266 | 2.8479 | 1.6434
10.0375 | 97.063 | 91.659 | 97.9667 | 91.9595 | 2.8446 | 1.6405
10.0417 | 96.872 | 91.499 | 97.7732 | 91.7983 | 2.8408 | 1.6373
10.0458 | 96.6963 | 91.3493 | 97.5947 | 91.6474 | 2.8365 | 1.6338
10.05 | 96.5553 | 91.2316 | 97.4509 | 91.5284 | 2.832 | 1.6302
10.0542 | 96.4442 | 91.1436 | 97.3369 | 91.439 | 2.8274 | 1.6265
10.0583 | 96.302 | 91.029 | 97.1917 | 91.323 | 2.8226 | 1.6227
10.0625 | 96.129 | 90.8874 | 97.0155 | 91.1801 | 2.8176 | 1.6189
10.0667 | 95.9587 | 90.748 | 96.8418 | 91.0391 | 2.8121 | 1.6148
10.0708 | 95.7982 | 90.6131 | 96.6775 | 90.9027 | 2.8062 | 1.6104
10.075 | 95.671 | 90.5073 | 96.5466 | 90.7953 | 2.8001 | 1.6059
10.0792 | 95.5639 | 90.4275 | 96.4356 | 90.7139 | 2.794 | 1.6015
10.0833 | 95.4262 | 90.3229 | 96.2939 | 90.6078 | 2.7876 | 1.5971
10.0875 | 95.2693 | 90.1956 | 96.1329 | 90.4788 | 2.7811 | 1.5926
10.0917 | 95.1167 | 90.0706 | 95.976 | 90.3522 | 2.7741 | 1.5879
10.0958 | 94.9674 | 89.948 | 95.8223 | 90.2279 | 2.7669 | 1.5831
10.1 | 94.8501 | 89.8513 | 95.7004 | 90.1294 | 2.7595 | 1.5783
10.1042 | 94.7536 | 89.7786 | 95.5993 | 90.055 | 2.752 | 1.5734
10.1083 | 94.6272 | 89.6833 | 95.4682 | 89.9581 | 2.7444 | 1.5686
10.1125 | 94.4867 | 89.5676 | 95.323 | 89.8407 | 2.7366 | 1.5638
10.1167 | 94.3502 | 89.4536 | 95.1815 | 89.7249 | 2.7285 | 1.5589
10.1208 | 94.209 | 89.3397 | 95.0352 | 89.6093 | 2.7201 | 1.5538
10.125 | 94.0991 | 89.2496 | 94.9202 | 89.5174 | 2.7117 | 1.5487
10.1292 | 94.0122 | 89.1831 | 94.8282 | 89.4492 | 2.7031 | 1.5436
10.1333 | 93.8959 | 89.0957 | 94.7066 | 89.3601 | 2.6944 | 1.5387
10.1375 | 93.7684 | 88.9879 | 94.5739 | 89.2505 | 2.6857 | 1.5337
10.1417 | 93.645 | 88.8811 | 94.445 | 89.1421 | 2.6767 | 1.5286
10.1458 | 93.514 | 88.7759 | 94.3085 | 89.0351 | 2.6674 | 1.5235
10.15 | 93.4135 | 88.6925 | 94.2025 | 88.9499 | 2.6581 | 1.5183
10.1542 | 93.3349 | 88.6289 | 94.1184 | 88.8847 | 2.6487 | 1.5133
10.1583 | 93.2252 | 88.5459 | 94.003 | 88.7999 | 2.6393 | 1.5082
10.1625 | 93.1051 | 88.4462 | 93.8774 | 88.6985 | 2.6298 | 1.5033
10.1667 | 92.9888 | 88.3477 | 93.7554 | 88.5983 | 2.6201 | 1.4982
10.1708 | 92.8643 | 88.2475 | 93.6251 | 88.4964 | 2.6101 | 1.4931
10.175 | 92.7703 | 88.1668 | 93.5253 | 88.4141 | 2.6002 | 1.488
10.1792 | 92.7016 | 88.1076 | 93.4508 | 88.3532 | 2.5902 | 1.4829
10.1833 | 92.61 | 88.0382 | 93.3533 | 88.2821 | 2.5801 | 1.4779
10.1875 | 92.505 | 87.9582 | 93.2426 | 88.2004 | 2.57 | 1.4729
10.1917 | 92.4135 | 87.886 | 93.1451 | 88.1266 | 2.5596 | 1.4678
10.1958 | 92.3325 | 87.8201 | 93.058 | 88.0589 | 2.549 | 1.4625
10.2 | 92.2736 | 87.7655 | 92.993 | 88.0026 | 2.5383 | 1.4572
10.2042 | 92.2188 | 87.7256 | 92.9324 | 87.961 | 2.5277 | 1.452
10.2083 | 92.1465 | 87.6899 | 92.854 | 87.9236 | 2.517 | 1.4466
10.2125 | 92.0544 | 87.6538 | 92.7557 | 87.8857 | 2.506 | 1.441
10.2167 | 91.9871 | 87.6444 | 92.6821 | 87.8745 | 2.4947 | 1.4352
10.2208 | 91.9708 | 87.6673 | 92.6593 | 87.8954 | 2.4831 | 1.4292
10.225 | 91.9649 | 87.684 | 92.647 | 87.9101 | 2.4714 | 1.423
10.2292 | 91.9488 | 87.6898 | 92.6245 | 87.914 | 2.4598 | 1.4168
10.2333 | 91.8669 | 87.6496 | 92.5362 | 87.8718 | 2.4482 | 1.4107
10.2375 | 91.7239 | 87.5657 | 92.3868 | 87.7859 | 2.4364 | 1.4045
10.2417 | 91.5687 | 87.4742 | 92.2252 | 87.6925 | 2.4246 | 1.3983
10.2458 | 91.4141 | 87.3753 | 92.0643 | 87.5918 | 2.413 | 1.3922
10.25 | 91.3055 | 87.3016 | 91.9496 | 87.5162 | 2.4016 | 1.3863
10.2542 | 91.224 | 87.25 | 91.862 | 87.4628 | 2.3903 | 1.3805
10.2583 | 91.128 | 87.196 | 91.7601 | 87.407 | 2.3791 | 1.3748
10.2625 | 91.0273 | 87.1436 | 91.6535 | 87.353 | 2.3682 | 1.3692
10.2667 | 90.9275 | 87.0941 | 91.5479 | 87.3017 | 2.3571 | 1.3636
10.2708 | 90.8295 | 87.0434 | 91.444 | 87.2494 | 2.3459 | 1.3579
10.275 | 90.7586 | 87.0031 | 91.3673 | 87.2073 | 2.3348 | 1.3522
10.2792 | 90.7124 | 86.9746 | 91.3154 | 87.177 | 2.3237 | 1.3466
10.2833 | 90.6349 | 86.9253 | 91.2322 | 87.1262 | 2.3127 | 1.3411
10.2875 | 90.53 | 86.8608 | 91.1217 | 87.06 | 2.3019 | 1.3356
10.2917 | 90.422 | 86.7922 | 91.0081 | 86.9898 | 2.291 | 1.3301
10.2958 | 90.3087 | 86.7223 | 90.8892 | 86.9183 | 2.28 | 1.3246
10.3 | 90.2272 | 86.6698 | 90.8021 | 86.8642 | 2.2691 | 1.3193
10.3042 | 90.1801 | 86.6325 | 90.7496 | 86.8253 | 2.2583 | 1.314
10.3083 | 90.1083 | 86.5849 | 90.6725 | 86.7762 | 2.2477 | 1.3087
10.3125 | 90.0087 | 86.5264 | 90.5676 | 86.7162 | 2.2372 | 1.3036
10.3167 | 89.9065 | 86.4643 | 90.4601 | 86.6526 | 2.2266 | 1.2985
10.3208 | 89.8035 | 86.402 | 90.3518 | 86.5888 | 2.2159 | 1.2934
10.325 | 89.7304 | 86.3547 | 90.2735 | 86.54 | 2.2052 | 1.2882
10.3292 | 89.6919 | 86.3201 | 90.2298 | 86.504 | 2.1948 | 1.2832
10.3333 | 89.6275 | 86.2742 | 90.1603 | 86.4566 | 2.1844 | 1.2783
10.3375 | 89.53 | 86.2172 | 90.0579 | 86.3983 | 2.1742 | 1.2734
10.3417 | 89.4303 | 86.1574 | 89.9532 | 86.3371 | 2.1638 | 1.2685
10.3458 | 89.3315 | 86.0981 | 89.8493 | 86.2764 | 2.1533 | 1.2636
10.35 | 89.262 | 86.0528 | 89.7748 | 86.2298 | 2.143 | 1.2588
10.3542 | 89.2271 | 86.0184 | 89.735 | 86.194 | 2.1327 | 1.254
10.3583 | 89.1679 | 85.9743 | 89.671 | 86.1486 | 2.1226 | 1.2492
10.3625 | 89.0773 | 85.9216 | 89.5757 | 86.0945 | 2.1126 | 1.2446
10.3667 | 88.9847 | 85.8659 | 89.4784 | 86.0376 | 2.1025 | 1.2399
10.3708 | 88.8961 | 85.8093 | 89.385 | 85.9797 | 2.0923 | 1.2352
10.375 | 88.8383 | 85.7682 | 89.3224 | 85.9373 | 2.082 | 1.2305
10.3792 | 88.8145 | 85.7408 | 89.2939 | 85.9086 | 2.072 | 1.2259
10.3833 | 88.7711 | 85.7074 | 89.2458 | 85.874 | 2.0619 | 1.2213
10.3875 | 88.7016 | 85.6665 | 89.1718 | 85.8318 | 2.052 | 1.2168
10.3917 | 88.6251 | 85.6189 | 89.0907 | 85.783 | 2.0419 | 1.2122
10.3958 | 88.5549 | 85.5708 | 89.0158 | 85.7337 | 2.0316 | 1.2076
10.4 | 88.5235 | 85.5446 | 88.9797 | 85.7062 | 2.0212 | 1.2029
10.4042 | 88.5249 | 85.5338 | 88.9765 | 85.6941 | 2.0108 | 1.1982
10.4083 | 88.5225 | 85.5276 | 88.9694 | 85.6866 | 2.0004 | 1.1935
10.4125 | 88.5125 | 85.5291 | 88.9546 | 85.6868 | 1.9898 | 1.1887
10.4167 | 88.4825 | 85.5149 | 88.9199 | 85.6713 | 1.979 | 1.1838
10.4208 | 88.4258 | 85.4878 | 88.8584 | 85.643 | 1.9682 | 1.1789
10.425 | 88.3894 | 85.4744 | 88.8172 | 85.6283 | 1.9572 | 1.1739
10.4292 | 88.3656 | 85.4686 | 88.7885 | 85.6211 | 1.9461 | 1.1687
10.4333 | 88.3317 | 85.4705 | 88.7498 | 85.6216 | 1.9349 | 1.1635
10.4375 | 88.3048 | 85.4864 | 88.7181 | 85.6362 | 1.9239 | 1.1583
10.4417 | 88.2656 | 85.4897 | 88.6742 | 85.6382 | 1.9127 | 1.153
10.4458 | 88.213 | 85.4763 | 88.6167 | 85.6234 | 1.9013 | 1.1476
10.45 | 88.1607 | 85.4528 | 88.5596 | 85.5985 | 1.8901 | 1.1423
10.4542 | 88.1107 | 85.4201 | 88.5049 | 85.5644 | 1.8788 | 1.137
10.4583 | 88.0254 | 85.3715 | 88.415 | 85.5145 | 1.8678 | 1.1318
10.4625 | 87.8984 | 85.305 | 88.2835 | 85.4468 | 1.8571 | 1.1268
10.4667 | 87.7835 | 85.2462 | 88.1642 | 85.3868 | 1.8463 | 1.1218
10.4708 | 87.6849 | 85.1967 | 88.0611 | 85.336 | 1.8355 | 1.1168
10.475 | 87.6301 | 85.1728 | 88.002 | 85.3109 | 1.8248 | 1.1119
10.4792 | 87.6188 | 85.1711 | 87.9864 | 85.308 | 1.8143 | 1.1071
10.4833 | 87.5912 | 85.1706 | 87.9545 | 85.3063 | 1.8039 | 1.1023
10.4875 | 87.5357 | 85.1663 | 87.8949 | 85.3008 | 1.7935 | 1.0974
10.4917 | 87.47 | 85.1509 | 87.825 | 85.2842 | 1.7829 | 1.0924
10.4958 | 87.4136 | 85.1316 | 87.7643 | 85.2637 | 1.7722 | 1.0875
10.5 | 87.3727 | 85.1102 | 87.7192 | 85.2411 | 1.7615 | 1.0825
10.5042 | 87.3392 | 85.087 | 87.6815 | 85.2166 | 1.751 | 1.0776
10.5083 | 87.2814 | 85.0557 | 87.6198 | 85.1842 | 1.7406 | 1.0727
10.5125 | 87.1896 | 85.0187 | 87.5239 | 85.1461 | 1.7302 | 1.0679
10.5167 | 87.0992 | 84.9832 | 87.4295 | 85.1095 | 1.7198 | 1.0632
10.5208 | 87.0301 | 84.9506 | 87.3563 | 85.0757 | 1.7093 | 1.0584
10.525 | 86.9885 | 84.9298 | 87.3108 | 85.0537 | 1.6989 | 1.0536
10.5292 | 86.9608 | 84.9148 | 87.2792 | 85.0377 | 1.6887 | 1.049
10.5333 | 86.9123 | 84.8947 | 87.2269 | 85.0165 | 1.6786 | 1.0444
10.5375 | 86.8369 | 84.8709 | 87.1477 | 84.9916 | 1.6684 | 1.0397
10.5417 | 86.7589 | 84.8445 | 87.0659 | 84.9642 | 1.6581 | 1.0351
10.5458 | 86.6993 | 84.8183 | 87.0025 | 84.9369 | 1.6478 | 1.0305
10.55 | 86.6618 | 84.7978 | 86.9613 | 84.9153 | 1.6376 | 1.0259
10.5542 | 86.6312 | 84.7798 | 86.927 | 84.8963 | 1.6275 | 1.0213
10.5583 | 86.5799 | 84.7567 | 86.872 | 84.8722 | 1.6174 | 1.0168
10.5625 | 86.5028 | 84.7303 | 86.7914 | 84.8447 | 1.6074 | 1.0123
10.5667 | 86.4254 | 84.7035 | 86.7102 | 84.8169 | 1.5972 | 1.0079
10.5708 | 86.371 | 84.6784 | 86.6522 | 84.7909 | 1.587 | 1.0034
10.575 | 86.3469 | 84.6619 | 86.6246 | 84.7733 | 1.5769 | 0.99888
10.5792 | 86.3365 | 84.6524 | 86.6106 | 84.7629 | 1.567 | 0.99447
10.5833 | 86.3069 | 84.6398 | 86.5776 | 84.7493 | 1.5571 | 0.99015
10.5875 | 86.2538 | 84.6238 | 86.5212 | 84.7323 | 1.5473 | 0.98585
10.5917 | 86.2067 | 84.6127 | 86.4705 | 84.7203 | 1.5372 | 0.98152
10.5958 | 86.18 | 84.6053 | 86.4404 | 84.712 | 1.527 | 0.97719
10.6 | 86.1921 | 84.6089 | 86.4491 | 84.7146 | 1.5168 | 0.97288
10.6042 | 86.224 | 84.6218 | 86.4775 | 84.7266 | 1.5066 | 0.96854
10.6083 | 86.2211 | 84.6242 | 86.4712 | 84.7281 | 1.4964 | 0.96424
10.6125 | 86.1844 | 84.6187 | 86.4311 | 84.7216 | 1.4863 | 0.95999
10.6167 | 86.148 | 84.6179 | 86.3912 | 84.7199 | 1.4758 | 0.95564
10.6208 | 86.1244 | 84.6184 | 86.3641 | 84.7194 | 1.4651 | 0.9512
10.625 | 86.1468 | 84.6357 | 86.383 | 84.7358 | 1.4543 | 0.94674
10.6292 | 86.2064 | 84.6747 | 86.4391 | 84.7738 | 1.4435 | 0.94223
10.6333 | 86.2285 | 84.7003 | 86.4577 | 84.7985 | 1.4328 | 0.93773
10.6375 | 86.1971 | 84.7094 | 86.423 | 84.8067 | 1.4221 | 0.93329
10.6417 | 86.1465 | 84.7118 | 86.3689 | 84.8081 | 1.4111 | 0.92878
10.6458 | 86.0927 | 84.7083 | 86.3115 | 84.8036 | 1.3999 | 0.92413
10.65 | 86.0668 | 84.7137 | 86.2822 | 84.8081 | 1.3888 | 0.91952
10.6542 | 86.0674 | 84.7306 | 86.2794 | 84.8241 | 1.3779 | 0.91501
10.6583 | 86.0486 | 84.7453 | 86.2573 | 84.8379 | 1.3672 | 0.91052
10.6625 | 86.0066 | 84.7524 | 86.212 | 84.8441 | 1.3564 | 0.906
10.6667 | 85.9503 | 84.7501 | 86.1524 | 84.8408 | 1.3456 | 0.90154
10.6708 | 85.9022 | 84.7432 | 86.1012 | 84.8331 | 1.3348 | 0.89714
10.675 | 85.8694 | 84.7323 | 86.0652 | 84.8214 | 1.3241 | 0.8928
10.6792 | 85.8246 | 84.7113 | 86.0174 | 84.7994 | 1.3137 | 0.88857
10.6833 | 85.7684 | 84.6939 | 85.9581 | 84.7812 | 1.3035 | 0.88442
10.6875 | 85.7048 | 84.6823 | 85.8915 | 84.7688 | 1.2933 | 0.88031
10.6917 | 85.6552 | 84.6815 | 85.839 | 84.7672 | 1.2829 | 0.87618
10.6958 | 85.6339 | 84.691 | 85.8148 | 84.7759 | 1.2727 | 0.87213
10.7 | 85.6451 | 84.7105 | 85.823 | 84.7947 | 1.2625 | 0.86806
10.7042 | 85.6671 | 84.7371 | 85.8423 | 84.8205 | 1.2523 | 0.86391
10.7083 | 85.6595 | 84.7552 | 85.8318 | 84.8377 | 1.2421 | 0.85976
10.7125 | 85.6373 | 84.768 | 85.8068 | 84.8497 | 1.232 | 0.85566
10.7167 | 85.6 | 84.7696 | 85.7667 | 84.8506 | 1.2217 | 0.85158
10.7208 | 85.5536 | 84.7621 | 85.7174 | 84.8423 | 1.2114 | 0.84746
10.725 | 85.5266 | 84.7531 | 85.6877 | 84.8325 | 1.2012 | 0.84341
10.7292 | 85.5042 | 84.7447 | 85.6627 | 84.8234 | 1.1912 | 0.83946
10.7333 | 85.4682 | 84.7397 | 85.6241 | 84.8177 | 1.1813 | 0.83557
10.7375 | 85.4321 | 84.7367 | 85.5853 | 84.8139 | 1.1715 | 0.83168
10.7417 | 85.4002 | 84.7383 | 85.5509 | 84.8148 | 1.1616 | 0.82782
10.7458 | 85.373 | 84.7419 | 85.5212 | 84.8177 | 1.1519 | 0.82403
10.75 | 85.3698 | 84.7485 | 85.5155 | 84.8236 | 1.1422 | 0.82025
10.7542 | 85.3781 | 84.7577 | 85.5213 | 84.8321 | 1.1325 | 0.81643
10.7583 | 85.3644 | 84.764 | 85.5052 | 84.8378 | 1.1229 | 0.81263
10.7625 | 85.343 | 84.7688 | 85.4815 | 84.8419 | 1.1134 | 0.8089
10.7667 | 85.3173 | 84.7705 | 85.4533 | 84.8429 | 1.1039 | 0.80519
10.7708 | 85.287 | 84.7701 | 85.4207 | 84.8418 | 1.0943 | 0.80144
10.775 | 85.2771 | 84.7705 | 85.4085 | 84.8416 | 1.0849 | 0.79773
10.7792 | 85.2761 | 84.771 | 85.4053 | 84.8415 | 1.0755 | 0.7941
10.7833 | 85.2558 | 84.7721 | 85.3828 | 84.8419 | 1.0663 | 0.7905
10.7875 | 85.2308 | 84.7736 | 85.3556 | 84.8427 | 1.0571 | 0.78687
10.7917 | 85.2088 | 84.7774 | 85.3314 | 84.8459 | 1.0479 | 0.78326
10.7958 | 85.1957 | 84.7846 | 85.3162 | 84.8525 | 1.0387 | 0.77969
10.8 | 85.2049 | 84.7896 | 85.3232 | 84.8569 | 1.0296 | 0.77617
10.8042 | 85.2241 | 84.7939 | 85.3404 | 84.8606 | 1.0204 | 0.77263
10.8083 | 85.2358 | 84.8033 | 85.35 | 84.8693 | 1.0113 | 0.76904
10.8125 | 85.2369 | 84.8149 | 85.349 | 84.8803 | 1.0022 | 0.76546
10.8167 | 85.2496 | 84.8351 | 85.3596 | 84.8999 | 0.99295 | 0.76187
10.8208 | 85.2791 | 84.8633 | 85.3871 | 84.9275 | 0.98351 | 0.75822
10.825 | 85.3147 | 84.8829 | 85.4206 | 84.9465 | 0.97409 | 0.75457
10.8292 | 85.3439 | 84.8963 | 85.4479 | 84.9592 | 0.96483 | 0.75098
10.8333 | 85.351 | 84.9096 | 85.4529 | 84.972 | 0.95553 | 0.74734
10.8375 | 85.3383 | 84.9197 | 85.4383 | 84.9814 | 0.9461 | 0.74361
10.8417 | 85.3352 | 84.939 | 85.4331 | 85.0001 | 0.93658 | 0.73988
10.8458 | 85.3578 | 84.9717 | 85.4537 | 85.0322 | 0.92708 | 0.73616
10.85 | 85.3892 | 84.9995 | 85.4832 | 85.0594 | 0.91756 | 0.73244
10.8542 | 85.4072 | 85.019 | 85.4993 | 85.0783 | 0.90812 | 0.72874
10.8583 | 85.3896 | 85.0319 | 85.4798 | 85.0906 | 0.89871 | 0.72505
10.8625 | 85.344 | 85.0404 | 85.4324 | 85.0985 | 0.88927 | 0.72131
10.8667 | 85.2903 | 85.0466 | 85.3767 | 85.1041 | 0.87979 | 0.7176
10.8708 | 85.2369 | 85.0367 | 85.3215 | 85.0936 | 0.87049 | 0.71392
10.875 | 85.2097 | 85.0306 | 85.2925 | 85.087 | 0.86129 | 0.71023
10.8792 | 85.2044 | 85.0213 | 85.2855 | 85.077 | 0.85208 | 0.70634
10.8833 | 85.1837 | 85.0118 | 85.2631 | 85.0669 | 0.84302 | 0.70251
10.8875 | 85.1566 | 85.0092 | 85.2343 | 85.0638 | 0.83417 | 0.69876
10.8917 | 85.1227 | 85.0019 | 85.1987 | 85.0558 | 0.82526 | 0.69502
10.8958 | 85.0705 | 84.9777 | 85.1449 | 85.0311 | 0.81629 | 0.69122
10.9 | 85.0384 | 84.9551 | 85.1112 | 85.0079 | 0.80743 | 0.68748
10.9042 | 85.0281 | 84.9392 | 85.0993 | 84.9914 | 0.79865 | 0.68368
10.9083 | 85.0126 | 84.9293 | 85.0823 | 84.9809 | 0.78988 | 0.67988
10.9125 | 84.9887 | 84.9283 | 85.0568 | 84.9793 | 0.78128 | 0.67607
10.9167 | 84.9701 | 84.9307 | 85.0367 | 84.9811 | 0.77256 | 0.67226
10.9208 | 84.9588 | 84.9317 | 85.0239 | 84.9816 | 0.76368 | 0.66836
10.925 | 84.9572 | 84.9287 | 85.0208 | 84.978 | 0.75477 | 0.66442
10.9292 | 84.9727 | 84.9231 | 85.0348 | 84.9718 | 0.74594 | 0.66044
10.9333 | 84.9599 | 84.9096 | 85.0205 | 84.9577 | 0.73719 | 0.65649
10.9375 | 84.9096 | 84.8929 | 84.9689 | 84.9404 | 0.7285 | 0.65246
10.9417 | 84.8507 | 84.8701 | 84.9086 | 84.9171 | 0.71978 | 0.64849
10.9458 | 84.7867 | 84.8377 | 84.8432 | 84.8841 | 0.71103 | 0.64455
10.95 | 84.7501 | 84.811 | 84.8052 | 84.8568 | 0.70241 | 0.64064
10.9542 | 84.7441 | 84.7885 | 84.7979 | 84.8337 | 0.69391 | 0.63665
10.9583 | 84.7343 | 84.7717 | 84.7868 | 84.8164 | 0.68553 | 0.63268
10.9625 | 84.7106 | 84.7626 | 84.7619 | 84.8067 | 0.67729 | 0.62876
10.9667 | 84.6853 | 84.7525 | 84.7352 | 84.7961 | 0.66897 | 0.62483
10.9708 | 84.6637 | 84.7363 | 84.7124 | 84.7793 | 0.6605 | 0.62081
10.975 | 84.6559 | 84.7183 | 84.7033 | 84.7608 | 0.65207 | 0.61677
10.9792 | 84.6675 | 84.7001 | 84.7137 | 84.742 | 0.64373 | 0.61271
10.9833 | 84.6619 | 84.6792 | 84.707 | 84.7206 | 0.63547 | 0.60865
10.9875 | 84.6326 | 84.6613 | 84.6765 | 84.7021 | 0.62723 | 0.60453
10.9917 | 84.5967 | 84.6383 | 84.6395 | 84.6785 | 0.61896 | 0.60043
10.9958 | 84.5599 | 84.6064 | 84.6016 | 84.6461 | 0.61065 | 0.59636
11 | 84.5455 | 84.5784 | 84.586 | 84.6176 | 0.60237 | 0.59227
11.0042 | 84.5531 | 84.5529 | 84.5926 | 84.5915 | 0.59412 | 0.58806
11.0083 | 84.5569 | 84.5333 | 84.5953 | 84.5714 | 0.58594 | 0.58385
11.0125 | 84.5553 | 84.5237 | 84.5926 | 84.5612 | 0.57776 | 0.57966
11.0167 | 84.5451 | 84.5047 | 84.5813 | 84.5417 | 0.56951 | 0.57547
11.0208 | 84.5303 | 84.4745 | 84.5654 | 84.5109 | 0.56115 | 0.57121
11.025 | 84.5396 | 84.4473 | 84.5737 | 84.4832 | 0.5527 | 0.56686
11.0292 | 84.561 | 84.4205 | 84.5941 | 84.4558 | 0.5442 | 0.56243
11.0333 | 84.5821 | 84.402 | 84.6141 | 84.4368 | 0.53571 | 0.55799
11.0375 | 84.6057 | 84.4085 | 84.6367 | 84.4427 | 0.52717 | 0.55357
11.0417 | 84.6144 | 84.4047 | 84.6444 | 84.4384 | 0.51853 | 0.54912
11.0458 | 84.607 | 84.3945 | 84.636 | 84.4277 | 0.50993 | 0.54483
11.05 | 84.6101 | 84.383 | 84.6382 | 84.4157 | 0.50133 | 0.54049
11.0542 | 84.6198 | 84.3651 | 84.6469 | 84.3972 | 0.49263 | 0.53602
11.0583 | 84.6211 | 84.3524 | 84.6473 | 84.3839 | 0.48404 | 0.53157
11.0625 | 84.6231 | 84.3555 | 84.6484 | 84.3865 | 0.47564 | 0.52721
11.0667 | 84.6251 | 84.3568 | 84.6495 | 84.3873 | 0.46717 | 0.52283
11.0708 | 84.6232 | 84.3523 | 84.6467 | 84.3823 | 0.4586 | 0.51842
11.075 | 84.6277 | 84.3458 | 84.6504 | 84.3753 | 0.45017 | 0.51401
11.0792 | 84.639 | 84.3412 | 84.6608 | 84.3702 | 0.44188 | 0.50956
11.0833 | 84.6242 | 84.3337 | 84.6452 | 84.3622 | 0.43376 | 0.50514
11.0875 | 84.5773 | 84.3228 | 84.5976 | 84.3508 | 0.42585 | 0.50077
11.0917 | 84.5388 | 84.3139 | 84.5583 | 84.3414 | 0.41797 | 0.49641
11.0958 | 84.5241 | 84.3008 | 84.5429 | 84.3278 | 0.41 | 0.49202
11.1 | 84.5364 | 84.2915 | 84.5545 | 84.3181 | 0.40217 | 0.48766
11.1042 | 84.5713 | 84.2802 | 84.5887 | 84.3063 | 0.39465 | 0.48341
11.1083 | 84.5914 | 84.2696 | 84.6082 | 84.2952 | 0.38721 | 0.47914
11.1125 | 84.5827 | 84.2645 | 84.5988 | 84.2897 | 0.37973 | 0.47484
11.1167 | 84.5644 | 84.2562 | 84.5798 | 84.2809 | 0.37218 | 0.47057
11.1208 | 84.5569 | 84.2493 | 84.5718 | 84.2736 | 0.36463 | 0.46641
11.125 | 84.5657 | 84.2452 | 84.58 | 84.2691 | 0.35706 | 0.46221
11.1292 | 84.5769 | 84.2374 | 84.5905 | 84.2608 | 0.34963 | 0.45798
11.1333 | 84.5782 | 84.2336 | 84.5913 | 84.2566 | 0.34227 | 0.45376
11.1375 | 84.571 | 84.2424 | 84.5835 | 84.265 | 0.33489 | 0.44955
11.1417 | 84.5572 | 84.2482 | 84.5691 | 84.2704 | 0.3274 | 0.44531
11.1458 | 84.5577 | 84.2525 | 84.5691 | 84.2742 | 0.31991 | 0.44114
11.15 | 84.5647 | 84.2541 | 84.5756 | 84.2755 | 0.31251 | 0.43701
11.1542 | 84.5618 | 84.2505 | 84.5722 | 84.2714 | 0.30523 | 0.4329
11.1583 | 84.5372 | 84.2443 | 84.5471 | 84.2648 | 0.29807 | 0.42883
11.1625 | 84.4891 | 84.2393 | 84.4986 | 84.2595 | 0.29097 | 0.42485
11.1667 | 84.4442 | 84.2372 | 84.4532 | 84.257 | 0.28389 | 0.42091
11.1708 | 84.4204 | 84.2381 | 84.4289 | 84.2576 | 0.27681 | 0.41701
11.175 | 84.4253 | 84.2468 | 84.4335 | 84.2659 | 0.26979 | 0.41313
11.1792 | 84.4427 | 84.257 | 84.4504 | 84.2757 | 0.2629 | 0.40931
11.1833 | 84.4505 | 84.2696 | 84.4578 | 84.2879 | 0.25607 | 0.4055
11.1875 | 84.4464 | 84.2872 | 84.4533 | 84.3052 | 0.24918 | 0.40168
11.1917 | 84.4334 | 84.302 | 84.4399 | 84.3197 | 0.24217 | 0.39785
11.1958 | 84.4315 | 84.3158 | 84.4377 | 84.3331 | 0.23514 | 0.39409
11.2 | 84.4442 | 84.3307 | 84.45 | 84.3477 | 0.22813 | 0.39034
11.2042 | 84.4606 | 84.3442 | 84.4661 | 84.3609 | 0.22115 | 0.38655
11.2083 | 84.4596 | 84.3534 | 84.4647 | 84.3698 | 0.21429 | 0.38283
11.2125 | 84.437 | 84.3612 | 84.4418 | 84.3772 | 0.2075 | 0.37922
11.2167 | 84.4173 | 84.372 | 84.4218 | 84.3878 | 0.2006 | 0.37558
11.2208 | 84.4101 | 84.3829 | 84.4143 | 84.3983 | 0.1936 | 0.37193
11.225 | 84.4334 | 84.4044 | 84.4373 | 84.4196 | 0.18661 | 0.36829
11.2292 | 84.4807 | 84.4338 | 84.4843 | 84.4487 | 0.17966 | 0.36472
11.2333 | 84.5081 | 84.4565 | 84.5114 | 84.471 | 0.17276 | 0.36117
11.2375 | 84.5088 | 84.4736 | 84.5119 | 84.4879 | 0.16587 | 0.35766
11.2417 | 84.5045 | 84.4895 | 84.5073 | 84.5035 | 0.15881 | 0.35411
11.2458 | 84.4988 | 84.4917 | 84.5014 | 84.5055 | 0.15161 | 0.35057
11.25 | 84.5185 | 84.4961 | 84.5208 | 84.5096 | 0.14441 | 0.34702
11.2542 | 84.5591 | 84.5053 | 84.5612 | 84.5185 | 0.13728 | 0.34341
11.2583 | 84.5793 | 84.5062 | 84.5812 | 84.5191 | 0.13019 | 0.33974
11.2625 | 84.5708 | 84.5138 | 84.5725 | 84.5264 | 0.12322 | 0.33614
11.2667 | 84.5484 | 84.5184 | 84.5499 | 84.5308 | 0.11616 | 0.33251
11.2708 | 84.5296 | 84.5219 | 84.531 | 84.534 | 0.10898 | 0.32879
11.275 | 84.5247 | 84.5248 | 84.5259 | 84.5366 | 0.1019 | 0.32507
11.2792 | 84.5288 | 84.5215 | 84.5298 | 84.533 | 0.095109 | 0.3214
11.2833 | 84.5282 | 84.5203 | 84.5291 | 84.5316 | 0.088389 | 0.31771
11.2875 | 84.5208 | 84.5228 | 84.5216 | 84.5338 | 0.081578 | 0.31388
11.2917 | 84.5077 | 84.525 | 84.5083 | 84.5357 | 0.074801 | 0.31005
11.2958 | 84.5031 | 84.5291 | 84.5036 | 84.5396 | 0.068173 | 0.3063
11.3 | 84.5038 | 84.5283 | 84.5042 | 84.5385 | 0.061613 | 0.30253
11.3042 | 84.4868 | 84.513 | 84.4871 | 84.5229 | 0.055166 | 0.2987
11.3083 | 84.4645 | 84.4981 | 84.4645 | 84.5078 | 0.048845 | 0.29486
11.3125 | 84.4506 | 84.4909 | 84.4506 | 84.5004 | 0.042533 | 0.29099
11.3167 | 84.4458 | 84.4866 | 84.4458 | 84.4958 | 0.036171 | 0.28711
11.3208 | 84.4548 | 84.477 | 84.4548 | 84.486 | 0.02995 | 0.28332
11.325 | 84.4847 | 84.4681 | 84.4847 | 84.4768 | 0.023732 | 0.2795
11.3292 | 84.5162 | 84.4583 | 84.5162 | 84.4667 | 0.017442 | 0.27558
11.3333 | 84.5305 | 84.4496 | 84.5305 | 84.4579 | 0.011177 | 0.27169
11.3375 | 84.5395 | 84.4498 | 84.5395 | 84.4578 | 0.0049917 | 0.26786
11.3417 | 84.5389 | 84.4523 | 84.5389 | 84.4601 | -0.0012711 | 0.26404
11.3458 | 84.529 | 84.4487 | 84.529 | 84.4563 | -0.0075223 | 0.2602
11.35 | 84.5331 | 84.4428 | 84.5331 | 84.4501 | -0.013664 | 0.25639
11.3542 | 84.5457 | 84.4347 | 84.5457 | 84.4418 | -0.01973 | 0.25259
11.3583 | 84.5536 | 84.4288 | 84.5536 | 84.4357 | -0.025692 | 0.24877
11.3625 | 84.5662 | 84.4277 | 84.5662 | 84.4344 | -0.031593 | 0.24493
11.3667 | 84.5733 | 84.4259 | 84.5733 | 84.4324 | -0.037439 | 0.24115
11.3708 | 84.5758 | 84.4222 | 84.5758 | 84.4285 | -0.043226 | 0.23742
11.375 | 84.5855 | 84.4122 | 84.5855 | 84.4183 | -0.048922 | 0.2337
11.3792 | 84.5898 | 84.3954 | 84.5898 | 84.4013 | -0.054536 | 0.22999
11.3833 | 84.589 | 84.3834 | 84.5886 | 84.3891 | -0.059999 | 0.2263
11.3875 | 84.5918 | 84.3796 | 84.5913 | 84.3851 | -0.065389 | 0.2226
11.3917 | 84.6028 | 84.3819 | 84.6023 | 84.3873 | -0.070808 | 0.21892
11.3958 | 84.6247 | 84.3855 | 84.6241 | 84.3907 | -0.076186 | 0.21529
11.4 | 84.6626 | 84.386 | 84.6618 | 84.3911 | -0.081492 | 0.21167
11.4042 | 84.7053 | 84.3868 | 84.7044 | 84.3916 | -0.086786 | 0.20804
11.4083 | 84.7353 | 84.3921 | 84.7343 | 84.3968 | -0.092055 | 0.2044
11.4125 | 84.7596 | 84.4031 | 84.7585 | 84.4076 | -0.097306 | 0.20083
11.4167 | 84.7803 | 84.4193 | 84.7792 | 84.4236 | -0.10257 | 0.19734
11.4208 | 84.807 | 84.4372 | 84.8057 | 84.4414 | -0.10789 | 0.19383
11.425 | 84.8377 | 84.4449 | 84.8362 | 84.4489 | -0.1131 | 0.19039
11.4292 | 84.8605 | 84.4455 | 84.8589 | 84.4494 | -0.11817 | 0.18705
11.4333 | 84.8753 | 84.4544 | 84.8736 | 84.4582 | -0.12326 | 0.18369
11.4375 | 84.8808 | 84.4661 | 84.8789 | 84.4697 | -0.12842 | 0.18031
11.4417 | 84.8949 | 84.4883 | 84.8929 | 84.4918 | -0.13368 | 0.177
11.4458 | 84.9304 | 84.5211 | 84.9283 | 84.5245 | -0.13897 | 0.17376
11.45 | 84.9726 | 84.5462 | 84.9702 | 84.5494 | -0.14427 | 0.17053
11.4542 | 85.0059 | 84.569 | 85.0034 | 84.5721 | -0.14951 | 0.16729
11.4583 | 85.021 | 84.5962 | 85.0184 | 84.5993 | -0.15478 | 0.16402
11.4625 | 85.0183 | 84.623 | 85.0154 | 84.6259 | -0.16012 | 0.16077
11.4667 | 85.014 | 84.6527 | 85.011 | 84.6554 | -0.16551 | 0.15758
11.4708 | 85.0192 | 84.6813 | 85.0159 | 84.684 | -0.17086 | 0.15442
11.475 | 85.0357 | 84.7033 | 85.0322 | 84.7058 | -0.1762 | 0.15128
11.4792 | 85.0498 | 84.718 | 85.0462 | 84.7205 | -0.18145 | 0.14811
11.4833 | 85.0454 | 84.7314 | 85.0415 | 84.7337 | -0.18661 | 0.14496
11.4875 | 85.0334 | 84.7517 | 85.0293 | 84.7539 | -0.19175 | 0.14167
11.4917 | 85.011 | 84.7705 | 85.0067 | 84.7726 | -0.19691 | 0.13842
11.4958 | 84.9814 | 84.7825 | 84.9769 | 84.7845 | -0.20191 | 0.13525
11.5 | 84.9746 | 84.7959 | 84.9698 | 84.7979 | -0.20688 | 0.13209
11.5042 | 84.9885 | 84.8044 | 84.9835 | 84.8062 | -0.21196 | 0.12878
11.5083 | 84.9965 | 84.8154 | 84.9913 | 84.8172 | -0.21692 | 0.12548
11.5125 | 84.9996 | 84.8324 | 84.9941 | 84.8341 | -0.22165 | 0.12225
11.5167 | 84.9936 | 84.8472 | 84.9879 | 84.8488 | -0.22646 | 0.11904
11.5208 | 84.9684 | 84.8554 | 84.9625 | 84.8568 | -0.23141 | 0.11576
11.525 | 84.9552 | 84.86 | 84.949 | 84.8614 | -0.23631 | 0.11249
11.5292 | 84.964 | 84.8647 | 84.9575 | 84.8661 | -0.24114 | 0.10924
11.5333 | 84.9684 | 84.8704 | 84.9617 | 84.8717 | -0.24598 | 0.106
11.5375 | 84.963 | 84.8743 | 84.9559 | 84.8754 | -0.25071 | 0.10275
11.5417 | 84.9595 | 84.8782 | 84.9522 | 84.8793 | -0.25554 | 0.099531
11.5458 | 84.9615 | 84.8867 | 84.9539 | 84.8877 | -0.26053 | 0.096287
11.55 | 84.9703 | 84.8954 | 84.9625 | 84.8964 | -0.26554 | 0.093087
11.5542 | 84.9899 | 84.902 | 84.9817 | 84.9029 | -0.27049 | 0.08991
11.5583 | 84.9889 | 84.913 | 84.9805 | 84.9138 | -0.27538 | 0.086776
11.5625 | 84.9608 | 84.9259 | 84.952 | 84.9266 | -0.28026 | 0.083576
11.5667 | 84.9219 | 84.9368 | 84.9128 | 84.9375 | -0.28516 | 0.080433
11.5708 | 84.8821 | 84.946 | 84.8727 | 84.9467 | -0.29007 | 0.07735
11.575 | 84.8634 | 84.9563 | 84.8537 | 84.9569 | -0.29496 | 0.074267
11.5792 | 84.8676 | 84.9632 | 84.8576 | 84.9637 | -0.29981 | 0.071138
11.5833 | 84.8683 | 84.9715 | 84.8579 | 84.9721 | -0.30458 | 0.068068
11.5875 | 84.8579 | 84.9848 | 84.8473 | 84.9853 | -0.30927 | 0.065037
11.5917 | 84.8379 | 84.9929 | 84.8269 | 84.9934 | -0.31404 | 0.062039
11.5958 | 84.809 | 84.9979 | 84.7977 | 84.9983 | -0.31891 | 0.059053
11.6 | 84.7925 | 85.0044 | 84.7808 | 85.0047 | -0.32377 | 0.056102
11.6042 | 84.7904 | 85.009 | 84.7784 | 85.009 | -0.3286 | 0.053171
11.6083 | 84.7892 | 85.0189 | 84.7768 | 85.0189 | -0.33345 | 0.050265
11.6125 | 84.7851 | 85.0332 | 84.7723 | 85.0332 | -0.3383 | 0.047361
11.6167 | 84.7766 | 85.0428 | 84.7635 | 85.0428 | -0.34323 | 0.044526
11.6208 | 84.7763 | 85.0522 | 84.7628 | 85.0522 | -0.34817 | 0.041741
11.625 | 84.7872 | 85.062 | 84.7733 | 85.062 | -0.35323 | 0.038938
11.6292 | 84.8107 | 85.0678 | 84.7964 | 85.0678 | -0.35822 | 0.036148
11.6333 | 84.8311 | 85.0798 | 84.8164 | 85.0798 | -0.3632 | 0.033414
11.6375 | 84.846 | 85.102 | 84.8309 | 85.102 | -0.36821 | 0.030649
11.6417 | 84.8484 | 85.1165 | 84.8328 | 85.1165 | -0.3733 | 0.027929
11.6458 | 84.842 | 85.1252 | 84.826 | 85.1252 | -0.37835 | 0.025308
11.65 | 84.8514 | 85.1371 | 84.8349 | 85.1371 | -0.38348 | 0.02267
11.6542 | 84.8668 | 85.144 | 84.85 | 85.144 | -0.38863 | 0.019966
11.6583 | 84.8859 | 85.1587 | 84.8686 | 85.1587 | -0.39377 | 0.017306
11.6625 | 84.908 | 85.185 | 84.8902 | 85.185 | -0.39882 | 0.014694
11.6667 | 84.9203 | 85.2074 | 84.9021 | 85.2074 | -0.40396 | 0.012078
11.6708 | 84.9281 | 85.2299 | 84.9094 | 85.2299 | -0.40914 | 0.0094423
11.675 | 84.9403 | 85.251 | 84.9212 | 85.251 | -0.41435 | 0.0068059
11.6792 | 84.9561 | 85.2727 | 84.9365 | 85.2727 | -0.41951 | 0.0041323
11.6833 | 84.9612 | 85.2954 | 84.941 | 85.2954 | -0.42459 | 0.0014833
11.6875 | 84.9497 | 85.3195 | 84.9291 | 85.3195 | -0.42951 | -0.0011845
11.6917 | 84.9367 | 85.3456 | 84.9156 | 85.3456 | -0.43448 | -0.0038262
11.6958 | 84.9322 | 85.374 | 84.9107 | 85.374 | -0.43949 | -0.0064565
11.7 | 84.9392 | 85.4022 | 84.9171 | 85.4022 | -0.44442 | -0.0090299
11.7042 | 84.9603 | 85.4359 | 84.9378 | 85.4359 | -0.44917 | -0.011601
11.7083 | 84.9677 | 85.4684 | 84.9447 | 85.4684 | -0.45384 | -0.014141
11.7125 | 84.9465 | 85.4933 | 84.923 | 85.4933 | -0.45837 | -0.016599
11.7167 | 84.9286 | 85.5217 | 84.9047 | 85.5217 | -0.46291 | -0.01902
11.7208 | 84.9363 | 85.5547 | 84.9118 | 85.5547 | -0.46759 | -0.021502
11.725 | 84.9645 | 85.5894 | 84.9396 | 85.5894 | -0.47222 | -0.023949
11.7292 | 85.0018 | 85.6227 | 84.9764 | 85.6227 | -0.47656 | -0.026232
11.7333 | 85.0321 | 85.6557 | 85.0063 | 85.6557 | -0.48086 | -0.028489
11.7375 | 85.0366 | 85.6869 | 85.0103 | 85.6869 | -0.48529 | -0.030823
11.7417 | 85.0324 | 85.7169 | 85.0057 | 85.7169 | -0.48975 | -0.033113
11.7458 | 85.045 | 85.7529 | 85.0178 | 85.7529 | -0.49411 | -0.035274
11.75 | 85.0699 | 85.7875 | 85.0422 | 85.7875 | -0.49848 | -0.03739
11.7542 | 85.0937 | 85.8164 | 85.0655 | 85.8164 | -0.50275 | -0.039516
11.7583 | 85.1135 | 85.8443 | 85.0848 | 85.8443 | -0.50693 | -0.041581
11.7625 | 85.1281 | 85.8757 | 85.0989 | 85.8757 | -0.51111 | -0.043592
11.7667 | 85.1387 | 85.9083 | 85.109 | 85.9083 | -0.51535 | -0.045562
11.7708 | 85.1618 | 85.9415 | 85.1317 | 85.9415 | -0.51959 | -0.047502
11.775 | 85.1905 | 85.977 | 85.1598 | 85.977 | -0.52374 | -0.049403
11.7792 | 85.212 | 86.0035 | 85.1809 | 86.0035 | -0.52778 | -0.051365
11.7833 | 85.2168 | 86.0288 | 85.1853 | 86.0288 | -0.5317 | -0.053288
11.7875 | 85.2015 | 86.0437 | 85.1694 | 86.0434 | -0.53554 | -0.055265
11.7917 | 85.1903 | 86.0596 | 85.1578 | 86.0593 | -0.53938 | -0.057235
11.7958 | 85.1995 | 86.0804 | 85.1666 | 86.08 | -0.54322 | -0.05925
11.8 | 85.2318 | 86.101 | 85.1984 | 86.1006 | -0.54701 | -0.061226
11.8042 | 85.275 | 86.1184 | 85.2412 | 86.1179 | -0.55065 | -0.063157
11.8083 | 85.3084 | 86.1311 | 85.2741 | 86.1307 | -0.55424 | -0.065068
11.8125 | 85.3231 | 86.1407 | 85.2883 | 86.1402 | -0.55784 | -0.067046
11.8167 | 85.3309 | 86.1504 | 85.2957 | 86.1499 | -0.56149 | -0.069001
11.8208 | 85.3437 | 86.1649 | 85.308 | 86.1644 | -0.56513 | -0.070937
11.825 | 85.3749 | 86.1833 | 85.3388 | 86.1827 | -0.56878 | -0.072866
11.8292 | 85.4151 | 86.1997 | 85.3785 | 86.1991 | -0.57236 | -0.07483
11.8333 | 85.4399 | 86.2115 | 85.4029 | 86.2108 | -0.57589 | -0.076747
11.8375 | 85.4517 | 86.2198 | 85.4142 | 86.2191 | -0.57934 | -0.078663
11.8417 | 85.4574 | 86.2285 | 85.4194 | 86.2278 | -0.58298 | -0.08062
11.8458 | 85.4717 | 86.2392 | 85.4333 | 86.2384 | -0.58669 | -0.082621
11.85 | 85.5045 | 86.2536 | 85.4656 | 86.2528 | -0.59039 | -0.084584
11.8542 | 85.5541 | 86.2725 | 85.5147 | 86.2716 | -0.59404 | -0.086563
11.8583 | 85.5849 | 86.2854 | 85.545 | 86.2845 | -0.59767 | -0.088549
11.8625 | 159.1796 | 86.2916 | 11.9922 | 86.2907 | 0 | -0.090544
11.8667 | 159.6226 | 86.2984 | 11.5484 | 86.2974 | 0 | -0.092553
11.8708 | 95.5634 | 86.3088 | 8.0709 | 86.3078 | 0 | -0.094646
11.875 | 95.6519 | 86.3204 | 7.6029 | 86.3194 | 0 | -0.096736
11.8792 | 124.2051 | 86.3308 | 149.4549 | 86.3298 | 0 | -0.098788
11.8833 | 124.4327 | 86.3407 | 149.8665 | 86.3396 | 0 | -0.10088
11.8875 | 113.3829 | 86.3483 | 153.1541 | 86.3471 | 0 | -0.10308
11.8917 | 113.5522 | 86.3526 | 153.5888 | 86.3514 | 0 | -0.10528
11.8958 | 74.6194 | 86.364 | 16.1937 | 86.3627 | 0 | -0.1075
11.9 | 74.5314 | 86.3704 | 15.7886 | 86.369 | 0 | -0.10973
11.9042 | 112.1553 | 86.3646 | 12.5987 | 86.3632 | 0 | -0.11198
11.9083 | 112.2647 | 86.3617 | 12.1717 | 86.3603 | 0 | -0.11423
11.9125 | 88.0336 | 86.3564 | 145.0942 | 86.3549 | 0 | -0.11656
11.9167 | 88.0474 | 86.3509 | 145.4671 | 86.3493 | 0 | -0.11887
11.9208 | 83.6008 | 86.3539 | 148.4837 | 86.3523 | 0 | -0.1212
11.925 | 83.5606 | 86.3536 | 148.8777 | 86.3519 | 0 | -0.12354
11.9292 | 106.1943 | 86.3426 | 20.0087 | 86.3408 | 0 | -0.12588
11.9333 | 106.294 | 86.3324 | 19.645 | 86.3306 | 0 | -0.12823
11.9375 | 81.6439 | 86.3239 | 16.7112 | 86.322 | 0 | -0.13069
11.9417 | 81.6389 | 86.3147 | 16.3276 | 86.3127 | 0 | -0.13316
11.9458 | 93.5694 | 86.3056 | 141.1324 | 86.3035 | 0 | -0.13556
11.95 | 93.5962 | 86.2933 | 141.4652 | 86.2912 | 0 | -0.13797
11.9542 | 98.5101 | 86.2788 | 144.2396 | 86.2766 | 0 | -0.14051
11.9583 | 98.6153 | 86.2628 | 144.5916 | 86.2605 | 0 | -0.14307
11.9625 | 83.3657 | 86.2616 | 23.4941 | 86.2592 | 0 | -0.14548
11.9667 | 83.3339 | 86.2609 | 23.1633 | 86.2585 | 0 | -0.14788
11.9708 | 98.0937 | 86.2687 | 20.4681 | 86.2662 | 0 | -0.15024
11.975 | 98.1543 | 86.2751 | 20.1191 | 86.2725 | 0 | -0.15257
11.9792 | 92.3142 | 86.2774 | 137.5024 | 86.2747 | 0 | -0.15483
11.9833 | 92.3611 | 86.2825 | 137.8034 | 86.2797 | 0 | -0.15708
11.9875 | 87.9542 | 86.2955 | 140.3519 | 86.2926 | 0 | -0.15942
11.9917 | 87.9503 | 86.3125 | 140.6703 | 86.3095 | 0 | -0.16173
11.9958 | 97.9887 | 86.3349 | 26.7047 | 86.3318 | 0 | -0.16396
12 | 98.0505 | 86.3549 | 26.4013 | 86.3518 | 0 | -0.16618
12.0042 | 89.4086 | 86.356 | 23.9266 | 86.3528 | 0 | -0.16836
12.0083 | 89.4079 | 86.3598 | 23.6067 | 86.3566 | 0 | -0.17056
12.0125 | 92.0694 | 86.3679 | 134.1496 | 86.3645 | 0 | -0.17275
12.0167 | 92.0978 | 86.3788 | 134.4242 | 86.3754 | 0 | -0.17492
12.0208 | 95.7395 | 86.398 | 136.7636 | 86.3945 | 0 | -0.17697
12.025 | 95.8116 | 86.4121 | 137.0541 | 86.4085 | 0 | -0.179
12.0292 | 89.4326 | 86.4188 | 29.6843 | 86.4151 | 0 | -0.18098
12.0333 | 89.4652 | 86.4269 | 29.4046 | 86.4232 | 0 | -0.18297
12.0375 | 77.0298 | 86.4389 | 27.1328 | 86.4351 | 0 | -0.18494
12.0417 | 76.9883 | 86.457 | 26.8384 | 86.4531 | 0 | -0.18689
12.0458 | 91.1957 | 86.4844 | 131.0304 | 86.4804 | 0 | -0.18881
12.05 | 91.2448 | 86.507 | 131.2826 | 86.5029 | 0 | -0.1907
12.0542 | 78.9265 | 86.5198 | 133.4292 | 86.5157 | 0 | -0.19248
12.0583 | 78.8937 | 86.5352 | 133.6952 | 86.531 | 0 | -0.19431
12.0625 | 40.7434 | 86.5533 | 32.4706 | 86.549 | 0 | -0.19617
12.0667 | 40.4821 | 86.5757 | 32.2085 | 86.5714 | 0 | -0.19799
12.0708 | 86.8768 | 86.6088 | 30.1256 | 86.6043 | 0 | -0.19972
12.075 | 86.8979 | 86.6384 | 29.8515 | 86.6339 | 0 | -0.20146
12.0792 | 42.7875 | 86.6582 | 128.1309 | 86.6536 | 0 | -0.20318
12.0833 | 42.5404 | 86.6797 | 128.3625 | 86.675 | 0 | -0.20489
12.0875 | 161.4083 | 86.7076 | 130.334 | 86.7028 | 0 | -0.20663
12.0917 | 161.8515 | 86.7359 | 130.5761 | 86.731 | 0 | -0.20836
12.0958 | 93.9409 | 86.7651 | 35.0731 | 86.7601 | 0 | -0.20999
12.1 | 94.0062 | 86.796 | 34.8306 | 86.791 | 0 | -0.21163
12.1042 | 111.2653 | 86.8226 | 32.9168 | 86.8175 | 0 | -0.21331
12.1083 | 111.3998 | 86.8482 | 32.6651 | 86.8431 | 0 | -0.21496
12.1125 | 113.8687 | 86.882 | 125.426 | 86.8768 | 0 | -0.21659
12.1167 | 114.0015 | 86.9129 | 125.6394 | 86.9075 | 0 | -0.2182
12.1208 | 64.1557 | 86.939 | 127.4495 | 86.9337 | 0 | -0.21977
12.125 | 63.9932 | 86.9673 | 127.6709 | 86.9618 | 0 | -0.22132
12.1292 | 113.8244 | 86.9917 | 37.5044 | 86.9861 | 0 | -0.22287
12.1333 | 113.9466 | 87.0186 | 37.2788 | 87.013 | 0 | -0.2244
12.1375 | 86.8625 | 87.0482 | 35.5212 | 87.0425 | 0 | -0.22589
12.1417 | 86.8546 | 87.0778 | 35.2887 | 87.072 | 0 | -0.22736
12.1458 | 80.9966 | 87.1062 | 122.8982 | 87.1003 | 0 | -0.2288
12.15 | 80.9415 | 87.1337 | 123.0941 | 87.1278 | 0 | -0.23023
12.1542 | 115.054 | 87.1623 | 124.7569 | 87.1563 | 0 | -0.23164
12.1583 | 115.1983 | 87.1917 | 124.9588 | 87.1856 | 0 | -0.23305
12.1625 | 72.5334 | 87.2138 | 39.7788 | 87.2077 | 0 | -0.23436
12.1667 | 72.4666 | 87.2342 | 39.5698 | 87.228 | 0 | -0.23563
12.1708 | 99.0064 | 87.2542 | 37.9546 | 87.248 | 0 | -0.2369
12.175 | 99.0551 | 87.2716 | 37.7405 | 87.2652 | 0 | -0.23816
12.1792 | 100.8857 | 87.2899 | 120.5321 | 87.2835 | 0 | -0.23929
12.1833 | 100.9851 | 87.3049 | 120.711 | 87.2985 | 0 | -0.24042
12.1875 | 75.1316 | 87.3265 | 122.2394 | 87.32 | 0 | -0.24164
12.1917 | 75.0375 | 87.3437 | 122.4228 | 87.3371 | 0 | -0.24286
12.1958 | 108.1142 | 87.3638 | 41.9089 | 87.3572 | 0 | -0.244
12.2 | 108.2249 | 87.3871 | 41.7163 | 87.3803 | 0 | -0.24514
12.2042 | 86.8902 | 87.4058 | 40.2308 | 87.399 | 0 | -0.24638
12.2083 | 86.9006 | 87.4269 | 40.0346 | 87.4201 | 0 | -0.24761
12.2125 | 87.8721 | 87.45 | 118.3141 | 87.4431 | 0 | -0.24879
12.2167 | 87.85 | 87.4702 | 118.4764 | 87.4633 | 0 | -0.24998
12.2208 | 105.2018 | 87.4828 | 119.8823 | 87.4757 | 0 | -0.25117
12.225 | 105.3015 | 87.4974 | 120.0479 | 87.4903 | 0 | -0.25237
12.2292 | 77.3952 | 87.5074 | 43.9059 | 87.5002 | 0 | -0.25352
12.2333 | 77.3202 | 87.5193 | 43.7273 | 87.5121 | 0 | -0.25467
12.2375 | 107.1228 | 87.5362 | 42.3622 | 87.5289 | 0 | -0.25581
12.2417 | 107.2335 | 87.5481 | 42.181 | 87.5407 | 0 | -0.25695
12.2458 | 90.8149 | 87.5637 | 116.2322 | 87.5563 | 0 | -0.25804
12.25 | 90.8523 | 87.58 | 116.3825 | 87.5725 | 0 | -0.25915
12.2542 | 77.7761 | 87.5913 | 117.6724 | 87.5837 | 0 | -0.26026
12.2583 | 77.7211 | 87.6066 | 117.8251 | 87.599 | 0 | -0.26136
12.2625 | 94.1692 | 87.6277 | 45.7867 | 87.62 | 0 | -0.26249
12.2667 | 94.2272 | 87.6449 | 45.616 | 87.6372 | 0 | -0.26362
12.2708 | 76.4575 | 87.6591 | 44.3667 | 87.6512 | 0 | -0.26468
12.275 | 76.4098 | 87.6749 | 44.1923 | 87.667 | 0 | -0.26578
12.2792 | 89.5097 | 87.6883 | 114.2522 | 87.6803 | 0 | -0.26694
12.2833 | 89.5249 | 87.7021 | 114.3963 | 87.694 | 0 | -0.26806
12.2875 | 36.9206 | 87.7203 | 115.5747 | 87.7122 | 0 | -0.26914
12.2917 | 36.647 | 87.7379 | 115.724 | 87.7297 | 0 | -0.27026
12.2958 | 98.8372 | 87.7546 | 47.6045 | 87.7463 | 0 | -0.27141
12.3 | 98.9134 | 87.7716 | 47.4391 | 87.7633 | 0 | -0.27254
12.3042 | 71.2229 | 87.7904 | 46.2972 | 87.7821 | 0 | -0.27366
12.3083 | 71.1259 | 87.8067 | 46.1263 | 87.7983 | 0 | -0.27481
12.3125 | 145.7967 | 87.8178 | 112.3257 | 87.8093 | 0 | -0.27593
12.3167 | 146.1454 | 87.8318 | 112.4662 | 87.8232 | 0 | -0.27706
12.3208 | 98.3763 | 87.849 | 113.542 | 87.8404 | 0 | -0.27823
12.325 | 98.4403 | 87.8657 | 113.6885 | 87.8569 | 0 | -0.27939
12.3292 | 100.3008 | 87.8828 | 49.3659 | 87.874 | 0 | -0.2805
12.3333 | 100.3499 | 87.8972 | 49.2061 | 87.8883 | 0 | -0.28161
12.3375 | 106.5111 | 87.9065 | 48.1612 | 87.8976 | 0 | -0.28275
12.3417 | 106.5909 | 87.9166 | 47.9951 | 87.9076 | 0 | -0.28388
12.3458 | 66.5822 | 87.9307 | 110.456 | 87.9217 | 0 | -0.285
12.35 | 66.4323 | 87.9469 | 110.5917 | 87.9377 | 0 | -0.28613
12.3542 | 109.4395 | 87.9568 | 111.5749 | 87.9476 | 0 | -0.28719
12.3583 | 109.5401 | 87.9671 | 111.7173 | 87.9578 | 0 | -0.28826
12.3625 | 89.5131 | 87.9759 | 51.0681 | 87.9665 | 0 | -0.28935
12.3667 | 89.5125 | 87.9827 | 50.9154 | 87.9733 | 0 | -0.29045
12.3708 | 82.1686 | 87.9971 | 49.9574 | 87.9876 | 0 | -0.29152
12.375 | 82.1242 | 88.0105 | 49.7978 | 88.001 | 0 | -0.29261
12.3792 | 114.7886 | 88.0173 | 108.6451 | 88.0077 | 0 | -0.29365
12.3833 | 114.9232 | 88.0237 | 108.7744 | 88.014 | 0 | -0.29469
12.3875 | 71.3265 | 88.0301 | 109.6747 | 88.0203 | 0 | -0.29575
12.3917 | 71.2462 | 88.0372 | 109.8113 | 88.0274 | 0 | -0.29684
12.3958 | 101.3379 | 88.0472 | 52.7097 | 88.0373 | 0 | -0.29786
12.4 | 101.3942 | 88.0571 | 52.5637 | 88.0471 | 0 | -0.29888
12.4042 | 100.5868 | 88.0717 | 51.6852 | 88.0617 | 0 | -0.29997
12.4083 | 100.6631 | 124.9268 | 51.5319 | 51.2355 | 0 | 0
12.4125 | 71.6743 | 125.0594 | 106.8941 | 51.1198 | 0 | 0
12.4167 | 71.5577 | 92.8824 | 107.0179 | 46.449 | 0 | 0
12.4208 | 113.5434 | 92.9192 | 107.8419 | 46.3015 | 0 | 0
12.425 | 113.6785 | 107.1717 | 107.9732 | 112.6695 | 0 | 0
12.4292 | 86.0022 | 107.2374 | 54.2899 | 112.7564 | 0 | 0
12.4333 | 85.998 | 103.0855 | 54.1498 | 116.8184 | 0 | 0
12.4375 | 84.1238 | 103.1454 | 53.3445 | 116.9323 | 0 | 0
12.4417 | 84.0687 | 84.8076 | 53.1968 | 56.4923 | 0 | 0
12.4458 | 110.9458 | 84.787 | 105.2044 | 56.4017 | 0 | 0
12.45 | 111.0732 | 103.2838 | 105.3234 | 52.7899 | 0 | 0
12.4542 | 72.8525 | 103.3389 | 106.0772 | 52.6762 | 0 | 0
12.4583 | 72.7517 | 92.0133 | 106.2039 | 107.3363 | 0 | 0
12.4625 | 114.4734 | 92.0251 | 55.8078 | 107.4009 | 0 | 0
12.4667 | 114.6179 | 90.1055 | 55.6727 | 110.5441 | 0 | 0
12.4708 | 85.7469 | 90.1147 | 54.935 | 110.6287 | 0 | 0
12.475 | 85.7486 | 100.8331 | 54.7922 | 60.5922 | 0 | 0
12.4792 | 67.448 | 100.8804 | 103.5772 | 60.5226 | 0 | 0
12.4833 | 67.3259 | 89.2957 | 103.6921 | 57.7181 | 0 | 0
12.4875 | 115.9623 | 89.2996 | 104.3812 | 57.6313 | 0 | 0
12.4917 | 116.1361 | 95.0195 | 104.5038 | 103.1695 | 0 | 0
12.4958 | 58.3232 | 95.0523 | 57.263 | 103.2143 | 0 | 0
12.5 | 58.1577 | 97.1971 | 57.132 | 105.6555 | 0 | 0
12.5042 | 96.1674 | 97.2166 | 56.4567 | 105.7153 | 0 | 0
12.5083 | 96.2189 | 90.2341 | 56.3181 | 63.9491 | 0 | 0
12.5125 | 46.2067 | 90.2589 | 102.0146 | 63.8922 | 0 | 0
12.5167 | 45.983 | 97.12 | 102.1255 | 61.7103 | 0 | 0
12.5208 | 103.3132 | 97.1448 | 102.7555 | 61.6431 | 0 | 0
12.525 | 103.395 | 94.3358 | 102.874 | 99.841 | 0 | 0
12.5292 | 93.6871 | 94.3552 | 58.6488 | 99.8727 | 0 | 0
12.5333 | 93.7139 | 92.487 | 58.5236 | 101.7729 | 0 | 0
12.5375 | 126.7994 | 92.509 | 57.9044 | 101.8109 | 0 | 0
12.5417 | 127.0276 | 97.0267 | 57.7709 | 66.7988 | 0 | 0
12.5458 | 101.6231 | 97.0434 | 100.5268 | 66.7502 | 0 | 0
12.55 | 101.6754 | 93.0831 | 100.6306 | 65.0514 | 0 | 0
12.5542 | 92.1788 | 93.1051 | 101.2086 | 64.9967 | 0 | 0
12.5583 | 92.1757 | 94.4467 | 101.3215 | 97.1088 | 0 | 0
12.5625 | 97.2079 | 94.462 | 59.9629 | 97.1316 | 0 | 0
12.5667 | 97.2278 | 95.9761 | 59.8456 | 98.6078 | 0 | 0
12.5708 | 76.0766 | 95.9902 | 59.2759 | 98.6369 | 0 | 0
12.575 | 75.9741 | 93.166 | 59.1488 | 69.2804 | 0 | 0
12.5792 | 101.8817 | 93.1873 | 99.1123 | 69.2379 | 0 | 0
12.5833 | 101.9514 | 86.7107 | 99.2088 | 67.9148 | 0 | 0
12.5875 | 94.6049 | 86.6951 | 99.7396 | 67.8648 | 0 | 0
12.5917 | 94.6202 | 93.8095 | 99.8466 | 94.6383 | 0 | 0
12.5958 | 84.4236 | 93.8262 | 61.2061 | 94.6539 | 0 | 0
12.6 | 84.3904 | 87.1242 | 61.0966 | 95.8031 | 0 | 0
12.6042 | 107.8688 | 87.1199 | 60.5722 | 95.8276 | 0 | 0
12.6083 | 107.9628 | 66.6493 | 60.4514 | 71.5594 | 0 | 0
12.6125 | 78.5241 | 66.5635 | 97.7698 | 71.5223 | 0 | 0
12.6167 | 78.4747 | 90.207 | 97.8592 | 70.489 | 0 | 0
12.6208 | 98.6916 | 90.2213 | 98.3469 | 70.4429 | 0 | 0
12.625 | 98.7281 | 66.5642 | 98.4482 | 92.3251 | 0 | 0
12.6292 | 97.2759 | 66.4869 | 62.3798 | 92.3376 | 0 | 0
12.6333 | 97.3155 | 123.6248 | 62.2778 | 93.2312 | 0 | 0
12.6375 | 76.6905 | 123.7559 | 61.7948 | 93.2529 | 0 | 0
12.6417 | 76.605 | 90.1808 | 61.6802 | 73.59 | 0 | 0
12.6458 | 111.9718 | 90.2092 | 96.4981 | 73.5591 | 0 | 0
12.65 | 112.0913 | 99.23 | 96.5804 | 72.7512 | 0 | 0
12.6542 | 87.7607 | 99.2519 | 97.0289 | 72.7082 | 0 | 0
12.6583 | 87.7532 | 101.5598 | 97.1245 | 90.2612 | 0 | 0
12.6625 | 79.3394 | 101.6169 | 63.4856 | 90.2649 | 0 | 0
12.6667 | 79.253 | 78.3516 | 63.3909 | 90.9612 | 0 | 0
12.6708 | 115.3627 | 78.3044 | 62.9457 | 90.98 | 0 | 0
12.675 | 115.5118 | 102.5827 | 62.837 | 75.3207 | 0 | 0
12.6792 | 76.2877 | 102.629 | 95.2954 | 75.2978 | 0 | 0
12.6833 | 76.2036 | 90.1215 | 95.371 | 74.6623 | 0 | 0
12.6875 | 108.0725 | 90.1311 | 95.7834 | 74.6249 | 0 | 0
12.6917 | 108.1728 | 87.3005 | 95.8738 | 88.4896 | 0 | 0
12.6958 | 86.6788 | 87.2879 | 64.5254 | 88.4897 | 0 | 0
12.7 | 86.6841 | 103.4046 | 64.4374 | 89.0339 | 0 | 0
12.7042 | 63.8008 | 103.4667 | 64.0271 | 89.0481 | 0 | 0
12.7083 | 63.6477 | 83.5347 | 63.9238 | 76.7504 | 0 | 0
12.7125 | 129.2518 | 83.5094 | 94.1596 | 76.7323 | 0 | 0
12.7167 | 129.4903 | 95.8337 | 94.2291 | 76.2304 | 0 | 0
12.7208 | 43.565 | 95.8615 | 94.6084 | 76.1989 | 0 | 0
12.725 | 43.3137 | 96.6806 | 94.6938 | 87.008 | 0 | 0
12.7292 | 103.6184 | 96.7059 | 65.5014 | 87.0045 | 0 | 0
12.7333 | 103.7064 | 84.9207 | 65.4193 | 87.431 | 0 | 0
12.7375 | 60.5558 | 84.9126 | 65.0415 | 87.4403 | 0 | 0
12.7417 | 60.4017 | 99.9861 | 64.9428 | 77.8874 | 0 | 0
12.7458 | 99.7651 | 100.0216 | 93.0887 | 77.8704 | 0 | 0
12.75 | 99.8202 | 90.24 | 93.1528 | 77.4746 | 0 | 0
12.7542 | 112.4898 | 90.2441 | 93.5012 | 77.4464 | 0 | 0
12.7583 | 112.6197 | 90.9711 | 93.5826 | 85.8068 | 0 | 0
12.7625 | 107.7679 | 90.9795 | 66.416 | 85.8035 | 0 | 0
12.7667 | 107.8732 | 98.4813 | 66.3388 | 86.1363 | 0 | 0
12.7708 | 100.9673 | 98.5066 | 65.9913 | 86.143 | 0 | 0
12.775 | 101.0032 | 86.0586 | 65.8964 | 78.726 | 0 | 0
12.7792 | 91.0204 | 86.0521 | 92.0802 | 78.7096 | 0 | 0
12.7833 | 91.0089 | 100.4445 | 92.1399 | 78.3963 | 0 | 0
12.7875 | 85.6243 | 100.4769 | 92.4594 | 78.3713 | 0 | 0
12.7917 | 85.5754 | 91.8101 | 92.5374 | 84.8876 | 0 | 0
12.7958 | 88.7411 | 91.8118 | 67.2716 | 84.8841 | 0 | 0
12.8 | 88.7134 | 87.2352 | 67.1984 | 85.1441 | 0 | 0
12.8042 | 96.5124 | 87.2312 | 66.8794 | 85.1482 | 0 | 0
12.8083 | 96.5591 | 94.8812 | 66.7876 | 79.3479 | 0 | 0
12.8125 | 95.7119 | 94.8897 | 91.1316 | 79.3329 | 0 | 0
12.8167 | 95.7191 | 86.0038 | 91.1878 | 79.0833 | 0 | 0
12.8208 | 88.6135 | 85.9902 | 91.4802 | 79.062 | 0 | 0
12.825 | 88.609 | 93.2107 | 91.5555 | 84.1709 | 0 | 0
12.8292 | 99.9434 | 93.2192 | 68.0707 | 84.1666 | 0 | 0
12.8334 | 99.9932 | 65.2592 | 68.0007 | 84.3704 | 0 | 0
12.8375 | 87.2647 | 65.161 | 67.7085 | 84.3714 | 0 | 0
12.8417 | 87.2498 | 96.2116 | 67.619 | 79.8104 | 0 | 0
12.8458 | 93.5009 | 96.2423 | 90.2404 | 79.7971 | 0 | 0
12.85 | 93.5081 | 79.1907 | 90.2938 | 79.597 | 0 | 0
12.8542 | 93.2491 | 79.1585 | 90.5609 | 79.5792 | 0 | 0
12.8583 | 93.2555 | 114.0329 | 90.6342 | 83.6034 | 0 | 0
12.8625 | 88.644 | 114.1282 | 68.8159 | 83.5978 | 0 | 0
12.8667 | 88.6303 | 91.9286 | 68.7485 | 83.7579 | 0 | 0
12.8708 | 102.9914 | 91.9576 | 68.4813 | 83.7561 | 0 | 0
12.875 | 103.0528 | 93.0899 | 68.3936 | 80.1536 | 0 | 0
12.8792 | 89.7371 | 93.0819 | 89.4041 | 80.1416 | 0 | 0
12.8833 | 89.7309 | 97.5435 | 89.4552 | 79.9806 | 0 | 0
12.8875 | 79.5355 | 97.5864 | 89.6986 | 79.9656 | 0 | 0
12.8917 | 79.4559 | 79.3653 | 89.7705 | 83.1476 | 0 | 0
12.8959 | 116.2526 | 79.3192 | 69.5036 | 83.141 | 0 | 0
12.9 | 116.3988 | 99.5109 | 69.4424 | 83.2668 | 0 | 0
12.9042 | 81.9635 | 99.5395 | 69.1934 | 83.2626 | 0 | 0
12.9083 | 81.9108 | 90.7576 | 69.1122 | 80.4065 | 0 | 0
12.9125 | 93.5716 | 90.7753 | 88.6258 | 80.3954 | 0 | 0
12.9167 | 93.5908 | 86.8898 | 88.672 | 80.2654 | 0 | 0
12.9208 | 96.9204 | 86.8673 | 88.8984 | 80.2525 | 0 | 0
12.925 | 96.9758 | 102.182 | 88.964 | 82.7766 | 0 | 0
12.9292 | 61.4462 | 102.2398 | 70.1313 | 82.7694 | 0 | 0
12.9333 | 61.27 | 82.1863 | 70.0748 | 82.8678 | 0 | 0
12.9375 | 130.9337 | 82.1525 | 69.8425 | 82.8621 | 0 | 0
12.9417 | 131.1792 | 95.7614 | 69.7674 | 80.5903 | 0 | 0
12.9459 | 41.7815 | 95.7833 | 87.909 | 80.5799 | 0 | 0
12.95 | 41.5152 | 95.7105 | 87.951 | 80.4746 | 0 | 0
12.9542 | 106.332 | 95.7365 | 88.1615 | 80.4632 | 0 | 0
12.9584 | 106.4238 | 82.2824 | 88.2215 | 82.4708 | 0 | 0
12.9625 | 74.5732 | 82.2538 | 70.7041 | 82.4632 | 0 | 0
12.9667 | 74.4927 | 101.4129 | 70.6518 | 82.54 | 0 | 0
12.9708 | 95.8014 | 101.456 | 70.4351 | 82.5331 | 0 | 0
12.975 | 95.8291 | 89.1264 | 70.3654 | 80.7209 | 0 | 0
12.9792 | 122.495 | 89.1238 | 87.2477 | 80.7111 | 0 | 0
12.9833 | 122.6711 | 87.6818 | 87.2858 | 80.6255 | 0 | 0
12.9875 | 93.0188 | 87.6723 | 87.4817 | 80.6152 | 0 | 0
12.9917 | 93.0317 | 100.4441 | 87.5366 | 82.2156 | 0 | 0
12.9958 | 99.0327 | 100.4819 | 71.2274 | 82.2078 | 0 | 0
13 | 99.052 | 83.1952 | 71.1789 | 82.2673 | 0 | 0
13.0042 | 92.2569 | 83.1715 | 70.9766 | 82.2597 | 0 | 0
13.0084 | 92.2471 | 102.3898 | 70.9119 | 80.8105 | 0 | 0
13.0125 | 75.65 | 102.4293 | 86.6366 | 80.801 | 0 | 0
13.0167 | 75.551 | 89.141 | 86.6712 | 80.7311 | 0 | 0
13.0209 | 102.7535 | 89.1363 | 86.8535 | 80.7217 | 0 | 0
13.025 | 102.8077 | 82.168 | 86.9038 | 81.9999 | 0 | 0
13.0292 | 91.5866 | 82.1384 | 71.706 | 81.992 | 0 | 0
13.0333 | 91.6032 | 104.7272 | 71.6609 | 82.0378 | 0 | 0
13.0375 | 92.3546 | 104.773 | 71.472 | 82.0298 | 0 | 0
13.0417 | 92.3363 | 77.0174 | 71.4118 | 80.8681 | 0 | 0
13.0458 | 96.9453 | 76.9701 | 86.0708 | 80.8589 | 0 | 0
13.05 | 96.9923 | 96.78 | 86.1023 | 80.8017 | 0 | 0
13.0542 | 91.7154 | 96.7952 | 86.272 | 80.7928 | 0 | 0
13.0583 | 91.715 | 69.3157 | 86.3181 | 81.8154 | 0 | 0
13.0625 | 92.1824 | 69.2331 | 72.144 | 81.8074 | 0 | 0
13.0667 | 92.1812 | 97.5351 | 72.1021 | 81.8423 | 0 | 0
13.0709 | 91.1192 | 97.5663 | 71.9256 | 81.834 | 0 | 0
13.075 | 91.1185 | 88.5848 | 71.8697 | 80.9008 | 0 | 0
13.0792 | 89.6069 | 88.5898 | 85.5463 | 80.892 | 0 | 0
13.0834 | 89.5843 | 104.0846 | 85.575 | 80.8447 | 0 | 0
13.0875 | 102.2159 | 104.136 | 85.733 | 80.8363 | 0 | 0
13.0917 | 102.2782 | 93.9525 | 85.7752 | 81.6555 | 0 | 0
13.0958 | 88.7574 | 93.9799 | 72.5454 | 81.6476 | 0 | 0
13.1 | 88.7345 | 88.873 | 72.5063 | 81.6737 | 0 | 0
13.1042 | 92.8338 | 88.8518 | 72.3414 | 81.6653 | 0 | 0
13.1083 | 92.838 | 93.5351 | 72.2893 | 80.9142 | 0 | 0
13.1125 | 87.4709 | 93.5571 | 85.0593 | 80.9055 | 0 | 0
13.1167 | 87.4405 | 83.9654 | 85.0854 | 80.8664 | 0 | 0
13.1209 | 107.4442 | 83.9362 | 85.2326 | 80.8583 | 0 | 0
13.125 | 107.5302 | 95.0313 | 85.2712 | 81.5154 | 0 | 0
13.1292 | 89.9548 | 95.0418 | 72.9134 | 81.5074 | 0 | 0
13.1334 | 89.9518 | 93.0977 | 72.877 | 81.5266 | 0 | 0
13.1375 | 80.647 | 93.1259 | 72.7226 | 81.5181 | 0 | 0
13.1417 | 80.5911 | 87.1251 | 72.6742 | 80.9124 | 0 | 0
13.1459 | 107.6579 | 87.0984 | 84.6065 | 80.9039 | 0 | 0
13.15 | 107.7591 | 98.1726 | 84.6302 | 80.8713 | 0 | 0
13.1542 | 60.0788 | 98.2145 | 84.7674 | 80.8634 | 0 | 0
13.1583 | 59.8971 | 85.4621 | 84.8028 | 81.3909 | 0 | 0
13.1625 | 126.5356 | 85.4397 | 73.251 | 81.3831 | 0 | 0
13.1667 | 126.7525 | 93.5168 | 73.2171 | 81.3966 | 0 | 0
13.1708 | 49.7416 | 93.5253 | 73.0726 | 81.3882 | 0 | 0
13.175 | 49.5095 | 93.7616 | 73.0275 | 80.8988 | 0 | 0
13.1792 | 102.9404 | 93.7839 | 84.1849 | 80.8905 | 0 | 0
13.1834 | 103.0125 | 84.3063 | 84.2064 | 80.8631 | 0 | 0
13.1875 | 88.4575 | 84.2785 | 84.3344 | 80.8554 | 0 | 0
13.1917 | 88.4488 | 99.6602 | 84.3667 | 81.2792 | 0 | 0
13.1959 | 92.2738 | 99.6973 | 73.561 | 81.2714 | 0 | 0
13.2 | 92.275 | 89.5897 | 73.5294 | 81.2805 | 0 | 0
13.2042 | 122.818 | 89.5883 | 73.394 | 81.2722 | 0 | 0
13.2084 | 122.9953 | 84.6144 | 73.352 | 80.876 | 0 | 0
13.2125 | 87.58 | 84.5896 | 83.7919 | 80.8679 | 0 | 0
13.2167 | 87.5542 | 102.2037 | 83.8114 | 80.8447 | 0 | 0
13.2208 | 93.2275 | 102.2509 | 83.9308 | 80.8371 | 0 | 0
13.225 | 93.2113 | 84.0609 | 83.9603 | 81.1777 | 0 | 0
13.2292 | 93.9059 | 84.0357 | 73.8457 | 81.17 | 0 | 0
13.2334 | 93.907 | 98.397 | 73.8162 | 81.1757 | 0 | 0
13.2375 | 73.5598 | 98.4235 | 73.6893 | 81.1674 | 0 | 0
13.2417 | 73.4585 | 90.3087 | 73.6501 | 80.8462 | 0 | 0
13.2459 | 110.6957 | 90.3091 | 83.4251 | 80.838 | 0 | 0
13.25 | 110.791 | 79.5844 | 83.4427 | 80.815 | 0 | 0
13.2542 | 87.1945 | 79.5403 | 83.5542 | 80.8109 | 0 | 0
13.2584 | 87.1828 | 110.5635 | 83.5811 | 81.0813 | 0 | 0
13.2625 | 89.8917 | 110.636 | 74.1073 | 81.0771 | 0 | 0
13.2667 | 89.8616 | 70.1041 | 74.0799 | 81.0829 | 0 | 0
13.2709 | 105.2138 | 70.0296 | 73.9607 | 81.0689 | 0 | 0
13.275 | 105.3045 | 99.669 | 73.9243 | 80.8165 | 0 | 0
13.2792 | 83.7513 | 99.692 | 83.0824 | 80.7972 | 0 | 0
13.2833 | 83.7016 | 75.4042 | 83.0982 | 80.7832 | 0 | 0
13.2875 | 92.8392 | 75.3523 | 83.2023 | 80.7784 | 0 | 0
13.2917 | 92.8345 | 94.6675 | 83.2269 | 80.9905 | 0 | 0
13.2959 | 94.6366 | 94.6829 | 74.3479 | 80.9961 | 0 | 0
13.3 | 94.6609 | 96.6467 | 74.3222 | 80.9939 | 0 | 0
13.3042 | 85.8764 | 96.6821 | 74.2104 | 80.9816 | 0 | 0
13.3084 | 85.825 | 95.2817 | 74.1764 | 80.7802 | 0 | 0
13.3125 | 110.749 | 95.2953 | 82.7617 | 80.7546 | 0 | 0
13.3167 | 110.8599 | 94.1804 | 82.776 | 80.7461 | 0 | 0
13.3209 | 76.7632 | 94.2024 | 82.8732 | 80.7411 | 0 | 0
13.325 | 76.6752 | 88.5164 | 82.8956 | 80.9074 | 0 | 0
13.3292 | 97.2918 | 88.4994 | 74.569 | 80.9185 | 0 | 0
13.3334 | 97.3129 | 88.725 | 74.545 | 80.9116 | 0 | 0
13.3375 | 97.5089 | 88.7203 | 74.4401 | 80.9002 | 0 | 0
13.3417 | 97.5393 | 89.652 | 74.4083 | 80.7392 | 0 | 0
13.3458 | 90.8985 | 89.6486 | 82.4613 | 80.7104 | 0 | 0
13.35 | 90.8885 | 92.0033 | 82.4742 | 80.7052 | 0 | 0
13.3542 | 102.8934 | 92.0022 | 82.5651 | 80.7001 | 0 | 0
13.3584 | 102.964 | 93.5937 | 82.5854 | 80.8304 | 0 | 0
13.3625 | 70.0089 | 93.6205 | 74.7725 | 80.8441 | 0 | 0
13.3667 | 69.8856 | 88.3095 | 74.75 | 80.8345 | 0 | 0
13.3709 | 113.0369 | 88.2882 | 74.6514 | 80.8238 | 0 | 0
13.375 | 113.1614 | 94.3421 | 74.6217 | 80.6946 | 0 | 0
13.3792 | 64.7412 | 94.3661 | 82.1797 | 80.6649 | 0 | 0
13.3834 | 64.5884 | 89.404 | 82.1913 | 80.6614 | 0 | 0
13.3875 | 116.2164 | 89.3965 | 82.2762 | 80.6564 | 0 | 0
13.3917 | 116.3634 | 90.2986 | 82.2947 | 80.7583 | 0 | 0
13.3959 | 62.7188 | 90.2933 | 74.9596 | 80.7727 | 0 | 0
13.4 | 62.5546 | 92.0899 | 74.9386 | 80.7618 | 0 | 0
13.4042 | 98.7059 | 92.1069 | 74.8459 | 80.7515 | 0 | 0
13.4084 | 98.7538 | 89.5091 | 74.8182 | 80.6475 | 0 | 0
13.4125 | 97.102 | 89.4968 | 81.9154 | 80.6182 | 0 | 0
13.4167 | 97.1292 | 94.4294 | 81.9258 | 80.6155 | 0 | 0
13.4209 | 91.1229 | 94.4475 | 82.0052 | 80.6107 | 0 | 0
13.425 | 91.1191 | 90.8677 | 82.022 | 80.69 | 0 | 0
13.4292 | 118.124 | 90.8714 | 75.1318 | 80.704 | 0 | 0
13.4334 | 118.2741 | 84.1668 | 75.112 | 80.6926 | 0 | 0
13.4375 | 86.9862 | 84.1368 | 75.0249 | 80.6827 | 0 | 0
13.4417 | 86.9433 | 102.0012 | 74.9989 | 80.5986 | 0 | 0
13.4459 | 85.1881 | 102.05 | 81.6671 | 80.5707 | 0 | 0
13.45 | 85.1345 | 86.6012 | 81.6763 | 80.5681 | 0 | 0
13.4542 | 98.0862 | 86.5838 | 81.7506 | 80.5634 | 0 | 0
13.4584 | 98.1132 | 91.1761 | 81.7658 | 80.6251 | 0 | 0
13.4625 | 77.012 | 91.1751 | 75.2902 | 80.6378 | 0 | 0
13.4667 | 76.9324 | 95.7127 | 75.2716 | 80.6265 | 0 | 0
13.4709 | 109.1 | 95.7341 | 75.1896 | 80.6169 | 0 | 0
13.475 | 109.1847 | 77.3848 | 75.1654 | 80.5486 | 0 | 0
13.4792 | 87.2346 | 77.3312 | 81.4335 | 80.5225 | 0 | 0
13.4834 | 87.2209 | 111.2593 | 81.4418 | 80.5197 | 0 | 0
13.4875 | 90.0532 | 111.3365 | 81.5113 | 80.5151 | 0 | 0
13.4917 | 90.0274 | 69.2088 | 81.525 | 80.5627 | 0 | 0
13.4959 | 107.6845 | 69.1302 | 75.4359 | 80.5739 | 0 | 0
13.5 | 107.7809 | 99.5951 | 75.4185 | 80.5629 | 0 | 0
13.5042 | 79.0769 | 99.6158 | 75.3413 | 80.5536 | 0 | 0
13.5084 | 79.0013 | 81.5359 | 75.3186 | 80.4979 | 0 | 0
13.5125 | 91.3769 | 81.5144 | 81.2136 | 80.4737 | 0 | 0
13.5167 | 91.3608 | 91.6362 | 81.221 | 80.4707 | 0 | 0
13.5209 | 102.5032 | 91.6344 | 81.286 | 80.466 | 0 | 0
13.525 | 102.5713 | 101.2022 | 81.2984 | 80.5026 | 0 | 0
13.5292 | 80.5342 | 101.2533 | 75.57 | 80.5121 | 0 | 0
13.5334 | 80.451 | 89.1682 | 75.5535 | 80.5016 | 0 | 0
13.5375 | 112.8015 | 89.1589 | 75.4809 | 80.4925 | 0 | 0
13.5417 | 112.9245 | 93.5526 | 75.4595 | 80.4468 | 0 | 0
13.5459 | 74.1922 | 93.5656 | 81.0064 | 80.4247 | 0 | 0
13.55 | 74.0905 | 89.7415 | 81.0129 | 80.4213 | 0 | 0
13.5542 | 97.559 | 89.735 | 81.0738 | 80.4166 | 0 | 0
13.5584 | 97.5753 | 84.4027 | 81.085 | 80.4444 | 0 | 0
13.5625 | 106.3644 | 84.3755 | 75.6933 | 80.4521 | 0 | 0
13.5667 | 106.4521 | 95.6326 | 75.6778 | 80.4421 | 0 | 0
13.5709 | 75.236 | 95.6562 | 75.6093 | 80.4334 | 0 | 0
13.575 | 75.1344 | 89.6258 | 75.5893 | 80.3957 | 0 | 0
13.5792 | 115.2108 | 89.6157 | 80.811 | 80.3755 | 0 | 0
13.5834 | 115.3464 | 91.747 | 80.8167 | 80.3717 | 0 | 0
13.5875 | 62.5261 | 91.7625 | 80.8737 | 80.367 | 0 | 0
13.5917 | 62.3607 | 91.8205 | 80.8838 | 80.3878 | 0 | 0
13.5959 | 114.4193 | 91.8165 | 75.8066 | 80.3938 | 0 | 0
13.6 | 114.5462 | 90.6584 | 75.792 | 80.3844 | 0 | 0
13.6042 | 73.1539 | 90.6626 | 75.7275 | 80.3759 | 0 | 0
13.6084 | 73.0461 | 91.1778 | 75.7087 | 80.3446 | 0 | 0
13.6125 | 102.3819 | 91.1794 | 80.6264 | 80.3263 | 0 | 0
13.6167 | 102.4483 | 89.2458 | 80.6316 | 80.3221 | 0 | 0
13.6209 | 79.0677 | 89.2365 | 80.6848 | 80.3173 | 0 | 0
13.625 | 78.9928 | 90.487 | 80.694 | 80.3326 | 0 | 0
13.6292 | 93.7028 | 90.495 | 75.9108 | 80.337 | 0 | 0
13.6334 | 93.7167 | 94.9811 | 75.897 | 80.3282 | 0 | 0
13.6375 | 99.0043 | 94.9903 | 75.8362 | 80.32 | 0 | 0
13.6417 | 99.0386 | 87.6816 | 75.8185 | 80.2938 | 0 | 0
13.6459 | 96.4564 | 87.674 | 80.4521 | 80.2772 | 0 | 0
13.65 | 96.4848 | 92.7281 | 80.4566 | 80.2726 | 0 | 0
13.6542 | 107.8453 | 92.7375 | 80.5064 | 80.2678 | 0 | 0
13.6584 | 107.9305 | 87.0129 | 80.5147 | 80.2787 | 0 | 0
13.6625 | 87.256 | 86.9933 | 76.0066 | 80.2817 | 0 | 0
13.6667 | 87.2074 | 97.6081 | 75.9934 | 80.2734 | 0 | 0
13.6709 | 82.0862 | 97.6414 | 75.9361 | 80.2654 | 0 | 0
13.675 | 82.028 | 90.7937 | 75.9194 | 80.2433 | 0 | 0
13.6792 | 101.0912 | 90.7906 | 80.2872 | 80.2283 | 0 | 0
13.6834 | 101.1309 | 84.5873 | 80.2911 | 80.2234 | 0 | 0
13.6875 | 81.6085 | 84.5611 | 80.3378 | 80.2186 | 0 | 0
13.6917 | 81.556 | 101.1617 | 80.3452 | 80.226 | 0 | 0
13.6959 | 102.8588 | 101.2043 | 76.0945 | 80.2277 | 0 | 0
13.7 | 102.9111 | 75.8872 | 76.082 | 80.2198 | 0 | 0
13.7042 | 91.3296 | 75.8287 | 76.0279 | 80.212 | 0 | 0
13.7084 | 91.3321 | 109.0256 | 76.0122 | 80.1933 | 0 | 0
13.7125 | 91.5971 | 109.0929 | 80.1311 | 80.1795 | 0 | 0
13.7167 | 91.585 | 72.738 | 80.1345 | 80.1745 | 0 | 0
13.7209 | 102.6008 | 72.6739 | 80.1782 | 80.1697 | 0 | 0
13.725 | 102.6606 | 96.4814 | 80.1848 | 80.1742 | 0 | 0
13.7292 | 80.7844 | 96.4902 | 76.1751 | 80.1749 | 0 | 0
13.7334 | 80.7205 | 87.8306 | 76.1633 | 80.1673 | 0 | 0
13.7375 | 89.7242 | 87.8364 | 76.1122 | 80.1597 | 0 | 0
13.7417 | 89.6977 | 89.1736 | 76.0974 | 80.1438 | 0 | 0
13.7459 | 108.7862 | 89.1584 | 79.9832 | 80.1312 | 0 | 0
13.75 | 108.8857 | 101.6854 | 79.9862 | 80.126 | 0 | 0
13.7542 | 76.0171 | 101.7366 | 80.0271 | 80.1211 | 0 | 0
13.7584 | 75.9133 | 87.6025 | 80.033 | 80.1235 | 0 | 0
13.7625 | 110.7812 | 87.5894 | 76.249 | 80.1232 | 0 | 0
13.7667 | 110.89 | 90.959 | 76.2378 | 80.1159 | 0 | 0
13.7709 | 79.6481 | 90.9552 | 76.1896 | 80.1086 | 0 | 0
13.775 | 79.5761 | 91.2944 | 76.1756 | 80.0947 | 0 | 0
13.7792 | 91.5535 | 91.3004 | 79.843 | 80.0832 | 0 | 0
13.7834 | 91.5364 | 83.3448 | 79.8455 | 80.0779 | 0 | 0
13.7875 | 115.1938 | 83.3094 | 79.8838 | 80.073 | 0 | 0
13.7917 | 115.3338 | 98.6195 | 79.889 | 80.0736 | 0 | 0
13.7959 | 63.6292 | 98.656 | 76.3168 | 80.0724 | 0 | 0
13.8 | 63.4576 | 87.8459 | 76.3061 | 80.0656 | 0 | 0
13.8042 | 121.8832 | 87.8313 | 76.2606 | 80.0584 | 0 | 0
13.8084 | 122.0568 | 90.2531 | 76.2473 | 80.0462 | 0 | 0
13.8125 | 62.1379 | 90.2574 | 79.71 | 80.0357 | 0 | 0
13.8167 | 61.9697 | 95.4775 | 79.7121 | 80.0303 | 0 | 0
13.8209 | 110.4298 | 95.4913 | 79.7479 | 80.0253 | 0 | 0
13.825 | 110.5272 | 87.1189 | 79.7525 | 80.0246 | 0 | 0
13.8292 | 82.5459 | 87.1055 | 76.3788 | 80.0227 | 0 | 0
13.8334 | 82.4942 | 91.1052 | 76.3686 | 80.0161 | 0 | 0
13.8375 | 91.7146 | 91.1086 | 76.3256 | 80.0091 | 0 | 0
13.8417 | 91.7196 | 91.3753 | 76.313 | 79.9983 | 0 | 0
13.8459 | 91.7382 | 91.374 | 79.5836 | 79.9886 | 0 | 0
13.85 | 91.7265 | 88.1186 | 79.5853 | 79.9831 | 0 | 0
13.8542 | 89.246 | 88.1145 | 79.6189 | 79.9781 | 0 | 0
13.8584 | 89.2349 | 98.4962 | 79.623 | 79.9764 | 0 | 0
13.8625 | 99.0843 | 98.5218 | 76.4354 | 79.9739 | 0 | 0
13.8667 | 99.1204 | 82.8018 | 76.4257 | 79.9677 | 0 | 0
13.8709 | 103.8278 | 82.7731 | 76.385 | 79.9608 | 0 | 0
13.875 | 103.8912 | 94.253 | 76.3731 | 79.9511 | 0 | 0
13.8792 | 93.0923 | 94.2671 | 79.4635 | 79.942 | 0 | 0
13.8834 | 93.0926 | 91.3043 | 79.4649 | 79.9364 | 0 | 0
13.8875 | 90.3689 | 91.3035 | 79.4963 | 79.9314 | 0 | 0
13.8917 | 90.3375 | 90.1282 | 79.4999 | 79.9289 | 0 | 0
13.8959 | 84.6836 | 90.1312 | 76.4871 | 79.926 | 0 | 0
13.9 | 84.6473 | 96.9786 | 76.4779 | 79.92 | 0 | 0
13.9042 | 98.5523 | 96.9981 | 76.4394 | 79.9132 | 0 | 0
13.9084 | 98.574 | 79.2882 | 76.4281 | 79.9045 | 0 | 0
13.9125 | 87.2987 | 79.2435 | 79.3492 | 79.896 | 0 | 0
13.9167 | 87.2797 | 103.9557 | 79.3503 | 79.8903 | 0 | 0
13.9209 | 97.1935 | 104.0078 | 79.3797 | 79.8853 | 0 | 0
13.925 | 97.2164 | 77.2557 | 79.3828 | 79.8822 | 0 | 0
13.9292 | 95.2008 | 77.2044 | 76.5343 | 79.8788 | 0 | 0
13.9334 | 95.216 | 104.0514 | 76.5255 | 79.873 | 0 | 0
13.9375 | 93.7641 | 104.0968 | 76.4891 | 79.8665 | 0 | 0
13.9417 | 93.7704 | 78.4968 | 76.4783 | 79.8584 | 0 | 0
13.9459 | 92.6303 | 78.4573 | 79.2404 | 79.8504 | 0 | 0
13.95 | 92.6279 | 92.9974 | 79.2413 | 79.8447 | 0 | 0
13.9542 | 89.1451 | 92.9933 | 79.2688 | 79.8397 | 0 | 0
13.9584 | 89.1286 | 92.0346 | 79.2715 | 79.8361 | 0 | 0
13.9625 | 87.338 | 92.0556 | 76.5772 | 79.8325 | 0 | 0
13.9667 | 87.2988 | 88.222 | 76.5687 | 79.8269 | 0 | 0
13.9709 | 109.773 | 88.2033 | 76.5343 | 79.8205 | 0 | 0
13.975 | 109.8742 | 99.9573 | 76.5241 | 79.8129 | 0 | 0
13.9792 | 77.3597 | 99.9986 | 79.1368 | 79.8054 | 0 | 0
13.9834 | 77.2692 | 88.3609 | 79.1374 | 79.7997 | 0 | 0
13.9875 | 103.9786 | 88.3532 | 79.1631 | 79.7947 | 0 | 0
13.9917 | 104.043 | 87.248 | 79.1654 | 79.7908 | 0 | 0
13.9959 | 89.408 | 87.2256 | 76.6161 | 79.7869 | 0 | 0
14 | 89.3921 | 93.8102 | 76.6081 | 79.7814 | 0 | 0
14.0042 | 83.5445 | 93.8305 | 76.5754 | 79.7752 | 0 | 0
14.0084 | 83.4838 | 84.5118 | 76.5657 | 79.7681 | 0 | 0
14.0125 | 121.1172 | 84.4784 | 79.038 | 79.7609 | 0 | 0
14.0167 | 121.2869 | 97.2782 | 79.0383 | 79.7552 | 0 | 0
14.0209 | 57.8017 | 97.31 | 79.0624 | 79.7503 | 0 | 0
14.025 | 57.5992 | 88.4358 | 79.0644 | 79.7461 | 0 | 0
14.0292 | 123.2984 | 88.4266 | 76.6514 | 79.742 | 0 | 0
14.0334 | 123.4798 | 89.8117 | 76.6437 | 79.7366 | 0 | 0
14.0375 | 66.6465 | 89.8077 | 76.6128 | 79.7305 | 0 | 0
14.0417 | 66.4974 | 96.4207 | 76.6036 | 79.7238 | 0 | 0
14.0459 | 102.4086 | 96.443 | 78.9437 | 79.717 | 0 | 0
14.05 | 102.4626 | 85.5165 | 78.9438 | 79.7114 | 0 | 0
14.0542 | 93.3945 | 85.4947 | 78.9664 | 79.7064 | 0 | 0
14.0584 | 93.4062 | 90.0469 | 78.968 | 79.702 | 0 | 0
14.0625 | 84.4301 | 90.0458 | 76.6833 | 79.6977 | 0 | 0
14.0667 | 84.3867 | 95.2058 | 76.6759 | 79.6925 | 0 | 0
14.0709 | 96.4967 | 95.221 | 76.6466 | 79.6866 | 0 | 0
14.075 | 96.5108 | 85.0451 | 76.6378 | 79.6802 | 0 | 0
14.0792 | 90.8155 | 85.0267 | 78.8536 | 79.6737 | 0 | 0
14.0834 | 90.8155 | 99.5485 | 78.8536 | 79.6681 | 0 | 0
14.0875 | 97.272 | 99.58 | 78.8747 | 79.6631 | 0 | 0
14.0917 | 97.2953 | 82.1543 | 78.876 | 79.6586 | 0 | 0
14.0959 | 107.1121 | 82.1214 | 76.7121 | 79.6542 | 0 | 0
14.1 | 107.191 | 93.3315 | 76.7049 | 79.649 | 0 | 0
14.1042 | 81.5621 | 93.342 | 76.6772 | 79.6432 | 0 | 0
14.1084 | 81.5032 | 95.9284 | 76.6688 | 79.6371 | 0 | 0
14.1125 | 95.0729 | 95.9475 | 78.7675 | 79.6309 | 0 | 0
14.1167 | 95.0655 | 82.8461 | 78.7673 | 79.6254 | 0 | 0
14.1209 | 88.8198 | 82.8181 | 78.7871 | 79.6204 | 0 | 0
14.125 | 88.8119 | 102.646 | 78.7881 | 79.6158 | 0 | 0
14.1292 | 92.4334 | 102.6873 | 76.7379 | 79.6113 | 0 | 0
14.1334 | 92.4212 | 75.9798 | 76.731 | 79.6062 | 0 | 0
14.1375 | 93.8186 | 75.9253 | 76.7047 | 79.6005 | 0 | 0
14.1417 | 93.8351 | 104.2344 | 76.6967 | 79.5946 | 0 | 0
14.1459 | 94.3145 | 104.2842 | 78.6853 | 79.5886 | 0 | 0
14.15 | 94.3251 | 80.7464 | 78.6849 | 79.5832 | 0 | 0
14.1542 | 95.1622 | 80.7115 | 78.7034 | 79.5782 | 0 | 0
14.1584 | 95.1688 | 97.5277 | 78.7041 | 79.5736 | 0 | 0
14.1625 | 96.986 | 97.5455 | 76.761 | 79.569 | 0 | 0
14.1667 | 97.0175 | 85.3643 | 76.7544 | 79.5639 | 0 | 0
14.1709 | 82.5106 | 85.3529 | 76.7294 | 79.5584 | 0 | 0
14.175 | 82.4467 | 89.747 | 76.7218 | 79.5527 | 0 | 0
14.1792 | 99.5649 | 89.7317 | 78.6065 | 79.5469 | 0 | 0
14.1834 | 99.6047 | 93.3446 | 78.606 | 79.5415 | 0 | 0
14.1875 | 84.8474 | 93.3674 | 78.6233 | 79.5366 | 0 | 0
14.1917 | 84.7993 | 90.3382 | 78.6238 | 79.5319 | 0 | 0
14.1959 | 106.2456 | 90.3306 | 76.7816 | 79.5273 | 0 | 0
14.2 | 106.3213 | 95.8774 | 76.7752 | 79.5223 | 0 | 0
14.2042 | 84.6581 | 95.8981 | 76.7515 | 79.5169 | 0 | 0
14.2084 | 84.6125 | 89.4468 | 76.7442 | 79.5114 | 0 | 0
14.2125 | 92.6854 | 89.4465 | 78.5311 | 79.5057 | 0 | 0
14.2167 | 92.6835 | 85.6476 | 78.5304 | 79.5005 | 0 | 0
14.2209 | 101.7107 | 85.6169 | 78.5466 | 79.4955 | 0 | 0
14.225 | 101.7636 | 95.438 | 78.5469 | 79.4909 | 0 | 0
14.2292 | 75.7845 | 95.4655 | 76.7998 | 79.4862 | 0 | 0
14.2334 | 75.6803 | 86.0714 | 76.7937 | 79.4813 | 0 | 0
14.2375 | 121.8865 | 86.0452 | 76.7712 | 79.476 | 0 | 0
14.2417 | 122.0595 | 94.2204 | 76.7641 | 79.4706 | 0 | 0
14.2459 | 60.6291 | 94.239 | 78.4588 | 79.4651 | 0 | 0
14.25 | 60.445 | 90.797 | 78.458 | 79.4599 | 0 | 0
14.2542 | 117.8613 | 90.7986 | 78.4731 | 79.455 | 0 | 0
14.2584 | 118.0066 | 89.7766 | 78.4732 | 79.4503 | 0 | 0
14.2625 | 73.2228 | 89.7683 | 76.8158 | 79.4457 | 0 | 0
14.2667 | 73.1083 | 94.2971 | 76.8099 | 79.4408 | 0 | 0
14.2709 | 96.7854 | 94.3152 | 76.7885 | 79.4356 | 0 | 0
14.275 | 96.8129 | 87.0477 | 76.7818 | 79.4303 | 0 | 0
14.2792 | 100.8102 | 87.0295 | 78.3895 | 79.425 | 0 | 0
14.2834 | 100.8579 | 88.3845 | 78.3886 | 79.4199 | 0 | 0
14.2875 | 79.4729 | 88.3763 | 78.4027 | 79.4151 | 0 | 0
14.2917 | 79.3953 | 98.3525 | 78.4026 | 79.4104 | 0 | 0
14.2959 | 97.5708 | 98.383 | 76.8298 | 79.4057 | 0 | 0
14.3 | 97.5942 | 82.8447 | 76.8241 | 79.4009 | 0 | 0
14.3042 | 96.9964 | 82.8144 | 76.8038 | 79.3958 | 0 | 0
14.3084 | 97.026 | 98.4671 | 76.7974 | 79.3906 | 0 | 0
14.3125 | 91.7477 | 98.4954 | 78.3229 | 79.3854 | 0 | 0
14.3167 | 91.7405 | 85.1829 | 78.3219 | 79.3804 | 0 | 0
14.3209 | 107.0798 | 85.1618 | 78.3351 | 79.3756 | 0 | 0
14.325 | 107.1561 | 89.6208 | 78.3349 | 79.3709 | 0 | 0
14.3292 | 77.5638 | 89.6164 | 76.842 | 79.3663 | 0 | 0
14.3334 | 77.4818 | 100.746 | 76.8365 | 79.3615 | 0 | 0
14.3375 | 97.2937 | 100.7848 | 76.8171 | 79.3566 | 0 | 0
14.3417 | 97.2985 | 77.3476 | 76.8109 | 79.3515 | 0 | 0
14.3459 | 92.4745 | 77.2968 | 78.259 | 79.3464 | 0 | 0
14.35 | 92.489 | 105.6947 | 78.258 | 79.3414 | 0 | 0
14.3542 | 87.0423 | 105.7478 | 78.2703 | 79.3367 | 0 | 0
14.3584 | 87.0014 | 76.0225 | 78.2699 | 79.332 | 0 | 0
14.3625 | 98.9133 | 75.9713 | 76.8523 | 79.3274 | 0 | 0
14.3667 | 98.954 | 101.6744 | 76.847 | 79.3227 | 0 | 0
14.3709 | 94.4897 | 101.7098 | 76.8286 | 79.3178 | 0 | 0
14.375 | 94.5037 | 85.2068 | 76.8227 | 79.3128 | 0 | 0
14.3792 | 90.5347 | 85.1927 | 78.1977 | 79.3078 | 0 | 0
14.3834 | 90.5106 | 92.1147 | 78.1965 | 79.303 | 0 | 0
14.3875 | 101.8667 | 92.11 | 78.208 | 79.2983 | 0 | 0
14.3917 | 101.9292 | 90.445 | 78.2075 | 79.2937 | 0 | 0
14.3959 | 75.0946 | 90.4529 | 76.8611 | 79.2891 | 0 | 0
14.4 | 74.9857 | 87.6071 | 76.8559 | 79.2844 | 0 | 0
14.4042 | 106.8399 | 87.587 | 76.8384 | 79.2796 | 0 | 0
14.4084 | 106.9194 | 93.4489 | 76.8327 | 79.2747 | 0 | 0
14.4125 | 85.3081 | 93.467 | 78.1386 | 79.2698 | 0 | 0
14.4167 | 85.2683 | 93.5956 | 78.1374 | 79.265 | 0 | 0
14.4209 | 98.561 | 93.6045 | 78.1481 | 79.2604 | 0 | 0
14.425 | 98.5868 | 90.114 | 78.1475 | 79.2558 | 0 | 0
14.4292 | 95.4073 | 90.1086 | 76.8683 | 79.2512 | 0 | 0
14.4334 | 95.4279 | 91.3523 | 76.8633 | 79.2466 | 0 | 0
14.4375 | 80.9657 | 91.3613 | 76.8467 | 79.2419 | 0 | 0
14.4417 | 80.896 | 86.5293 | 76.8412 | 79.2371 | 0 | 0
14.4459 | 111.9621 | 86.5016 | 78.0818 | 79.2323 | 0 | 0
14.45 | 112.0683 | 94.2842 | 78.0805 | 79.2276 | 0 | 0
14.4542 | 70.5224 | 94.3065 | 78.0905 | 79.2229 | 0 | 0
14.4584 | 70.3928 | 88.276 | 78.0898 | 79.2184 | 0 | 0
14.4625 | 119.4842 | 88.2615 | 76.8741 | 79.2139 | 0 | 0
14.4667 | 119.6421 | 91.7796 | 76.8693 | 79.2093 | 0 | 0
14.4709 | 68.6885 | 91.7852 | 76.8535 | 79.2047 | 0 | 0
14.475 | 68.5468 | 92.4941 | 76.8481 | 79.2 | 0 | 0
14.4792 | 106.487 | 92.5042 | 78.0271 | 79.1952 | 0 | 0
14.4834 | 106.5667 | 90.4135 | 78.0257 | 79.1906 | 0 | 0
14.4875 | 83.068 | 90.4064 | 78.0351 | 79.186 | 0 | 0
14.4917 | 83.0104 | 90.3452 | 78.0342 | 79.1815 | 0 | 0
14.4959 | 94.3412 | 90.3486 | 76.8786 | 79.1771 | 0 | 0
14.5 | 94.3556 | 91.0166 | 76.874 | 79.1725 | 0 | 0
14.5042 | 100.0946 | 91.0131 | 76.8589 | 79.1679 | 0 | 0
14.5084 | 100.134 | 86.4452 | 76.8537 | 79.1633 | 0 | 0
14.5125 | 80.6667 | 86.4297 | 77.9744 | 79.1587 | 0 | 0
14.5167 | 80.5978 | 99.3384 | 77.973 | 79.1541 | 0 | 0
14.5209 | 97.1879 | 99.3742 | 77.9817 | 79.1496 | 0 | 0
14.525 | 97.2123 | 83.3132 | 77.9807 | 79.1451 | 0 | 0
14.5292 | 101.6553 | 83.2819 | 76.882 | 79.1407 | 0 | 0
14.5334 | 101.7047 | 95.0396 | 76.8774 | 79.1362 | 0 | 0
14.5375 | 86.2654 | 95.0559 | 76.863 | 79.1317 | 0 | 0
14.5417 | 86.2329 | 90.3916 | 76.8581 | 79.1271 | 0 | 0
14.5459 | 105.2991 | 90.3912 | 77.9236 | 79.1226 | 0 | 0
14.55 | 105.36 | 84.8952 | 77.9221 | 79.118 | 0 | 0
14.5542 | 79.3842 | 84.8715 | 77.9303 | 79.1136 | 0 | 0
14.5584 | 79.3126 | 104.3415 | 77.9292 | 79.1092 | 0 | 0
14.5625 | 96.3722 | 104.3944 | 76.8841 | 79.1048 | 0 | 0
14.5667 | 96.3772 | 74.6671 | 76.8797 | 79.1004 | 0 | 0
14.5709 | 94.7691 | 74.6062 | 76.866 | 79.0959 | 0 | 0
14.575 | 94.7934 | 105.9143 | 76.8612 | 79.0914 | 0 | 0
14.5792 | 85.3985 | 105.967 | 77.8746 | 79.0869 | 0 | 0
14.5834 | 85.3521 | 78.5448 | 77.8731 | 79.0825 | 0 | 0
14.5875 | 100.2552 | 78.5064 | 77.8806 | 79.0781 | 0 | 0
14.5917 | 100.2983 | 97.2693 | 77.8795 | 79.0737 | 0 | 0
14.5959 | 96.9906 | 97.2841 | 76.8853 | 79.0694 | 0 | 0
14.6 | 97.0203 | 90.2463 | 76.881 | 79.065 | 0 | 0
14.6042 | 83.8257 | 90.2543 | 76.8679 | 79.0606 | 0 | 0
14.6084 | 83.7619 | 88.2156 | 76.8633 | 79.0562 | 0 | 0
14.6125 | 106.7417 | 88.1956 | 77.8273 | 79.0518 | 0 | 0
14.6167 | 106.8301 | 92.2124 | 77.8258 | 79.0474 | 0 | 0
14.6209 | 71.9433 | 92.2254 | 77.8328 | 79.043 | 0 | 0
14.625 | 71.8184 | 88.513 | 77.8316 | 79.0387 | 0 | 0
14.6292 | 108.8582 | 88.5009 | 76.8854 | 79.0344 | 0 | 0
14.6334 | 108.9478 | 92.3429 | 76.8813 | 79.0301 | 0 | 0
14.6375 | 89.3577 | 92.3502 | 76.8688 | 79.0258 | 0 | 0
14.6417 | 89.3424 | 95.4791 | 76.8643 | 79.0214 | 0 | 0
14.6459 | 88.1434 | 95.5 | 77.7816 | 79.0171 | 0 | 0
14.65 | 88.109 | 85.8683 | 77.7801 | 79.0127 | 0 | 0
14.6542 | 107.7349 | 85.8439 | 77.7866 | 79.0084 | 0 | 0
14.6584 | 107.8298 | 93.3081 | 77.7853 | 79.0042 | 0 | 0
14.6625 | 70.7458 | 93.3239 | 76.8847 | 78.9999 | 0 | 0
14.6667 | 70.6132 | 88.1771 | 76.8806 | 78.9957 | 0 | 0
14.6709 | 116.8801 | 88.1585 | 76.8687 | 78.9914 | 0 | 0
14.675 | 117.0133 | 91.5156 | 76.8644 | 78.9871 | 0 | 0
14.6792 | 71.8462 | 91.5249 | 77.7375 | 78.9828 | 0 | 0
14.6834 | 71.7306 | 90.947 | 77.7359 | 78.9785 | 0 | 0
14.6875 | 113.0718 | 90.9455 | 77.7419 | 78.9743 | 0 | 0
14.6917 | 113.1874 | 90.6344 | 77.7406 | 78.9701 | 0 | 0
14.6959 | 77.0474 | 90.6327 | 76.8831 | 78.9659 | 0 | 0
14.7 | 76.9508 | 92.124 | 76.8792 | 78.9617 | 0 | 0
14.7042 | 96.4529 | 92.1343 | 76.8678 | 78.9574 | 0 | 0
14.7084 | 96.4794 | 92.2015 | 76.8636 | 78.9532 | 0 | 0
14.7125 | 92.9505 | 92.2007 | 77.6948 | 78.9489 | 0 | 0
14.7167 | 92.9457 | 86.0736 | 77.6932 | 78.9447 | 0 | 0
14.7209 | 92.3176 | 86.0592 | 77.6988 | 78.9405 | 0 | 0
14.725 | 92.3207 | 95.3898 | 77.6974 | 78.9364 | 0 | 0
14.7292 | 94.7532 | 95.405 | 76.8808 | 78.9322 | 0 | 0
14.7334 | 94.7625 | 85.1489 | 76.8769 | 78.9281 | 0 | 0
14.7375 | 88.098 | 85.128 | 76.8661 | 78.9239 | 0 | 0
14.7417 | 88.0678 | 97.8992 | 76.862 | 78.9197 | 0 | 0
14.7459 | 94.1797 | 97.9291 | 77.6535 | 78.9155 | 0 | 0
14.75 | 94.191 | 86.5896 | 77.6519 | 78.9114 | 0 | 0
14.7542 | 103.0646 | 86.5705 | 77.6571 | 78.9072 | 0 | 0
14.7584 | 103.1184 | 89.7656 | 77.6556 | 78.9031 | 0 | 0
14.7625 | 84.5084 | 89.7622 | 76.8777 | 78.899 | 0 | 0
14.7667 | 84.4694 | 96.4231 | 76.874 | 78.8949 | 0 | 0
14.7709 | 101.4032 | 96.4459 | 76.8636 | 78.8908 | 0 | 0
14.775 | 101.4385 | 80.5829 | 76.8597 | 78.8867 | 0 | 0
14.7792 | 84.3605 | 80.5427 | 77.6136 | 78.8825 | 0 | 0
14.7834 | 84.3178 | 105.6769 | 77.6119 | 78.8784 | 0 | 0
14.7875 | 94.0924 | 105.7339 | 77.6166 | 78.8744 | 0 | 0
14.7917 | 94.0906 | 75.6658 | 77.6152 | 78.8703 | 0 | 0
14.7959 | 94.751 | 75.6103 | 76.8739 | 78.8662 | 0 | 0
14.8 | 94.7688 | 102.9469 | 76.8685 | 78.8622 | 0 | 0
14.8042 | 88.6311 | 102.9863 | 76.8585 | 78.8581 | 0 | 0
14.8084 | 88.608 | 82.368 | 76.8548 | 78.854 | 0 | 0
14.8125 | 96.8924 | 82.3468 | 77.573 | 78.85 | 0 | 0
14.8167 | 96.9122 | 93.5953 | 77.5749 | 78.8459 | 0 | 0
14.8209 | 100.874 | 93.5937 | 77.5795 | 78.8419 | 0 | 0
14.825 | 100.925 | 93.7001 | 77.5778 | 78.8379 | 0 | 0
14.8292 | 78.0438 | 93.722 | 76.8733 | 78.8339 | 0 | 0
14.8334 | 77.9486 | 85.8154 | 76.8627 | 78.8298 | 0 | 0
14.8375 | 109.0412 | 85.7882 | 76.8547 | 78.8258 | 0 | 0
14.8417 | 109.1405 | 92.2313 | 76.8496 | 78.8218 | 0 | 0
14.8459 | 74.5141 | 92.2409 | 77.5319 | 78.8178 | 0 | 0
14.85 | 74.4071 | 91.5579 | 77.539 | 78.8138 | 0 | 0
14.8542 | 104.5299 | 91.5618 | 77.5416 | 78.8098 | 0 | 0
14.8584 | 104.5907 | 89.6603 | 77.5415 | 78.8058 | 0 | 0
14.8625 | 96.1932 | 89.6524 | 76.8717 | 78.8019 | 0 | 0
14.8667 | 96.2194 | 96.1285 | 76.8564 | 78.7979 | 0 | 0
14.8709 | 78.947 | 96.1554 | 76.8503 | 78.794 | 0 | 0
14.875 | 78.8621 | 84.7543 | 76.8438 | 78.79 | 0 | 0
14.8792 | 116.8962 | 84.7239 | 77.4924 | 78.786 | 0 | 0
14.8834 | 117.0389 | 93.6378 | 77.5041 | 78.7821 | 0 | 0
14.8875 | 63.7157 | 93.6533 | 77.5049 | 78.7782 | 0 | 0
14.8917 | 63.5421 | 89.8989 | 77.5061 | 78.7742 | 0 | 0
14.8959 | 118.3325 | 89.8916 | 76.8693 | 78.7703 | 0 | 0
14.9 | 118.478 | 89.1672 | 76.8498 | 78.7664 | 0 | 0
14.9042 | 78.0035 | 89.1631 | 76.8454 | 78.7625 | 0 | 0
14.9084 | 77.9219 | 92.7207 | 76.8377 | 78.7586 | 0 | 0
14.9125 | 101.9974 | 92.7289 | 77.4543 | 78.7547 | 0 | 0
14.9167 | 102.0467 | 91.0592 | 77.47 | 78.7508 | 0 | 0
14.9209 | 86.0614 | 91.0582 | 77.4693 | 78.7469 | 0 | 0
14.925 | 86.0185 | 89.755 | 77.4717 | 78.743 | 0 | 0
14.9292 | 91.3656 | 89.7555 | 76.8661 | 78.7391 | 0 | 0
14.9334 | 91.3634 | 94.8679 | 76.8428 | 78.7353 | 0 | 0
14.9375 | 97.0918 | 94.8781 | 76.8399 | 78.7314 | 0 | 0
14.9417 | 97.1081 | 82.7758 | 76.8312 | 78.7275 | 0 | 0
14.9459 | 92.3037 | 82.7476 | 77.4174 | 78.7237 | 0 | 0
14.95 | 92.3076 | 98.196 | 77.4369 | 78.7198 | 0 | 0
14.9542 | 89.1468 | 98.2237 | 77.4348 | 78.716 | 0 | 0
14.9584 | 89.1228 | 85.6149 | 77.4368 | 78.7122 | 0 | 0
14.9625 | 96.5237 | 85.5953 | 76.8622 | 78.7083 | 0 | 0
14.9667 | 96.5385 | 94.1611 | 76.8341 | 78.7045 | 0 | 0
14.9709 | 90.3831 | 94.1756 | 76.8339 | 78.7007 | 0 | 0
14.975 | 90.38 | 91.7902 | 76.8259 | 78.6969 | 0 | 0
14.9792 | 101.8023 | 91.7919 | 77.3819 | 78.6931 | 0 | 0
14.9834 | 101.8407 | 84.1799 | 77.4061 | 78.6893 | 0 | 0
14.9875 | 86.3306 | 84.1551 | 77.4013 | 78.6855 | 0 | 0
14.9917 | 86.3023 | 101.2435 | 77.4029 | 78.6817 | 0 | 0
14.9959 | 96.5051 | 101.2841 | 76.8577 | 78.6779 | 0 | 0
1
2
3
Exit of
Check Valve C
Inlet of
Check Valve C

## Main Path Pressure Profile
Transient Maximum and Minimum pressures (m H2O abs) along pipes
| 4QBEP |  | 4QOP
Length (m) | Max | Min | Max | Min | Graph Points
0 | 75.0021 | 74.5843 | 75.0021 | 74.8621 | Check Valve
5 | 145.3116 | 2.9335 | 107.2287 | 40.4519 | 10 | 45
5 | 151.7276 | 9.5756 | 114.8443 | 48.7107 | 10 | 200
10 | 153.5888 | 7.6029 | 116.9323 | 46.3015
10 | 161.8515 | 36.647 | 125.0594 | 65.161 | Pump
15 | 127.9246 | 59.6865 | 108.9884 | 76.8413 | 5 | 20
15 | 127.5932 | 59.3417 | 108.9199 | 76.7686 | 5 | 200
20 | 127.6244 | 52.9858 | 109.0361 | 72.6126
25 | 131.6492 | 51.0149 | 109.1415 | 72.7384 | Atmospheric
30 | 128.2857 | 52.4219 | 109.2436 | 74.6683 | 0 | 10.3
35 | 128.5726 | 54.3297 | 109.3476 | 74.3904 | 130 | 10.3
40 | 130.5153 | 55.91 | 109.4455 | 75.1177
45 | 129.1632 | 51.3328 | 109.5459 | 73.7712
50 | 129.4525 | 56.2067 | 109.6514 | 75.1568
55 | 129.7213 | 55.7128 | 109.7528 | 74.9548
60 | 129.9988 | 52.0583 | 109.8577 | 73.7143
65 | 130.2922 | 58.4952 | 109.958 | 76.1305
70 | 130.5741 | 54.2655 | 110.0642 | 74.1861
75 | 130.843 | 53.8802 | 110.1695 | 74.3267
80 | 131.1127 | 60.1536 | 110.2707 | 76.8248
85 | 131.3942 | 51.9906 | 110.3732 | 72.9731
90 | 131.6494 | 58.5893 | 110.4754 | 75.9862
95 | 131.8837 | 58.7834 | 110.5716 | 75.7754
100 | 134.0576 | 51.0169 | 110.6689 | 72.1797
105 | 132.4091 | 62.9367 | 110.7636 | 78.878
110 | 132.6787 | 56.3249 | 110.8549 | 74.9827
115 | 126.6277 | 59.7164 | 106.5494 | 75.3707
115 | 126.8065 | 59.8942 | 106.5864 | 75.4083
120 | 123.293 | 69.4621 | 106.0248 | 80.0187
120 | 123.293 | 69.4621 | 106.0248 | 80.0187
125 | 123.9274 | 66.8643 | 106.1886 | 78.369
125 | 120.56 | 63.7775 | 105.5027 | 77.7212
130 | 90.0025 | 89.6785 | 90.0025 | 89.894