## Manufacturer Curve
Grundfos 1220-A/B KP double suction, horizontal split case pump operating at 893 RPM with a 472 mm impeller trim
Raw Data |  |  | Third Order Polynomial Curve Fit
Flow (m3/s) | Head (m) | Power (kW) | Flow (m3/s) | Head (m) | Power (kW) | Curve Constants
0 | 29.1431 |  | 0 | 28.8581 | 51.4766 | Head
0.0098897 | 29.1658 | 53.4297 | 0.01 | 28.9986 | 52.8342 | a | 28.8581
0.019779 | 29.196 | 54.5557 | 0.02 | 29.1245 | 54.1959 | b | 14.7834
0.029669 | 29.2315 | 55.7176 | 0.03 | 29.2357 | 55.5608 | c | -73.3227
0.039559 | 29.2703 | 56.9126 | 0.04 | 29.3323 | 56.9278 | d | 2.1696
0.049448 | 29.3104 | 58.1379 | 0.05 | 29.4143 | 58.296
0.059338 | 29.35 | 59.3909 | 0.06 | 29.4816 | 59.6643 | Power
0.069228 | 29.3871 | 60.6685 | 0.07 | 29.5344 | 61.0317 | a | 51.4766
0.079117 | 29.4203 | 61.9678 | 0.08 | 29.5726 | 62.3974 | b | 135.5255
0.089007 | 29.4478 | 63.2859 | 0.09 | 29.5963 | 63.7602 | c | 25.4998
0.098897 | 29.4683 | 64.6195 | 0.1 | 29.6054 | 65.1193 | d | -164.8457
0.10879 | 29.4802 | 65.9657 | 0.11 | 29.6 | 66.4735
0.11868 | 29.4823 | 67.3214 | 0.12 | 29.58 | 67.822
0.12857 | 29.4734 | 68.6833 | 0.13 | 29.5456 | 69.1636
0.13846 | 29.4523 | 70.0484 | 0.14 | 29.4966 | 70.4976
0.14835 | 29.4181 | 71.4136 | 0.15 | 29.4332 | 71.8228
0.15823 | 29.3698 | 72.7756 | 0.16 | 29.3553 | 73.1382
0.16812 | 29.3066 | 74.1314 | 0.17 | 29.2629 | 74.4429
0.17801 | 29.2277 | 75.478 | 0.18 | 29.1561 | 75.736
0.1879 | 29.1324 | 76.8123 | 0.19 | 29.0349 | 77.0163
0.19779 | 29.0204 | 78.1314 | 0.2 | 28.8993 | 78.2829
0.20768 | 28.891 | 79.4326 | 0.21 | 28.7492 | 79.5348
0.21757 | 28.7438 | 80.713 | 0.22 | 28.5848 | 80.7711
0.22746 | 28.5788 | 81.9701 | 0.23 | 28.4059 | 81.9907
0.23735 | 28.3956 | 83.2014 | 0.24 | 28.2128 | 83.1926
0.24724 | 28.1942 | 84.4047 | 0.25 | 28.0052 | 84.3759
0.25713 | 27.9745 | 85.5779 | 0.26 | 27.7833 | 85.5396
0.26702 | 27.7368 | 86.7192 | 0.27 | 27.5471 | 86.6827
0.27691 | 27.4812 | 87.827 | 0.28 | 27.2966 | 87.8042
0.2868 | 27.208 | 88.8998 | 0.29 | 27.0318 | 88.9031
0.29669 | 26.9176 | 89.9368 | 0.3 | 26.7527 | 89.9783
0.30658 | 26.6104 | 90.9372 | 0.31 | 26.4593 | 91.0291
0.31647 | 26.2871 | 91.9009 | 0.32 | 26.1517 | 92.0542
0.32636 | 25.9483 | 92.8279 | 0.33 | 25.8298 | 93.0528
0.33625 | 25.5948 | 93.7189 | 0.34 | 25.4937 | 94.0239
0.34614 | 25.2275 | 94.575 | 0.35 | 25.1433 | 94.9664
0.35603 | 24.8472 | 95.398 | 0.36 | 24.7788 | 95.8795
0.36592 | 24.4551 | 96.1903 | 0.37 | 24.4 | 96.762
0.37581 | 24.0523 | 96.955 | 0.38 | 24.0071 | 97.613
0.3857 | 23.64 | 97.6961 | 0.39 | 23.6 | 98.4315
0.39559 | 23.2196 | 98.4181 | 0.4 | 23.1787 | 99.2166
0.40548 | 22.7924 | 99.1272 | 0.41 | 22.7433 | 99.9672
0.41537 | 22.3601 | 99.8299 | 0.42 | 22.2938 | 100.6823
0.42526 | 21.9242 | 100.5345 | 0.43 | 21.8301 | 101.361
0.43515 | 21.4864 | 101.2507 | 0.44 | 21.3524 | 102.0023
0.44504 | 21.0484 | 101.9892 | 0.45 | 20.8605 | 102.6052
0.45493 | 20.6124 | 102.7634 | 0.46 | 20.3546 | 103.1686
0.46481 | 20.1801 | 103.5878 | 0.47 | 19.8346 | 103.6917
0.4747 | 19.7537 | 104.48 | 0.48 | 19.3006 | 104.1733
0.48459 | 19.3354 | 105.46 | 0.49 | 18.7525 | 104.6126
|  |  | 0.5 | 18.1904 | 105.0085

## Valve Characteristic
Opening and closing profiles for a typical linearly actuated ball valve
Time (%) | Closing (%) | Opening (%)
0 | 100 | 0
1 | 98.4209 | 0.085117
2 | 97.3275 | 0.17023
3 | 95.6942 | 0.25533
4 | 93.7341 | 0.34045
5 | 91.2029 | 0.42557
6 | 88.1379 | 0.51068
7 | 85.065 | 0.59578
8 | 81.7399 | 0.6809
9 | 78.2271 | 0.76602
10 | 74.5273 | 0.85113
11 | 70.6159 | 0.93878
12 | 66.5249 | 1.1249
13 | 62.3503 | 1.3043
14 | 58.7863 | 1.4488
15 | 55.7123 | 1.6253
16 | 52.8361 | 1.8225
17 | 50.1959 | 1.9993
18 | 47.7186 | 2.179
19 | 45.3861 | 2.4426
20 | 43.2232 | 2.6138
21 | 41.1543 | 2.8654
22 | 39.2039 | 3.0931
23 | 37.3497 | 3.2304
24 | 35.6013 | 3.3655
25 | 33.9431 | 3.5693
26 | 32.3426 | 3.8129
27 | 30.8219 | 4.0238
28 | 29.423 | 4.2331
29 | 28.0683 | 4.4862
30 | 26.7595 | 4.7462
31 | 25.5352 | 5.0068
32 | 24.3506 | 5.3027
33 | 23.2183 | 5.5744
34 | 22.1557 | 5.8344
35 | 21.1428 | 6.1269
36 | 20.1587 | 6.4234
37 | 19.2283 | 6.7148
38 | 18.3772 | 7.0423
39 | 17.5598 | 7.343
40 | 16.7801 | 7.675
41 | 16.0435 | 8.0175
42 | 15.3523 | 8.356
43 | 14.704 | 8.6966
44 | 14.0945 | 9.0483
45 | 13.5239 | 9.4073
46 | 12.9955 | 9.7795
47 | 12.5359 | 10.159
48 | 12.1174 | 10.5258
49 | 11.7031 | 10.923
50 | 11.3102 | 11.3102
51 | 10.923 | 11.7031
52 | 10.5258 | 12.1174
53 | 10.159 | 12.5359
54 | 9.7795 | 12.9955
55 | 9.4073 | 13.5239
56 | 9.0483 | 14.0945
57 | 8.6966 | 14.704
58 | 8.356 | 15.3523
59 | 8.0175 | 16.0435
60 | 7.675 | 16.7801
61 | 7.343 | 17.5598
62 | 7.0423 | 18.3772
63 | 6.7148 | 19.2283
64 | 6.4234 | 20.1587
65 | 6.1269 | 21.1428
66 | 5.8344 | 22.1557
67 | 5.5744 | 23.2183
68 | 5.3027 | 24.3506
69 | 5.0068 | 25.5352
70 | 4.7462 | 26.7595
71 | 4.4862 | 28.0683
72 | 4.2331 | 29.423
73 | 4.0238 | 30.8219
74 | 3.8129 | 32.3426
75 | 3.5693 | 33.9431
76 | 3.3655 | 35.6013
77 | 3.2304 | 37.3497
78 | 3.0931 | 39.2039
79 | 2.8654 | 41.1543
80 | 2.6138 | 43.2232
81 | 2.4426 | 45.3861
82 | 2.179 | 47.7186
83 | 1.9993 | 50.1959
84 | 1.8225 | 52.8361
85 | 1.6253 | 55.7123
86 | 1.4488 | 58.7863
87 | 1.3043 | 62.3503
88 | 1.1249 | 66.5249
89 | 0.93878 | 70.6159
90 | 0.85113 | 74.5273
91 | 0.76602 | 78.2271
92 | 0.6809 | 81.7399
93 | 0.59578 | 85.065
94 | 0.51068 | 88.1379
95 | 0.42557 | 91.2029
96 | 0.34045 | 93.7341
97 | 0.25533 | 95.6942
98 | 0.17023 | 97.3275
99 | 0.085117 | 98.4209
100 | 0 | 100

## Check Valve Information
Check Valve Closure (Example 4) based on data from Thorley, A. R. D., (2004), Fluid Transients in Pipeline Systems, D. & L. George Ltd, Hertfordshire, England.
Fluid Deceleration (m/s2) | Reverse Velocity (m/s)
0.75152 | 0.16273
0.881 | 0.18994
0.97642 | 0.2101
1.1197 | 0.2418
1.2082 | 0.26037
1.3515 | 0.29219
1.4128 | 0.30485
1.6447 | 0.35621
1.8561 | 0.4024
1.9174 | 0.41528
2.1154 | 0.46221
2.1904 | 0.47742
2.4155 | 0.5275
2.4699 | 0.53735
2.6542 | 0.58017
2.7085 | 0.58842
2.8383 | 0.62023
2.9063 | 0.63328
3.0633 | 0.66897
3.2337 | 0.70512
3.3086 | 0.7204
3.3768 | 0.73532
3.445 | 0.75037
3.5132 | 0.76502
3.5813 | 0.77967
3.6495 | 0.79432
3.7177 | 0.80923
3.7859 | 0.82361
3.854 | 0.8384
3.9222 | 0.85331
3.9904 | 0.86796
4.0586 | 0.88301
4.1267 | 0.89699
4.1949 | 0.91177
4.2631 | 0.92642
4.3313 | 0.94107
4.3995 | 0.95599
4.4676 | 0.9705
4.5359 | 0.98609
4.604 | 1.0009
4.679 | 1.0168
4.7539 | 1.0319
4.9586 | 1.0775
5.0268 | 1.0924
5.095 | 1.1075
5.1632 | 1.1233
5.2314 | 1.1385
5.2997 | 1.1546
5.3679 | 1.1699
5.4362 | 1.1854
5.5045 | 1.2017
5.5728 | 1.2183
5.6342 | 1.2323
5.6957 | 1.248
5.7641 | 1.2651
5.8256 | 1.2804
5.887 | 1.2955
5.9485 | 1.3103
6.0101 | 1.3271
6.0717 | 1.3427
6.1333 | 1.3595
6.1949 | 1.3767
6.2497 | 1.3916
6.3044 | 1.4061
6.3592 | 1.4215
6.414 | 1.4372
6.4688 | 1.4526
6.5236 | 1.4688
6.5785 | 1.4852
6.6334 | 1.5022
6.6884 | 1.5197
6.7365 | 1.5353
6.7846 | 1.5513
6.8395 | 1.5691
6.8877 | 1.5857
6.9289 | 1.5987
6.9736 | 1.6131
7.0251 | 1.6298
7.0664 | 1.645
7.1079 | 1.6619
7.1391 | 1.6763
7.1827 | 1.6937
7.2256 | 1.7126
7.2673 | 1.733
7.3078 | 1.7545
7.3373 | 1.7735
7.3666 | 1.7888
7.3922 | 1.8099
7.4177 | 1.8289
7.4436 | 1.8539
7.4712 | 1.8641
7.5244 | 1.9211
7.5298 | 1.9341
7.5487 | 1.9486
7.5675 | 1.9742
7.5743 | 1.9945
Process for estimation of check valve closure velocity:
1) Determine the fluid deceleration through the check valve.
a) Run a transient MOC simulation with the check valve locked open.
b) Export the data for fluid velocity through the check valve.
c) Assume the fluid deceleration is equal to the velocity change from the beginning of the velocity change to the point where it crosses zero.
i) The initial velocity and time are that were it approximately begins it's downturn.
ii) The final time is where the velocity reaches zero.
d) With the delta velocity and delta time, make an estimate for acceleration - dv/dt
2) With this deceleration, look up a maximum reverse velocity with the Swing Check curve from Figure 1.13 "Typical dynamic performance characteristics for various types of check valve" from Thorley's "Fluid Transients in Pipeline Systems", second edition (shown here)
a) Note that Thorley's dimensional data is based on a swing check valve for DN100 - approximately 4 inch pipe. In this example, the pipe size of 0.5 m is approximately 18 inches. We are assuming for the purposes of this study that the DN100 data can adequately be applied to the 0.5 m check valve.
Reverse velocities were calculated for each specific speed and each 4QDC option - the reverse velocities at different specific speeds were found to be approximately the same, and an average value for each 4QDC option was used:
4QBEP Reverse Velocity for Check Valve C: -0.6 m/s
4QOP Reverse Velocity for Check Valve C: -0.3 m/s

## 4Q Suter Data
Raw Four Quadrant Data in Suter Form for various Specific Speeds
Ns = 0.42 from Brown, R. J., and Rogers, D. C. (1980), “Development of Pump Characteristics from Field Tests”, ASME Journal of Mechanical Design, Vol. 102, No. 4, 807-817.
Ns = 0.46 from Wylie, E. B. and Streeter, V. L. (1993), Fluid Transients in Systems, Prentice Hall, Englewood Cliffs, NJ. Original measurements by Swanson, 1953
Ns = 0.79 from Thorley, A. R. D., and Chaudry, A., (1996) “Pump Characteristics for Transient Flow Analysis”, Proc. 7th International conference on pressure surges & fluid transients in pipelines and open channels, BHR Group, Harrogate, UK, April 1996
Ns = 0.42 (22.1 Metric/1140 US) |  |  | Ns = 0.46 (24.6 Metric/1270 US) |  |  | Ns = 0.79 (41.9 Metric/2160 US)
in θ=π + atan(ν/α) form
θ | FH | FB | θ | FH | FB | θ | FH | FB
0 | -0.37 | -0.42 | 0 | 0.634 | -0.684 | 0 | -0.55 | -0.56
5 | -0.32 | -0.27 | 4.091 | 0.643 | -0.547 | 5 | -0.44 | -0.36
10 | -0.24 | -0.12 | 8.182 | 0.646 | -0.414 | 10 | -0.34 | -0.2
15 | -0.15 | 0.01 | 12.273 | 0.64 | -0.292 | 15 | -0.24 | -0.01
20 | -0.06 | 0.14 | 16.364 | 0.629 | -0.187 | 20 | -0.14 | 0.09
25 | 0.02 | 0.24 | 20.455 | 0.613 | -0.105 | 25 | -0.04 | 0.18
30 | 0.18 | 0.33 | 24.545 | 0.595 | -0.053 | 30 | 0.03 | 0.27
35 | 0.31 | 0.41 | 28.636 | 0.575 | -0.012 | 35 | 0.16 | 0.38
40 | 0.41 | 0.47 | 32.727 | 0.552 | 0.042 | 40 | 0.29 | 0.44
45 | 0.5 | 0.5 | 36.818 | 0.533 | 0.097 | 45 | 0.5 | 0.5
50 | 0.61 | 0.54 | 40.909 | 0.516 | 0.156 | 50 | 0.62 | 0.56
55 | 0.7 | 0.56 | 45 | 0.505 | 0.227 | 55 | 0.76 | 0.64
60 | 0.84 | 0.59 | 49.091 | 0.504 | 0.3 | 60 | 0.96 | 0.66
65 | 0.94 | 0.58 | 53.182 | 0.51 | 0.371 | 65 | 1.1 | 0.66
70 | 1.08 | 0.58 | 57.273 | 0.512 | 0.444 | 70 | 1.23 | 0.66
75 | 1.2 | 0.54 | 61.364 | 0.522 | 0.522 | 75 | 1.42 | 0.66
80 | 1.29 | 0.47 | 65.455 | 0.539 | 0.596 | 80 | 1.56 | 0.64
85 | 1.35 | 0.39 | 69.545 | 0.559 | 0.672 | 85 | 1.69 | 0.59
90 | 1.38 | 0.32 | 73.636 | 0.58 | 0.738 | 90 | 1.82 | 0.56
95 | 1.4 | 0.26 | 77.727 | 0.601 | 0.763 | 95 | 2.02 | 0.47
100 | 1.41 | 0.21 | 81.818 | 0.63 | 0.797 | 100 | 2.1 | 0.41
105 | 1.42 | 0.21 | 85.909 | 0.662 | 0.837 | 105 | 2.04 | 0.34
110 | 1.44 | 0.24 | 90 | 0.692 | 0.865 | 110 | 2.04 | 0.31
115 | 1.45 | 0.29 | 94.091 | 0.722 | 0.883 | 115 | 2.13 | 0.31
120 | 1.44 | 0.33 | 98.182 | 0.753 | 0.886 | 120 | 2.16 | 0.31
125 | 1.44 | 0.38 | 102.273 | 0.782 | 0.877 | 125 | 2.1 | 0.32
130 | 1.41 | 0.41 | 106.364 | 0.808 | 0.859 | 130 | 2.02 | 0.34
135 | 1.48 | 0.43 | 110.455 | 0.832 | 0.838 | 135 | 1.96 | 0.35
140 | 1.45 | 0.46 | 114.546 | 0.857 | 0.804 | 140 | 1.82 | 0.36
145 | 1.42 | 0.48 | 118.636 | 0.879 | 0.758 | 145 | 1.72 | 0.37
150 | 1.38 | 0.5 | 122.727 | 0.904 | 0.703 | 150 | 1.56 | 0.41
155 | 1.33 | 0.52 | 126.818 | 0.93 | 0.645 | 155 | 1.44 | 0.49
160 | 1.26 | 0.56 | 130.909 | 0.959 | 0.583 | 160 | 1.54 | 0.69
165 | 1.19 | 0.59 | 135 | 0.996 | 0.52 | 165 | 1.64 | 0.9
170 | 1.08 | 0.6 | 139.091 | 1.027 | 0.454 | 170 | 1.61 | 0.9
175 | 1.09 | 0.57 | 143.182 | 1.06 | 0.408 | 175 | 1.44 | 0.77
180 | 0.85 | 0.48 | 147.273 | 1.09 | 0.37 | 180 | 1.32 | 0.74
185 | 0.71 | 0.39 | 151.364 | 1.124 | 0.343 | 185 | 1.23 | 0.74
190 | 0.59 | 0.34 | 155.455 | 1.165 | 0.331 | 190 | 1.3 | 0.79
195 | 0.51 | 0.29 | 159.546 | 1.204 | 0.329 | 195 | 1.28 | 0.76
200 | 0.45 | 0.25 | 163.636 | 1.238 | 0.338 | 200 | 1.19 | 0.67
205 | 0.44 | 0.21 | 167.727 | 1.258 | 0.354 | 205 | 1.04 | 0.61
210 | 0.45 | 0.19 | 171.818 | 1.271 | 0.372 | 210 | 0.81 | 0.5
215 | 0.48 | 0.15 | 175.909 | 1.282 | 0.405 | 215 | 0.77 | 0.44
220 | 0.53 | 0.11 | 180 | 1.288 | 0.45 | 220 | 0.83 | 0.34
225 | 0.59 | 0.07 | 184.091 | 1.281 | 0.486 | 225 | 0.9 | 0.25
230 | 0.63 | 0.03 | 188.182 | 1.26 | 0.52 | 230 | 0.94 | 0.15
235 | 0.69 | -0.02 | 192.273 | 1.225 | 0.552 | 235 | 0.98 | 0.07
240 | 0.77 | -0.06 | 196.364 | 1.172 | 0.579 | 240 | 0.96 | 0
245 | 0.85 | -0.11 | 200.455 | 1.107 | 0.603 | 245 | 0.92 | -0.1
250 | 0.91 | -0.19 | 204.546 | 1.031 | 0.616 | 250 | 0.9 | -0.18
255 | 0.94 | -0.27 | 208.636 | 0.942 | 0.617 | 255 | 0.88 | -0.25
260 | 0.94 | -0.38 | 212.727 | 0.842 | 0.606 | 260 | 0.88 | -0.32
265 | 0.91 | -0.49 | 216.818 | 0.733 | 0.582 | 265 | 0.86 | -0.42
270 | 0.86 | -0.62 | 220.909 | 0.617 | 0.546 | 270 | 0.86 | -0.48
275 | 0.77 | -0.73 | 225 | 0.5 | 0.5 | 275 | 0.72 | -0.66
280 | 0.69 | -0.81 | 229.091 | 0.368 | 0.432 | 280 | 0.53 | -0.83
285 | 0.64 | -0.86 | 233.182 | 0.24 | 0.36 | 285 | 0.49 | -0.98
290 | 0.59 | -0.87 | 237.273 | 0.125 | 0.288 | 290 | 0.36 | -1.08
295 | 0.5 | -0.9 | 241.364 | 0.011 | 0.214 | 295 | -0.03 | -1.23
300 | 0.42 | -0.93 | 245.455 | -0.102 | 0.123 | 300 | -0.25 | -1.42
305 | 0.31 | -1.09 | 249.546 | -0.168 | 0.037 | 305 | -0.42 | -1.51
310 | 0.21 | -1.09 | 253.636 | -0.255 | -0.053 | 310 | -0.58 | -1.61
315 | 0.12 | -1.09 | 257.727 | -0.342 | -0.161 | 315 | -0.74 | -1.64
320 | 0.05 | -1.1 | 261.818 | -0.423 | -0.248 | 320 | -0.86 | -1.64
325 | -0.04 | -0.97 | 265.909 | -0.494 | -0.314 | 325 | -0.94 | -1.61
330 | -0.13 | -0.95 | 270 | -0.556 | -0.372 | 330 | -1 | -1.6
335 | -0.22 | -0.92 | 274.091 | -0.62 | -0.58 | 335 | -1.21 | -1.56
340 | -0.3 | -0.88 | 278.182 | -0.655 | -0.74 | 340 | -1.44 | -1.49
345 | -0.36 | -0.78 | 282.273 | -0.67 | -0.88 | 345 | -1 | -1.37
350 | -0.38 | -0.69 | 286.364 | -0.67 | -1 | 350 | -0.86 | -1.08
355 | -0.38 | -0.59 | 290.455 | -0.66 | -1.12 | 355 | -0.67 | -0.81
360 | -0.37 | -0.42 | 294.545 | -0.655 | -1.25 | 360 | -0.55 | -0.56
|  |  | 298.636 | -0.64 | -1.37
|  |  | 302.727 | -0.6 | -1.49
|  |  | 306.818 | -0.57 | -1.59
|  |  | 310.909 | -0.52 | -1.66
|  |  | 315 | -0.47 | -1.69
|  |  | 319.091 | -0.43 | -1.77
|  |  | 323.182 | -0.36 | -1.65
|  |  | 327.273 | -0.275 | -1.59
|  |  | 331.364 | -0.16 | -1.52
|  |  | 335.455 | -0.04 | -1.42
|  |  | 339.545 | 0.13 | -1.32
|  |  | 343.636 | 0.295 | -1.23
|  |  | 347.727 | 0.43 | -1.1
|  |  | 351.818 | 0.55 | -0.98
|  |  | 355.909 | 0.62 | -0.82
|  |  | 360 | 0.634 | -0.684