## Input Pump Handbook
Based on "Jet Pump Example.fth" Model
Pressure Ratio at Zero Flow
| PR | 2.8088 |  |  | From Pump Handbook (p. 4.9 in 2nd Ed., p. 4.30 in 3rd Ed.)
| Psupply | 100 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 30 | psig
| DP | 38.7 | psid | (approximate)
Pressure Ratio at Max Flow (200 gpm supply, 130 gpm suction)
| PR | 6.509
| Psupply | 100 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 8 | psig
| DP | 16.7 | psid | (approximate)
Max Flow ratio
| QR | 0.65
| Qsupply | 200 | gpm
| Qsuction | 130 | gpm

## Input Model
Based on "Jet Pump Example.fth" Model
Pressure Ratio at Zero Flow |  |  |  |  | Jet Pump Input Data (junction J7)
| PR | 2.8088
| Psupply | 100 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 30 | psig
| DP | 38.7 | psid | (approximate)
Pressure Ratio at Max Flow (200 gpm supply, 130 gpm suction)
| PR | 6.509
| Psupply | 100 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 8 | psig
| DP | 16.7 | psid | (approximate)
Max Flow ratio
| QR | 0.65
| Qsupply | 200 | gpm
| Qsuction | 130 | gpm
From Pump Handbook (p. 4.9 in 2nd Ed., p. 4.30 in 3rd Ed.)

## Equivalent Centrifugal Pump
Based on "Jet Pump Example.fth" Model
Equivalent Centrifugal Pump Input Data (junction J4)
Pressure Ratio at Zero Flow | [5 empty] | This is provided for general interest to better understand how the jet pump model works
| PR | 2.8088
| Psupply | 100 | psig | 85.3 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 30 | psig | 15.3 | psig
| DP | 38.7 | psid | (approximate)
Pressure Ratio at Max Flow (200 gpm supply, 130 gpm suction)
| PR | 6.509
| Psupply | 100 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 8 | psig | -6.7 | psig
| DP | 16.7 | psid | (approximate)
Max Flow ratio
| QR | 0.65
| Qsupply | 200 | gpm
| Qsuction | 130 | gpm

## Output
Based on "Jet Pump Example.fth" Model
Pipe Output
Pipe | Name | Vol. Flow Rate (gal/min) | Velocity (feet/sec) | P Static Max (psia) | P Static Min (psia) | Elevation Inlet (feet) | Elevation Outlet (feet) | dP Stag. Total (psid) | dP Static Total (psid) | dP Gravity (psid) | dH (feet) | P Static In (psig) | P Static Out (psig) | P Stag. In (psig) | P Stag. Out (psig)
1 | Pipe | 99.9 | 2.518 | 14.65 | 5.947 | 0 | 20 | 8.7067 | 8.7067 | 8.654 | 0.12185 | -0.04263 | -8.749 | 0 | -8.707
2 | Pipe | 298.48 | 7.522 | 27.4 | 26.984 | 20 | 20 | 0.41731 | 0.41731 | 0 | 0.96443 | 12.706 | 12.289 | 13.09 | 12.669
3 | Pipe | 99.9 | 2.518 | 27.74 | 27.74 | 20 | 20 | 0.0008117 | 0.0008117 | 0 | 0.001876 | 13.0441 | 13.044 | 13.09 | 13.086
11 | Pipe | 100 | 2.52 | 14.65 | 5.947 | 0 | 20 | 8.7068 | 8.7068 | 8.654 | 0.12207 | -0.0427 | -8.749 | 0 | -8.707
12 | Pipe | 298.58 | 7.525 | 27.4 | 26.984 | 20 | 20 | 0.4177 | 0.4177 | 0 | 0.96533 | 12.706 | 12.288 | 13.09 | 12.669
Suction flow predictions are virtually the same at 100 gpm
Junction Output
Jct | Name | P Static In (psia) | P Static Out (psia) | P Stag. In (psia) | P Stag. Out (psia) | Vol. Flow Rate Thru Jct (gal/min) | Mass Flow Rate Thru Jct (lbm/sec) | Loss Factor (K) | dP Stag. Total (psid)
1 | Reservoir | 14.696 | 14.7 | 14.696 | 14.7 | 99.9 | 13.87 | 0 | 0
3 | Assigned Pressure | 26.984 | 26.98 | 27.365 | 27.36 | 298.48 | 41.44 | 0 | 0
4 | Pump | 5.947 | 27.74 | 5.989 | 27.78 | 99.9 | 13.87 | 0 | -21.79
5 | Branch | 27.74 | 27.4 | 27.782 | 27.78 | N/A | N/A | 0 | 0
7 | Jet Pump | 5.947 | 27.4 | 5.989 | 27.78 | 100 | 13.88 | 0 | -21.79
11 | Reservoir | 14.696 | 14.7 | 14.696 | 14.7 | 100 | 13.88 | 0 | 0
13 | Assigned Pressure | 26.984 | 26.98 | 27.365 | 27.36 | 298.58 | 41.45 | 0 | 0
Pump pressure rise the same at 21.8 psid
Pressure Ratio at Zero Flow | [7 empty] | Actual Flow Ratio = 0.5
| PR | 2.8088 | [6 empty] | Qsupply | 200 | gpm
[9 empty] | Qsuction | 100 | gpm
| Psupply | 100 | psig | [5 empty] | QR | 0.5 | gpm
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 30 | psig
Pressure Ratio at QR = 0.5
| DP | 38.7 | psid | (approximate) |  |  |  |  | QR | Pdischarge
[9 empty] | - | (psig)
[9 empty] | 0 | 30
Pressure Ratio at Max Flow (200 gpm supply, 130 gpm suction) | [8 empty] | 0.65 | 8
| PR | 6.509 | [6 empty] | 0.5 | 13.0769 | psig
| Psupply | 100 | psig
| Psuction | -8.7 | psig | (approximate)
| Pdischarge | 8 | psig
| DP | 16.7 | psid | (approximate)
Max Flow ratio
| QR | 0.65
| Qsupply | 200 | gpm
| Qsuction | 130 | gpm